# Attachment B
Statement of Special Inspections*

[*  As an alternative to the Word tables, a spreadsheet is acceptable.]

****************************************************************************************************************

Statement of Special Inspections (SSI)

This template must be edited for each project.  For example, the Special Cases table will need to be filled out with specific inspection requirements outlined in the building component’s ICC-ES report or LBO-approved equal.

The SSI must also be edited to delete inspection requirement tables for building components not used in the project – and all author’s notes such as these.

******************************************************************************************************************************

| Project: | XYZ Structure |
| --- | --- |
| Location: | TA-XX, Bldg XXXX |
| IBC Code Year: | [2009] |
| Primary Design Professionals: | Name, Firm, Structural Name, Firm, Architectural Name, Firm, Electrical Name, Firm, Mechanical Name, Firm, Fire |

This SSI is a requirement of International Building Code (IBC) Chapter 17.  The special inspections listed herein are hold/witness points – they must be observed by LANL (will be conducted by LANL if LANL chooses).  Special tests, while rarely required, are always Subcontractor responsibility except as noted.

This SSI encompasses the following disciplines:

| Structural | Mechanical/Electrical/Plumbing |
| --- | --- |
| Architectural | Other: |  |
| Fire |  |  |

The LANL Special Inspectors on the project shall keep records of all inspections and shall furnish interim inspection reports to the LANL Chief Inspector (LCI) and the LANL Project Manager.  LANL ESM Chapter 16, Section IBC-IP Attachment D – IBC Inspection Daily Report shall be used as the basis for the report.  Discovered discrepancies shall be brought to the immediate attention of the constructor (e.g., Subcontractor) for correction.  If such discrepancies are not corrected, the discrepancies shall be brought to the attention of the LCI and DPIRC. The LANL inspection program does not relieve the constructor (e.g., Subcontractor) of their responsibilities.

| Interim Report Frequency: | Daily as inspections are performed |
| --- | --- |

A Final Report documenting completion of all required inspections, testing and correction of any discrepancies noted in the inspection reports shall be submitted to the LCI prior to issuance of Official Acceptance of Construction.  LANL ESM Chapter 16, Section IBC-IP Attachment E – IBC Inspection Final Report shall be used as the basis for the report.

Job site safety and means and methods of construction are solely the responsibility of the constructor (e.g., Subcontractor).

Special Inspections are not required where the work is done on the premises of a fabricator registered and approved by the LBO to perform such work without special inspection in accordance with IBC Section 1704.2.2 and ESM Chapter 16.

In the event of a true conflict between this plan and the Project Specification, the more stringent requirement applies.

[Structural Observations:  Shall be provided per the provisions of IBC Section 1710 and shall consist of visual observations of the structural systems by a registered design professional (Engineer of Record unless otherwise approved by LANL) for conformance to the approved construction documents at significant construction stages and at completion of the structural system.]

****************************************************************************************************************

Note:  If Structural Observation (SO) applies to the Project, the DPIRC is responsible for appending the SO form to the SSI.  Template of form is Att G of ESM Ch. 16, Sect. IBC-IP.

Make template project-specific by filling in Project title / name, and description / listing of seismic force resisting system(s) and/or designated seismic systems.  Commit to the number of visits and extent of observation planned.

****************************************************************************************************************

## Signature Page

| Statement of Special Inspections Prepared By: |
| --- |
| (type or print name) |
| Signature | Date |

| Statement of Special Inspections Submitted By: |
| --- |
| (type or print name) |
| Signature | Date |

| Design Professional Seal Structural | Design Professional Seal Architectural |
| --- | --- |
| Design Professional Seal Mechanical | Design Professional Seal Electrical |

| LANL Inspection Group (CM-CE) Acceptance |  | LBO stamp applied by LANL Design Eng |
| --- | --- | --- |
| Signature | Date |  |  |  |

## Schedule of Inspection and Testing Agencies

This Statement of Special Inspections includes the following building systems:

Fabrication of structural load bearing members

Soils

Seismic Force-Resisting Systems

Driven Deep Foundations

Cast-in-Place Deep Foundations

Helical Pile Foundations

Concrete

Structural Steel

Cold-Formed Steel Framing

Masonry	Level 1

Masonry	Level 2

Wood

Spray Fire Resistant Material

Mastic and Intumescent Fire-resistant Coatings

Exterior Insulation and Finish System

Special Cases as required by LBO

Smoke Control

| Special Inspection Agencies | Firm | Address, Telephone, e-mail |
| --- | --- | --- |
| 1. IBC Special Inspections unless otherwise noted | LANL | LANL |
| 2. Soils Testing Agency | TBD | TBD |
| 3. Concrete Testing Agency | TBD | TBD |
| 4. Masonry Testing Agency | TBD | TBD |
| 5. Steel/Rebar Testing Agency | TBD | TBD |
| 6. Other | TBD | TBD |
| 7. Engineer of Record | TBD | TBD |

TBD: To be determined

Note:  The inspectors shall be engaged by the LANL or LANL’s Agent except where SSI notes “Subcontractor Scope.” In those cases, the testing agencies must be approved by the LANL Building Official (LBO) before engaged by the Subcontractor.  Any conflict of interest must be disclosed to the LANL Chief Inspector prior to commencing work.

******************************************************************************************************************************

When project includes construction or fabrication of a main seismic-force-resisting system, designated seismic system, or a seismic-resisting component, list required inspections in this document and list the need to submit to LANL a Subcontractors Statement of Responsibility with respect to Special Inspections in accordance with IBC-IP Attachment H prior to the commencement of work in Exhibit I Submittal Procedures (or Spec Section 01 3300 if present – e.g., if general constructor is LANL), and 01 4000, Quality Requirements.

******************************************************************************************************************************

Seismic Resistance Plan

###### Systems for Seismic Resistance

| Seismic Design Category | D |
| --- | --- |
| Statement of Responsibility Required (Y/N) | [Y] |
| Description of seismic-force-resisting system and designated seismic systems [edit text below for Project specifics]: Seismic Force Resisting System: Main Seismic Force Resisting System: Ordinary Steel Concentric Braced Framing Designated Seismic System Components: Mechanical Exhaust Ventilation System Hazardous Waste System Fire Sprinklers/Suppression Indicate whether “Demand-Critical” welding is required so fabricator can determine whether they have enough qualified welders to meet the need The more stringent of AISC 341 and AWS D1.8 QA plan requirements that apply to the Project must either be included herein (in the Steel table), or (preferably) in an attachment that consists of a project-specific version of the attached QA Plan template. If the latter option is selected, ensure that the SSI refers to the attachment (as a minimum, in the table(s) for Steel -- and possibly tables for seismic force resisting tests and inspections). |

[Statement of Responsibility

Each Subcontractor and Subtier responsible for the construction or fabrication of a system or component designated above must submit a Statement of Responsibility.

The form for this ‘statement’ must be attached to this SSI and DPIRC has to have completed the portions of it that are within his / her purview. ]

SSI Tables

***********************************************************************************************************************

The minimum scope of the inspections required for the project must be determined by the Design Professional in Responsible Change (DPIRC) but shall not be less than those required by IBC Chapter 17.  The LBO, through its reviewers, may require addition inspections per Special Cases table below.  Thus, the engineer-of-record cannot delete any special inspections specified by the code or the tables in Chapter 17 unless they are not applicable (e.g., there is no masonry) nor can they change the indicated inspection frequency (i.e., ’continuous’ vs. ’periodic’). The engineer-of-record can and should add additional inspections beyond the IBC minimum where appropriate.  EOR MUST delete entire tables that are N/A, and delete or mark “N/A” any row not applicable.]

***********************************************************************************************************************

X or Y means required    	-- or N or N/A means not required

| FABRICATORS -- Special Inspection and Verification (1704.2.1) |
| --- |
| Special Inspection Required Y/N | Verification and Inspection Task | Inspection Frequency | Reference for Criteria |
|  |  | Continuous During Task Listed | Periodically During Task Listed | IBC Reference |
| Y | Verify that the fabricator maintains detailed fabrication and quality control procedures that provide a basis for inspection control of the workmanship and the fabricator's ability to conform to approved construction documents and referenced standards. [DPIRC Note: See 1704.2 for exception] | ---- | X | 1704.2.1 |
| Y | Review the procedures for completeness and adequacy relative to the code requirements for the fabricator's scope of work. [DPIRC Note: See 1704.2.2 for exception] | ---- | X | 1704.2.1 |

| SOILS -- Special Inspection and Verification (1704.7) |
| --- |
| Special Inspection Required Y/N | Verification and Inspection Task | Inspection Frequency | Reference for Criteria |
|  |  | Continuous During Task Listed | Periodically During Task Listed | IBC Reference |
| Y | Civil PE: Verify materials below shallow foundations are adequate to achieve the design bearing capacity. | ---- | X | 1704.7 |
| Y | Verify excavations are extended to proper depth and have reached proper material. | ---- | X | 1704.7 |
| Y | Subcontractor Scope Tests (3rd party): Perform classification and testing of compacted fill materials | ---- | X | 1704.7 |
| Y | Verify use of proper materials, densities and lift thicknesses during placement and compaction of compacted fill. | X | ---- | 1704.7 |
| Y | Prior to placement of compacted fill, observe subgrade and verify that site has been prepared properly. | ---- | X | 1704.7 |

| SEISMIC RESISTANCE OF SEISMIC FORCE RESISTING SYSTEMS -- STRUCTURAL TESTING (1708) |
| --- |
| Special Inspection Required Y/N | Verification and Inspection Task | Inspection Frequency | Reference for Criteria |
|  |  | Continuous During Task Listed | Periodically During Task Listed | IBC Reference |
| Y | Where concrete-reinforcing steel (rebar) complying with ASTM A 615 is used to resist earthquake-induced flexural and axial forces in special moment frames, special structural walls and coupling beams connecting special structural walls, the rebar must comply with Section 21.1.5.2 of ACI 318 and the Spec. Review certified mill test reports for each shipment of such rebar. | X | ---- | 1708.2 |
| Y | Where concrete-reinforcing steel complying with ASTM A 615 is to be welded, perform chemical tests to determine weldability in accordance with Section 3.5.2 of ACI 318. | X | ---- | 1708.2 |
| Y | Testing of structural steel per the QA plan requirements of AISC 341. [DPIRC Note: See 1708.3 2 for exception.] | Per AISC 341 | Per AISC 341 | 1708.3 |

| SEISMIC-FORCE-RESISTING AND DESIGNATED SYSTEMS -- SPECIAL INSPECTION (1707) |
| --- |
| Special Inspection Required Y/N | Verification and Inspection Task | Inspection Frequency | Reference for Criteria |
|  |  | Continuous During Task Listed | Periodically During Task Listed | IBC Reference |
|  | Structural Steel: |
| Y | a. Inspection per the QA plan requirements of AISC 341 Section 18 and Q (thus Appendix A of this SSI). [DPIRC Note: See Section 1707.2.1 for exception.] | Per AISC 341 | Per AISC 341 | 1707.2 |
|  | Structural Wood: |
| Y | a. Field gluing operations of elements in the system | X | ---- | 1707.3 |
| Y | b. Nailing, bolting, anchoring, and other fastening of components within the seismic-force-resisting system, including wood shear walls, wood diaphragms, drag struts, braces, and hold-downs. [DPIRC Note: See Sections 1707.3 for exception] | ---- | X | 1707.3 |
|  | Cold-Formed Steel Framing: |
| Y | a. Welding operations of elements of the systems. | ---- | X | 1707.4 |
| Y | b. Screw attachments, bolting, anchoring, and other fastening of components within the system including shear walls, braces, diaphragms, collectors and hold-downs. [DPIRC Note: See Section 1707.4 for exceptions] | ---- | X | 1707.4 |
|  | Storage Racks and Access Floors: |
| Y | a. Anchorage of access floors. | ---- | X | 1707.5 |
| Y | b. Anchorage of storage racks 8 feet or greater in height. | ---- | X | 1707.5 |
|  | Architectural Components: |
| Y | a. Erection and fastening of exterior cladding, interior and exterior nonbearing walls and interior and exterior veneer. [DPIRC Note: See Section 1707.6 for exceptions.] | ---- | X | 1707.6 |
|  | Mechanical and Electrical Components: |
| Y | a. Anchorage of electrical equipment for emergency or standby power systems. | ---- | X | 1707.7 |
| Y | b. Installation of piping systems intended to carry flammable, combustible or highly toxic contents and their associated mechanical units. | ---- | X | 1707.7 |
| Y | c. Installation of HVAC ductwork that will contain hazardous materials | ---- | X | 1707.7 |
| Y | d. Installation of vibration isolation systems where the construction documents require a nominal clearance of 1/4" or less between the equipment support frame and restraint. | ---- | X | 1707.7 |
|  | Designated Seismic System Verifications: |
| Y | Examine systems requiring seismic qualification in accordance with Section 1708.4; verify that the label, anchorage or mounting conforms to the certificate of compliance. | Per ASCE 13.2.1 and 13.2.2 | Per ASCE 13.2.1 and 13.2.2 | 1707.8 |
|  | Seismic Isolation Systems: |
| Y | a. Fabrication and installation of isolator units and energy dissipation devices that are part of the systems. | ---- | X | 1707.9 |

| DRIVEN DEEP FOUNDATION ELEMENTS -- Special Inspection and Verification (1704.8) |
| --- |
| Special Inspection Required Y/N | Verification and Inspection Task | Inspection Frequency | Reference for Criteria |
|  |  | Continuous During Task Listed | Periodically During Task Listed | IBC Reference |
| Y | Verify element materials, sizes and lengths. | X | ---- | 1704.8 |
| Y | Determine capacities of test elements and conduct additional load tests as required. | X | ---- | 1704.8 |
| Y | Observe driving operations and maintain complete and accurate records for each element. | X | ---- | 1704.8 |
| Y | Verify placement locations and plumbness, confirm type and size of hammer, record number of blows per foot of penetration, determine required penetrations to achieve design capacity, record tip and butt elevations and document any damage to foundation element. | X | ---- | 1704.8 |
| Y | For steel, perform additional inspections in accordance with Section 1704.3. | ---- | ---- | 1704.8 |
| Y | For concrete and concrete-filled elements, perform additional inspections per Section 1704.4. | ---- | ---- | 1704.8 |
| Y | For specialty elements, perform additional inspections as determined by the registered design professional in responsible charge. | ---- | ---- | 1704.8 |

| CAST-IN-PLACE DEEP FOUNDATIONS -- Special Inspection and Verification (1704.9) |
| --- |
| Special Inspection Required Y/N | Verification and Inspection Task | Inspection Frequency | Reference for Criteria |
|  |  | Continuous During Task Listed | Periodically During Task Listed | IBC Reference |
| Y | Observe drilling operations and maintain complete and accurate records for each element. | X | ---- | 1704.9 |
| Y | Verify placement locations and plumbness, confirm element diameters, bell diameters (if applicable), lengths, embedment into bedrock (if applicable) and adequate end-bearing strata capacity. Record concrete and grout volumes. | X | ---- | 1704.9 |
| Y | For concrete elements, perform additional inspections in accordance with Section 1704.4. | ---- | ---- | 1704.9 |

| HELICAL PILE FOUNDATIONS -- Special Inspection and Verification (1704.10) |
| --- |
| Special Inspection Required Y/N | Verification and Inspection Task | Inspection Frequency | Reference for Criteria |
|  |  | Continuous During Task Listed | Periodically During Task Listed | IBC Reference |
| Y | Observe installation of helical pile foundation. | X | ---- | 1704.10 |
| Y | Record installation equipment used, pile dimensions, tip elevations, final depth, final installation torque and other pertinent installation data as required by the DPIRC. | X | ---- | 1704.10 |

| CONCRETE -- Special Inspection and Verification (1904-1913) |
| --- |
| Special Inspection Required Y/N | Verification and Inspection Task | Inspection Frequency | Reference for Criteria |
|  |  | Continuous During Task Listed | Periodically During Task Listed | Referenced Standard | IBC Reference |
|  | [DPIRC Note: See 1704.4 for exceptions] |  |
| Y | Inspect reinforcing steel, including prestressing tendons, and placement. | ---- | X | ACI 318: 3.5, 7.1-7.7 | 1913.4 |
| Y | Inspect reinforcing steel welding in accordance with Table 1704.3, Item 5b. | ---- | ---- | AWS D1.4 ACI 318: 3.5.2 | ---- |
| Y | Inspect bolts to be installed in concrete prior to and during placement of concrete where allowable loads have been increased or where strength design is used. | X | ---- | ACI 318: 8.1.3, 21.1.8 | 1911.5, 1912.1 |
| Y | Inspect anchors installed in hardened concrete. | ---- | X | ACI 318: 3.8.6, 8.1.3, 21.1.8 | 1912.1 |
| Y | Verify use of required design mix. | ---- | X | ACI 318: Ch. 4, 5.2-5.4 | 1904.3, 1913.2, 1913.3 |
| Y | Subcontractor Scope Tests (3rd party): At the time fresh concrete is sampled to fabricate specimens for strength tests, perform slump and air content tests, and determine the temperature of the concrete. | X | ---- | ASTM C 172, ASTM C 31, ACI 318: 5.6, 5.8 | 1913.10 |
| Y | Inspect concrete and shotcrete placement for proper application techniques. | X | ---- | ACI 318: 5.9, 5.10 | 1913.6, 1913.7, 1913.8 |
| Y | Inspect maintenance of specified curing temperature and techniques. | ---- | X | ACI 318: 5.11-5.13 | 1913.9 |
| Y | Inspect Prestressed Concrete: |
| Y | a. Application of prestressing forces. | X | ---- | ACI 318: 18.20 | ---- |
| Y | b. Grouting of bonded prestressing tendons in the seismic-force-resisting system. | X | ---- | ACI 318: 18.18.4 | ---- |
| Y | Erection of precast concrete members. | ---- | X | ACI 318: Ch. 16 | ---- |
| Y | Verify in-situ concrete strength prior to stressing of tendons in post-tensioned concrete and prior to removal of shores and forms from beams and structural slabs. | ---- | X | ACI 318: 6.2 | ---- |
| Y | Inspect formwork for shape, location and dimensions of the concrete member being formed. | ---- | X | ACI 318: 6.1.1 | ---- |

| STEEL -- Special Inspection and Verification (1704.3) |
| --- |
| Special Inspection Required Y/N | Verification and Inspection Task | Inspection Frequency | Reference for Criteria |
|  |  | Continuous During Task Listed | Periodically During Task Listed | Referenced Standard | IBC Reference |
|  | [DPIRC Note: See 1704.3 for exceptions] |  |
|  | Material Verification of High-Strength Bolts, Nuts and Washers: |
| Y | a. Identification markings conform to ASTM Standards specified in the approved construction documents. | ---- | X | AISC 360, Sec. A3.3 and Applicable ASTM Material Standards | ---- |
| Y | b. Manufacturer's certificate of compliance received and acceptable. | ---- | X | ---- | ---- |
|  | Inspection of High-Strength Bolting: |
| Y | a. Snug-tight joints. | ---- | X | AISC 360, Section M2.5 | 1704.3.3 |
| Y | b. Pretensioned and slip-critical joints using turn-of-nut match-marking, twist-off bolt, or direct tension indicator methods of installation. | ---- | X |  |  |
| Y | c. Pretensioned and slip-critical joints using turn-of-nut without matchmarking or calibrated wrench methods of installation. | X | ---- |  |  |
|  | Material Verification of Structural Steel and Cold-Formed Steel Deck: |
| Y | a. For structural steel, identification markings to conform to AISC 360 | ---- | X | AISC 360, Sec. M5.5 | ---- |
| Y | b. For other steel, identification markings to conform to ASTM Standards specified in the approved construction documents. | ---- | X | Applicable ASTM Material Standards | ---- |
| Y | c. Manufacturer's certified test reports. | ---- | X | ---- | ---- |
|  | Material Verification of Weld Filler Materials: |
| Y | a. Identification markings to conform to AWS specification in the approved construction documents. | ---- | X | AISC 360, Sec. A3.5 and Applicable AWS A5 Documents | ---- |
| Y | b. Manufacturer's certification of compliance required. | ---- | X | ---- | ---- |
|  | Subcontractor Scope NDE (3rd party): Inspection of Welding: |
|  | a. Structural Steel and Cold Formed Steel Deck: |
| Y | Complete and partial joint penetration groove welds. | X | ---- | AWS D1.1 | 1704.3.1 |
| Y | Multipass fillet welds. | X | ---- |  |  |
| Y | Single-pass fillet welds > 5/16". | X | ---- |  |  |
| Y | Plug and slot welds. | X | ---- |  |  |
| Y | Single-pass fillet welds ≤ 5/16". | ---- | X |  |  |
| Y | Floor and roof deck welds. | ---- | X | AWS D1.3 | ---- |
| Y | Welded Studs when used for structural diaphragm. | ---- | X | ---- | 1704.3 2.3 |
| Y | Welded sheet steel for cold-formed steel members. | ---- | X | ---- | 1704.3 2.4 |
| Y | Welding of stairs and railing systems. | ---- | X | ---- | 1704.3 2.5 |
|  | b. Steel Headed Shear Studs (Type B studs in composite beam construction): |
| Y | Qualification of weld application procedure. | X | ---- | AWS D1.1 Sec. 7.6 | ---- |
| Y | Stud size and count. | ---- | X | ---- | ---- |
| Y | Stud location on beam and within deck valleys. | ---- | X | AWS D1.1 AISC 360 P. 16.1-88 | ---- |
| Y | Weld verification. | ---- | X | AWS D1.1 Sec. 7.8 | ---- |
|  | c. Reinforcing Steel: |
| Y | Weldability of reinforcing steel other than ASTM A 706. | ---- | X | AWS D1.4 ACI 318: Sec. 3.5.2 | ---- |
| Y | Reinforcing steel resisting flexural and axial forces in intermediate and special moment frames, and boundary elements of special structural walls of concrete and shear reinforcement. | X | ---- |  |  |
| Y | Shear reinforcement. | X | ---- |  |  |
| Y | Other reinforcing steel. | ---- | X |  |  |
|  | Inspection of Steel Frame Joint Details for compliance: |
| Y | Details such as bracing and stiffening. | ---- | X | ---- | 1704.3.2 |
| Y | Member Locations. | ---- | X |  |  |
| Y | Application of joint details at each connection. | ---- | X |  |  |
| COLD FORMED STEEL FRAMING -- Special Inspection and Verification (1704.3.4) |
| Special Inspection Required Y/N | Verification and Inspection Task | Inspection Frequency | Reference for Criteria |
|  |  | Continuous During Task Listed | Periodically During Task Listed | IBC Reference |
| Y | Structural stud size and gauge. | ---- | X | * |
| Y | Proper seating of studs in track. | ---- | X | * |
| Y | Stud header size, gauge, and construction per structural drawings. | ---- | X | * |
| Y | Screw attachments, bolting, anchoring, and other fastening of components per structural drawings. | ---- | X | * |
| Y | Welding of elements per structural drawings. | ---- | X | * |
| Y | Steel stud bridging spacing and end attachment. | ---- | X | * |
| Y | Shear wall strap size, location and welding per structural drawings. | ---- | X | * |
| Y | Shear wall anchorage and diaphragm connection per structural drawings. | ---- | X | * |
| Y | Where a cold-formed steel truss clear span is 60 feet or greater, verify that the temporary installation restraint/bracing and the permanent individual truss member restraint/bracing are installed in accordance with the approved truss submittal package. | ---- | X | 1704.3.4 |
| * = Above and beyond IBC 2009 requirements. |  |  |  |  |

| MASONRY - LEVEL #1 -- Special Inspection and Verification (2104-2105) |
| --- |
| Special Inspection Required Y/N | Verification and Inspection Task | Inspection Frequency | Reference for Criteria |
|  |  | Continuous During Task Listed | Periodically During Task Listed | IBC Ref. | TMS 402/ACI 530/ASCE 5 | TMS 602/ACI 530.1/ASCE 6 |
| Y | Compliance with required inspection provisions of the construction documents and the approved submittals. | ---- | X | ---- | ---- | Art. 1.5 |
| Y | Verification of f'm and f'aac prior to construction except where specifically exempted by this code. | ---- | X | ---- | ---- | Art. 1.4B |
| Y | Verification of slump flow and VSI as delivered to the site for self-consolidating grout. | X | ---- | ---- | ---- | Art. 1.5B.1.b.3 |
|  | As Masonry Construction Begins, verify the following: |
| Y | Proportions of site-prepared mortar. | ---- | X | ---- | ---- | Art. 2.6A |
| Y | Construction of mortar joints. | ---- | X | ---- | ---- | Art. 3.3B |
| Y | Location of reinforcement, connectors, prestressing tendons and anchorages. | ---- | X | ---- | ---- | Art. 3.4, 3.6A |
| Y | Prestressing techniques. | ---- | X | ---- | ---- | Art. 3.6B |
| Y | Grade and size of prestressing tendons and anchorages. | ---- | X | ---- | ---- | Art. 2.4B, 2.4H |
|  | During Construction verify: |
| Y | Size and location of structural elements. | ---- | X | ---- | ---- | Art. 3.3F |
| Y | Type, size and location of anchors, including other details of anchorage of masonry to structural members, frames, or other construction. | ---- | X | ---- | Sec. 1.2.2(e), 1.16.1 | ---- |
| Y | Specified size, grade, and type of reinforcement, anchor bolts, prestressing tendons and anchorages. | ---- | X | ---- | Sec. 1.15 | Art. 2.4, 3.4 |
| Y | Welding of reinforcing bars. | X | ---- | ---- | Sec. 2.1.9.7.2, 3.3.3.4(b) | ---- |
| Y | Preparation, construction, and protection of masonry during cold weather (temperature below 40°F) or hot weather (temperature above 90°F). | ---- | X | 2104.3, 2104.4 | ---- | Art. 1.8C, 1.8D |
| Y | Application and measurement of prestressing force. | X | ---- | ---- | ---- | Art. 3.6B |
|  | Prior to grouting, verify: |
| Y | Grout space is clean. | ---- | X | --- | ---- | Art. 3.2D |
| Y | Placement of reinforcement and connectors, and prestressing tendons and anchorages. | ---- | X | --- | Sec. 1.13 | Art. 3.4 |
| Y | Proportions of site-prepared grout and prestressing grout for bonded tendons. | ---- | X | --- | ---- | Art. 2.6B |
| Y | Construction of mortar joints. | ---- | X | --- | ---- | Art. 3.3B |
| Y | Specified reinforcing bar laps for vertical and horizontal bars. | ---- |  | --- | ---- | ---- |
| Y | Cleanouts are present at base of grouted cells for high lift grouting. | ---- | X | --- | ---- | ---- |
| Y | Cell perimeter to insure excess mortar has been removed from inside of cell prior to high lift grouting. | ---- | X | --- | ---- | ---- |
| Y | Grout placement: | X | ---- | --- | ---- | Art. 3.5 |
| Y | Grouting of prestressing bonded tendons. | X | ---- | --- | ---- | Art. 3.6C |
| Y | Subcontractor Scope Tests (3rd party): Preparation, observation, and testing of any required grout specimens and/or prisms. | ---- | X | Sec. 2105.2.2, 2105.3 | ---- | Art. 1.4 |

| MASONRY - LEVEL #2 -- Special Inspection and Verification (2104-2105) |
| --- |
| Special Inspection Required Y/N | Verification and Inspection Task | Inspection Frequency | Reference for Criteria |
|  |  | Continuous During Task Listed | Periodically During Task Listed | IBC Ref. | TMS 402/ACI 530/ASCE 5 | TMS 602/ACI 530.1/ASCE 6 |
| Y | Compliance with required inspection provisions of the construction documents and the approved submittals. | ---- | X | ---- | ---- | Art. 1.5 |
| Y | Verification of f'm and f'aac prior to construction and for every 5000 square feet during construction. | ---- | X | ---- | ---- | Art. 1.4B |
| Y | Verification of proportions of materials in premixed or preblended mortar and grout as delivered to the site. | ---- | X | ---- | ---- | Art. 1.5B |
| Y | Verification of slump flow and VSI as delivered to the site for self-consolidating grout. | X | ---- | ---- | ---- | Art. 1.5B.1.b.3 |
|  | Verify the following: |
| Y | Proportions of site-prepared mortar, grout and prestressing grout for bonded tendons. | ---- | X | ---- | ---- | Art. 2.6A |
| Y | Placement of masonry units and construction of mortar joints. | ---- | X | ---- | ---- | Art. 3.3B |
| Y | Placement of reinforcement, connectors, prestressing tendons and anchorages. | ---- | X | ---- | Sec. 1.15 | Art. 3.4, 3.6A |
| Y | Grout space prior to grout. | X | ---- | ---- | ---- | Art. 3.2D |
| Y | Placement of grout. | X | ---- | ---- | ---- | Art. 3.5 |
| Y | Placement of prestressing grout. | X | ---- | ---- | ---- | Art. 3.6C |
| Y | Size and location of structural elements. | ---- | X | ---- | ---- | Art. 3.3F |
| Y | Type, size and location of anchors, including other details of anchorage of masonry to structural members, frames or other construction. | X | ---- | ---- | Sec. 1.2.2(e), 1.16.1 | ---- |
| Y | Specified size, grade and type of reinforcement, anchor bolts, prestressing tendons and anchorages. | ---- | X | ---- | Sec. 1.15 | Art. 2.4, 3.4 |
| Y | Welding of reinforcing bars. | X | ---- | ---- | Sec. 2.1.9.7.2, 3.3.3.4(b) | ---- |
| Y | Preparation, construction, and protection of masonry during cold weather (temperature below 40°F) or hot weather (temperature above 90°F). | ---- | X | 2104.3, 2104.4 | ---- | Art. 1.8C, 1.8D |
| Y | Application and measurement of prestressing force. | X | ---- | ---- | ---- | Art. 3.6B |
| Y | Specified Reinforcing bar laps for vertical and horizontal bars. | ---- | X | ---- | ---- | ---- |
| Y | Cleanouts are present at base of grouted cells for high lift grouting. | ---- | X | ---- | ---- | ---- |
| Y | Cell perimeter to insure excess mortar has been removed from inside of cell prior to high lift grouting. | ---- | X | ---- | ---- | ---- |
| Y | Subcontractor Scope Tests (3rd party): Preparation, observation, and testing of any required grout specimens and/or prisms. | X | ---- | 2105.2.2, 2105.3 | ---- | Art. 1.4 |

| WOOD -- Special Inspection and Verification (1704) |
| --- |
| Special Inspection Required Y/N | Verification and Inspection Task | Inspection Frequency | Reference for Criteria |
|  |  | Continuous During Task Listed | Periodically During Task Listed | IBC Reference |
| Y | Fabrication process of prefabricated wood structural elements and assemblies per Section 1704.2. | ---- | X | 1704.6, 1704.2 |
|  | High Load Diaphragms: |
| Y | Inspect the wood structural panel sheathing to ascertain whether it is of the grade and thickness shown on the approved building plans. | ---- | X | 1704.6.1 |
| Y | Verify the nominal size of framing members at adjoining panel edges, the nail or staple diameter and length, the number of fastener lines and that the spacing between fasteners in each line and at edge margins agrees with the approved building plans. | ---- | X | 1704.6.1 |
|  | Metal-plate-connected Wood Truss (spanning 60 ft or greater): |
| Y | Verify that the temporary installation restraint/bracing and the permanent individual truss member restraints/bracing are installed in accordance with the approved truss submittal package. | ---- | X | 1704.6.2 |

| SPRAYED FIRE-RESISTANT MATERIALS -- Special Inspection and Verification (1704.12) |
| --- |
| Special Inspection Required Y/N | Verification and Inspection Task | Inspection Frequency | Reference for Criteria |
|  |  | Continuous During Task Listed | Periodically During Task Listed | Referenced Standard | IBC Reference |
| Y | Sprayed fire-resistant materials applied to floor, roof and wall assemblies and structural members per Sections 1704.12.1 through 1704.12.6, performed after the rough installation of electrical, automatic sprinkler, mechanical and plumbing systems and suspension systems for ceilings, where applicable. | ---- | X | ---- | 1704.12 |
|  | Perform the following visual and physical tests: |
| Y | Condition of substrates | ---- | X | ---- | 1704.12.1 |
|  | Thickness of application |  |  |  |  |
|  | Density in pounds per cubic foot |  |  |  |  |
|  | Bond strength adhesion/cohesion |  |  |  |  |
|  | Condition of finished application |  |  |  |  |

| MASTIC AND INTUMESCENT FIRE-RESISTANT COATINGS -- Special Inspection and Verification (1704.13) |
| --- |
| Special Inspection Required Y/N | Verification and Inspection Task | Inspection Frequency | Criteria Reference |
|  |  | Continuous During Task Listed | Periodically During Task Listed | Referenced Standard | IBC Reference |
| Y | Coatings applied to structural elements and decks in accordance with AWCI 12-B. | ---- | X | AWCI 12-B | 1704.13 |

| EXTERIOR INSULATION AND FINISH SYSTEMS (EIFS) -- Special Inspection and Verification (1704.14) |
| --- |
| Special Inspection Required Y/N | Verification and Inspection Task | Inspection Frequency | Reference for Criteria |
|  |  | Continuous During Task Listed | Periodically During Task Listed | Referenced Standard | IBC Reference |
| Y | Required for all EIFS applications. [DPIRC Note: See 1704.14 for exceptions] | ---- | X | ---- | 1704.14 |
| Y | Water-resistive barrier coating complying with ASTM E 2570 requires special inspection of the water-resistive barrier coating when installed over sheathing substrate. | ---- | X | ASTM E 2570 | 1704.14.1 |

**********************************************************************************************************************************************************************

“Special Cases as Required by LANL Building Official” table shall be filled out for each specific Special Cases building component in accordance with their respective ICC-ES report or similar LBO-approved basis.  (n/a for post-installed anchors already in Concrete table).

**********************************************************************************************************************************************************************

| SPECIAL CASES AS REQUIRED BY LANL BUILDING OFFICIAL -- Special Inspection and Verification (1704.15) |
| --- |
| Special Inspection Required Y/N | Verification and Inspection Task | Inspection Frequency | Reference for Criteria |
|  |  | Continuous During Task Listed | Periodically During Task Listed | Referenced Standard | IBC Reference |
| Y | Required for proposed work that is, in the opinion of the building official, unusual in its nature, such as, but not limited to the following examples: | ---- | ---- | LANL ESM (STD-342-100) Ch. 16 Sect. IBC-GEN (8.0 in Rev.7) | 1704.15 |
|  | Construction materials and systems that are alternatives to materials and systems prescribed in IBC 2009. | ---- | ---- |  |  |
|  | Unusual design applications of materials described in IBC 2009. | ---- | ---- |  |  |
|  | Materials and systems required to be installed in accordance with additional manufacturer's instructions that prescribe requirements not contained in the IBC 2009. | ---- | ---- |  |  |
| Y | Any roofing work more than patching less than 10% of total (true repair) except when managed by DOE central initiative (e.g., RAMP, BTA) |  | X |  | Ch. 15 |

| SMOKE CONTROL -- Special Inspection and Verification (1704.16) |
| --- |
| Special Inspection Required Y/N | Verification and Inspection Task | Inspection Frequency | Reference for Criteria |
|  |  | Continuous During Task Listed | Periodically During Task Listed | Referenced Standard | IBC Reference |
|  | Smoke Control Testing Scope: |
| Y | During erection of ductwork and prior to concealment for the purpose of leakage testing and recording of device location. | ---- | ---- | ---- | 1704.16.1 |
|  | Prior to occupancy and after sufficient completion for the purpose of pressure difference testing, flow measurements and detection and control verification. |  |  |  |  |

# Instructions – Preparation of the Statement of Special Inspections

- Who Prepares the Plan:

The program of special inspection and testing for a project shall be prepared by the Design Professional in Responsible Charge (DPIRC) that is in responsible charge of the building system requiring inspections and testing.  The Structural Engineer of Record (SER) should prepare the sections required for the structural elements such as foundations, concrete, structural steel, etc.  The Architect and MEP Engineers of Record should prepare the corresponding sections of the SSI for the building systems that they are responsible for, etc.  For further explanation, refer to LANL ESM Chapter 16, Section IBC-IP.

- The Front Page:

2-1.	At the top of the page indicate the project name and location as they appear on the Contract Documents, and indicate the Design Professional in Responsible Charge.  This should be the DPIRC in responsible charge of the building systems for which this SSI is being prepared.  See explanation in item 1 above.

2-2.	Next, read the first paragraph and check the box below indicating the discipline(s) that this SSI will encompass (Structural, Architectural, Mechanical/Electrical/ Plumbing, or Other).

2-3.	Near the bottom of the page, the DPIRC must print, sign, and date the form, and stamp the form with their professional seal in the box provided.

2-4.	LANL must sign and date the front page after the SSI has been completed by the DPIRC.

2-5.	LANL must sign and date the form upon acceptance.

- Page 2 – Schedule of Inspection and Testing Agencies:

3-1.	The top of the page lists all of the categories of building systems with a box next to each.  The DPIRC must check the boxes for only the building systems that are going to be covered in this SSI.  A completed inspection program page must be attached for each building system that is checked off.  (See instruction #5 below.)

- Page 3 – Seismic resisting systems Statement of Responsibility:

4-1.	The DPIRC must review sections 1705 in Chapter 17 of the IBC to determine if the project requires a Statement of Responsibility from the Subcontractor for the seismic force-resisting systems and components.  See also ESM Ch 5, Structural.

4-2.	The DPIRC must indicate whether or not a Statement of Responsibility is required by filling in the information requested on the page.  It is only necessary to provide descriptions of the seismic force-resisting systems if it is determined that a Statement of Responsibility is required.

- Inspection Program Pages for Each Building System:

5-1.	There is a page attached for each building system where the DPIRC identifies the inspection requirements of each system.  Fill out the pages for only the building systems included in this SSI.  Do not include blank pages for building systems not covered under this SSI.

5-2. 	The Special Inspection Requirement of each inspection must be filled in Y/N by the DPIRC. The verification and inspection task is the mandated minimum inspection requirements designated by the IBC Chapter 17. The DPIRC must determine if the project falls under the requirements of Sections 1704 to 1708 and add the required inspections to the building systems.  The final scope of the inspections required for the project must be determined by the DPIRC but shall not be less than those required by IBC Chapter 17.

5-3.	Descriptions of all inspections must include the required frequency of each inspection or test (continuous, periodic).

5-4.	Notes of clarification may be included below the relevant building systems table.

Statement of Special Inspections

Appendix A

QUALITY CONTROL AND QUALITY ASSURANCE PLAN

FOR SEISMIC FORCE RESISTING SYSTEMS

based on AISC 341-10

This appendix addresses requirements for quality control and quality assurance.

User Note: All requirements of AISC 341-10 apply, as do references therein to AISC 360-10 Chapter N or equivalent, unless specifically modified by this plan.

This attachment is organized as follows:

- Scope

- Fabricator and Erector Documents

- Quality Assurance Agency Documents

- Inspection and Nondestructive Testing Personnel

- Inspection Tasks

- Welding Inspection and Nondestructive Testing

- Inspection of High-Strength Bolting

- Other Steel Structure Inspections

- Inspection of Composite Structures

- Inspection of Piling

TERMS

| EOR | Engineer of record. Whenever term is used, EOR’s designee is also acceptable. |
| --- | --- |
| IBC | International Building Code, as amended by LANL |
| LBO | LANL Building Official |
| NDT | nondestructive testing |
| QA | quality assurance |
| QC | quality control |
| SFRS | seismic force resisting system |
| AISC 360 | AISC Specification for Structural Steel Buildings (ANSI/AISC 360) |

Italics are used to highlight titles or terms defined by the IBC or AISC 341.

In tables, P = perform, O = observe, and D = document (per J5 1-3)

J1. 	SCOPE

Quality Control (QC) as specified in this attachment shall be provided by the fabricator, erector or other responsible Subcontractor as applicable. Quality Assurance (QA) as specified in this attachment shall be provided by others when required by the LANL Building Official (LBO), International Building Code (IBC), or engineer of record (EOR). Nondestructive testing (NDT) shall be performed by the LBO-approved testing agency retained by the Subcontractor or Subtiers, except as permitted LBO in accordance with AISC 360 Section N7.

User Note: The quality assurance plan of this section is considered adequate and effective for most seismic force resisting systems (SFRS) and should be used without modification. The quality assurance plan is intended to ensure that the SFRS is significantly free of defects that would greatly reduce the ductility of the system. There may be cases (for example, non-redundant major transfer members, or where work is performed in a location that is difficult to access) where supplemental testing might be advisable. Additionally, where the fabricator’s or erector’s quality control program has demonstrated the capability to perform some tasks this plan has assigned to quality assurance, modification of the plan could be considered.

J2. FABRICATOR AND ERECTOR DOCUMENTS

- Documents to be Submitted for Steel Construction

In addition to the requirements of AISC 360 Section N3.1, the following documents shall be submitted for review by the EOR prior to fabrication or erection of the affected work, as applicable:

- Welding procedure specifications (WPS)

- Copies of the manufacturer’s typical certificate of conformance for all electrodes, fluxes and shielding gasses to be used

- For demand critical welds, applicable manufacturer’s certifications that the filler metal meets the supplemental notch toughness requirements, as applicable. Should the filler metal manufacturer not supply such supplemental certifications, the fabricator or erector, as applicable, shall have the necessary testing performed and provide the applicable test reports

- Manufacturer’s product data sheets or catalog data for SMAW, FCAW and GMAW composite (cored) filler metals to be used

- Bolt installation procedures

- Specific assembly order, welding sequence, welding technique, or other special precautions for joints or groups of joints where such items are designated to be submitted to the EOR.

- Documents to be Available for Review for Steel Construction

Additional documents as required by the EOR in the Subcontract documents shall be available by the fabricator and erector for review by the EOR prior to fabrication or erection, as applicable.

The fabricator and erector shall retain their document(s) for at least one year after substantial completion of construction.

- Documents to be Submitted for Composite Construction

The following documents shall be submitted by the responsible Subcontractor for review by the EOR prior to concrete production or placement, as applicable:

- Concrete mix design and test reports for the mix design

- Reinforcing steel shop drawings

- Concrete placement sequences, techniques and restriction

- Documents to be Available for Review for Composite Construction

The following documents shall be available from the responsible Subcontractor for review by the EOR prior to fabrication or erection, as applicable, unless specified to be submitted:

- Material test reports for reinforcing steel

- Inspection procedures

- Nonconformance procedure

- Material control procedure

- Welder performance qualification records (WPQR) as required by AWS D1.4/D1.4M

- QC Inspector qualifications

The responsible Subcontractor shall retain their document(s) for at least one year after substantial completion of construction.

J3. 	QUALITY ASSURANCE AGENCY DOCUMENTS

The agency responsible for quality assurance (QA) shall submit the following documents to the EOR and LBO for approval:

- QA agency’s written practices for the monitoring and control of the agency’s operations. The written practice shall include:

- The agency’s procedures for the selection and administration of inspection personnel, describing the training, experience and examination requirements for qualification and certification of inspection personnel, and

- The agency’s inspection procedures, including general inspection, material controls, and visual welding inspection

- Qualifications of management and QA personnel designated for the project

- Qualification records for inspectors and NDT technicians designated for the project

- NDT procedures and equipment calibration records for NDT to be performed and equipment to be used for the project

- For composite construction, concrete testing procedures and equipment

J4. 	INSPECTION AND NONDESTRUCTIVE TESTING PERSONNEL

In addition to the requirements of AISC 360 Sections N4.1 and N4.2, visual welding inspection and nondestructive testing (NDT) shall be conducted by personnel qualified in accordance with AWS D1.8/D1.8M clause 7.2.  In addition to the requirements of AISC 360 Section N4.3, ultrasonic testing technicians shall be qualified in accordance with AWS D1.8/D1.8M clause 7.2.4.

J5. 	INSPECTION TASKS

Inspection tasks and documentation for quality control (QC) and QA for the seismic force resisting system (SFRS) shall be as provided in the tables in Sections J6, J7, J8, J9, and J10. The following entries are used in the tables:

- Observe (O)

The inspector shall observe these functions on a random, daily basis. Operations need not be delayed pending observations.

- Perform (P)

These inspections shall be performed prior to the final acceptance of the item.

- Document (D)

The inspector shall prepare reports indicating that the work has been performed in accordance with the Subcontract documents. The report need not provide detailed measurements for joint fit-up, WPS settings, completed welds, or other individual items listed in the tables. For shop fabrication, the report shall indicate the piece mark of the piece inspected. For field work, the report shall indicate the reference grid lines and floor or elevation inspected. Work not in compliance with the Subcontract documents and whether the noncompliance has been satisfactorily repaired shall be noted in the inspection report.

- Coordinated Inspection

Where a task is noted to be performed by both QC and QA, coordination of the inspection function between QC and QA is permitted in accordance with AISC 360 Section N5.3.

J6. 	WELDING INSPECTION AND NONDESTRUCTIVE TESTING

Welding inspection and nondestructive testing shall satisfy the requirements of AISC 360, this section and AWS D1.8/D1.8M.

User Note: AWS D1.8/D1.8M was specifically written to provide additional requirements for the welding of SFRS, and has been coordinated when possible with this plan. AWS D1.8/D1.8M requirements related to inspection and nondestructive testing are organized as follows, including normative (mandatory) annexes: 1. General Requirements 7. Inspection Annex F. Supplemental Ultrasonic Technician Testing Annex G. Supplemental Magnetic Particle Testing Procedures Annex H. Flaw Sizing by Ultrasonic Testing

1.	Visual Welding Inspection

All requirements of AISC 360 shall apply, except as specifically modified by AWS D1.8/D1.8M.

Visual welding inspection shall be performed by both QC and QA personnel. As a minimum, tasks shall be as listed in Tables J6-1, J6-2, and J6-3.

| TABLE J6-1 Visual Inspection Tasks Prior to Welding |
| --- |
| Visual Inspection Tasks Prior to Welding | QC | QA |
|  | Task | Doc. | Task | Doc. |
| Material identification (Type/Grade) | O | – | O | – |
| Welder identification system | O | – | O | – |
| Fit-up of Groove Welds (including joint geometry) - Joint preparation - Dimensions (alignment, root opening, root face, bevel) - Cleanliness (condition of steel surfaces) - Tacking (tack weld quality and location) - Backing type and fit (if applicable) | P/O** | – | O | – |
| Configuration and finish of access holes | O | – | O | – |
| Fit-up of Fillet Welds - Dimensions (alignment, gaps at root) - Cleanliness (condition of steel surfaces) - Tacking (tack weld quality and location) | P/O** | – | O | – |
| ** Following performance of this inspection task for ten welds to be made by a given welder, with the welder demonstrating understanding of requirements and possession of skills and tools to verify these items, the Perform designation of this task shall be reduced to Observe, and the welder shall perform this task. Should the inspector determine that the welder has discontinued performance of this task, the task shall be returned to Perform until such time as the Inspector has re-established adequate assurance that the welder will perform the inspection tasks listed. |

| TABLE J6-2 Visual Inspection Tasks During Welding |
| --- |
| Visual Inspection Tasks During Welding | QC | QA |
|  | Task | Doc. | Task | Doc. |
| WPS followed - Settings on welding equipment - Travel speed - Selected welding materials - Shielding gas type/flow rate - Preheat applied - Interpass temperature maintained (min/max.) - Proper position (F, V, H, OH) - Intermix of filler metals avoided unless approved | O | – | O | – |
| Use of qualified welders | O | – | O | – |
| Control and handling of welding consumables - Packaging - Exposure control | O | – | O | – |
| Environmental conditions - Wind speed within limits - Precipitation and temperature | O | – | O | – |
| Welding techniques - Interpass and final cleaning - Each pass within profile limitations - Each pass meets quality requirements | O | – | O | – |
| No welding over cracked tacks | O | – | O | – |

| TABLE J6-3 Visual Inspection Tasks After Welding |
| --- |
| Visual Inspection Tasks After Welding | QC | QA |
|  | Task | Doc. | Task | Doc. |
| Welds cleaned | O | – | O | – |
| Size, length, and location of welds | P | – | P | – |
| Welds meet visual acceptance criteria - Crack prohibition - Weld/base-metal fusion - Crater cross section - Weld profiles and size - Undercut - Porosity | P | D | P | D |
| Placement of reinforcing or contouring fillet welds (if required) | P | D | P | D |
| Backing removed, weld tabs removed and finished, and fillet welds added (if required) | P | D | P | D |
| Repair activities | P | – | P | D |

2.	NDT of Welded Joints

In addition to the requirements of AISC 360 Section N4.5, nondestructive testing of welded joints shall be as required in this section:

- k-Area NDT

Where welding of doubler plates, continuity plates, or stiffeners has been performed in the k-area, the web shall be tested for cracks using magnetic particle testing (MT).  The MT inspection area shall include the k-area base metal within 3 in. (75 mm) of the weld.  The MT shall be performed no sooner than 48 hours following completion of the welding.

- CJP Groove Weld NDT

Ultrasonic testing (UT) shall be performed on 100% of CJP groove welds in materials 5/16 in. (8 mm) thick or greater. Ultrasonic testing in materials less than 5/16 in. (8 mm) thick is not required. Weld discontinuities shall be accepted or rejected on the basis of criteria of AWS D1.1/D1.1M Table 6.2. Magnetic particle testing shall be performed on 25% of all beam-to-column CJP groove welds. The rate of UT and MT is permitted to be reduced in accordance with Sections J6.2g and J6.2h, respectively.

Exception: For ordinary moment frames, UT and MT of CJP groove welds are required only for demand critical welds.

- Base Metal NDT for Lamellar Tearing and Laminations

After joint completion, base metal thicker than 11/2 in. (38 mm) loaded in tension in the through-thickness direction in tee and corner joints, where the connected material is greater than 3/4 in. (19 mm) and contains CJP groove welds, shall be ultrasonically tested for discontinuities behind and adjacent to the fusion line of such welds. Any base metal discontinuities found within t/4 of the steel surface shall be accepted or rejected on the basis of criteria of AWS D1.1/D1.1M Table 6.2, where t is the thickness of the part subjected to the through-thickness strain.

- Beam Cope and Access Hole NDT

At welded splices and connections, thermally cut surfaces of beam copes and access holes shall be tested using magnetic particle testing or penetrant testing, when the flange thickness exceeds 1-1/2 in. (38 mm) for rolled shapes, or when the web thickness exceeds 11/2 in. (38 mm) for built-up shapes.

- Reduced Beam Section Repair NDT

Magnetic particle testing shall be performed on any weld and adjacent area of the reduced beam section (RBS) cut surface that has been repaired by welding, or on the base metal of the RBS cut surface if a sharp notch has been removed by grinding.

- Weld Tab Removal Sites

At the end of welds where weld tabs have been removed, magnetic particle testing shall be performed on the same beam-to-column joints receiving UT as required under Section J6.2b. The rate of MT is permitted to be reduced in accordance with Section J6.2h. MT of continuity plate weld tabs removal sites is not required.

- Reduction of Percentage of Ultrasonic Testing

The reduction of percentage of UT is permitted to be reduced in accordance with AISC 360 Section N5.5e, except no reduction is permitted for demand critical welds.

- Reduction of Percentage of Magnetic Particle Testing

The amount of MT on CJP groove welds is permitted to be reduced if approved by the EOR and LBO Chief Welding Inspector. The MT rate for an individual welder or welding operator is permitted to be reduced to 10%, provided the reject rate is demonstrated to be 5% or less of the welds tested for the welder or welding operator. A sampling of at least 20 completed welds for a job shall be made for such reduction evaluation. Reject rate is the number of welds containing rejectable defects divided by the number of welds completed. This reduction is prohibited on welds in the k-area, at repair sites, backing removal sites, and access holes.

J7.	 INSPECTION OF HIGH-STRENGTH BOLTING

Bolting inspection shall satisfy the requirements of AISC 360 Section N5.6 and this section. Bolting inspection shall be performed by both QC and QA personnel. As a minimum, the tasks shall be as listed in Tables J7-1, J7-2, and J7-3.

| TABLE J7-1 Inspection Tasks Prior to Bolting |
| --- |
| Inspection Tasks Prior to Bolting | QC | QA |
|  | Task | Doc. | Task | Doc. |
| Proper fasteners selected for the joint detail | O | – | O | – |
| Proper bolting procedure selected for joint detail | O | – | O | – |
| Connecting elements, including the appropriate faying surface condition and hole preparation, if specified, meet applicable requirements | O | – | O | – |
| Pre-installation verification testing by installation personnel observed for fastener assemblies and methods used | P | D | O | D |
| Proper storage provided for bolts, nuts, washers and other fastener components | O | – | O | – |

| TABLE J7-2 Inspection Tasks During Bolting |
| --- |
| Inspection Tasks During Bolting | QC | QA |
|  | Task | Doc. | Task | Doc. |
| Fastener assemblies placed in all holes and washers (if required) are positioned as required | O | – | O | – |
| Joint brought to the snug tight condition prior to the pretensioning operation | O | – | O | – |
| Fastener component not turned by the wrench prevented from rotating | O | – | O | – |
| Bolts are pretension progressing systematically from the most rigid point toward the free edges | O | – | O | – |

| TABLE J7-3 Inspection Tasks After Bolting |
| --- |
| Inspection Tasks After Bolting | QC | QA |
|  | Task | Doc. | Task | Doc. |
| Document accepted and rejected connections | P | D | P | D |

- OTHER STEEL STRUCTURE INSPECTIONS

Other inspections of the steel structure shall satisfy the requirements of AISC 360 Section N5.7 and this section. Such inspections shall be performed by both QC and QA personnel. Where applicable, the inspection tasks listed in Table J8- 1 shall be performed.

| TABLE J8-1 Other Inspection Tasks |
| --- |
| Other Inspection Tasks | QC | QA |
|  | Task | Doc. | Task | Doc. |
| RBS requirements, if applicable – Contour and finish – Dimensional tolerances | P | D | P | D |
| Protected zone—no holes and unapproved attachments made by fabricator or erector, as applicable | P | D | P | D |

User Note: The protected zone should be inspected by others following completion of the work of other trades, including those involving curtainwall, mechanical, electrical, plumbing and interior partitions.

- INSPECTION OF COMPOSITE STRUCTURES

Where applicable, inspections of the composite structures shall satisfy the requirements of AISC 360 Section N6 and this section. These inspections shall be performed by the responsible Subcontractor’s QC personnel and by QA personnel.

Where applicable, inspection of structural steel used in composite structures shall comply with the requirements of this Attachment. Where applicable, inspection of reinforced concrete shall comply with the requirements of ACI 318, and inspection of welded reinforcing steel shall comply with the applicable requirements of Section J6.1.

Where applicable to the type of composite construction, the minimum inspection tasks shall be as listed in Tables J9-1, J9-2, and J9-3.

| TABLE J9-1 Inspection of Composite Structures Prior to Concrete Placement |
| --- |
| Inspection of Composite Structures Prior to Concrete Placement | QC | QA |
|  | Task | Doc. | Task | Doc. |
| Material identification of reinforcing steel (Type/Grade) | O | – | O | – |
| Determination of carbon equivalent for reinforcing steel other than ASTM A706 | O | – | O | – |
| Proper reinforcing steel size, spacing and orientation | O | – | O | – |
| Reinforcing steel has not been rebent in the field | O | – | O | – |
| Reinforcing steel has been tied and supported as required | O | – | O | – |
| Required reinforcing steel clearances have been provided | O | – | O | – |
| Composite member has required size | O | – | O | – |

| TABLE J9-2 Inspection of Composite Structures During Concrete Placement |
| --- |
| Inspection of Composite Structures During Concrete Placement | QC | QA |
|  | Task | Doc. | Task | Doc. |
| Concrete: Material identification (mix design, compressive strength, maximum large aggregate size, maximum slump) | O | D | O | D |
| Limits on water added at the truck or pump | O | D | O | D |
| Proper placement techniques to limit segregation | O | – | O | – |

| TABLE J9-3 Inspection of Composite Structures After Concrete Placement |
| --- |
| Inspection of Composite Structures After Concrete Placement | QC | QA |
|  | Task | Doc. | Task | Doc. |
| Achievement of minimum specified concrete compressive strength at specified age | - | D | - | D |

J10. 	INSPECTION OF H-PILES

Where applicable, inspection of piling shall satisfy the requirements of this section. These inspections shall be performed by both the responsible Subcontractor’s QC personnel and by QA personnel. Where applicable, the inspection tasks listed in Table J10-1 shall be performed.

| TABLE J10-1 Inspection of H-Piles |
| --- |
| Inspection of Piling | QC | QA |
|  | Task | Doc. | Task | Doc. |
| Protected zone—no holes and unapproved attachments made by the responsible Subcontractor, as applicable | P | D | P | D |

RECORD OF REVISIONS

(delete from edited document)

| Rev | Date | Description | POC | RM |
| --- | --- | --- | --- | --- |
| 0 | 10/27/06 | Initial issue. | Tobin Oruch, CENG-OFF | Kirk Christensen, CENG-OFF |
| 1 | 6/26/07 | Reformatted | Tobin Oruch, CENG-OFF | Kirk Christensen, CENG-OFF |
| 2 | 7/21/08 | Minor changes. | Tobin Oruch, CENG-OFF | Kirk Christensen, CENG-OFF |
| 3 | 9/15/09 | Added App H (SSRwrtSI) reference. | Tobin Oruch, CENG-OFF | Gary Read, CENG-OFF |
| 4 | 8/25/10 | CM-CE must approve TIP. | Tobin Oruch, CENG-OFF | Larry Goen, CENG-OFF |
| 5 | 3/8/12 | Update for 2009 IBC and addition of AISC 341 QA plan template. | Tobin Oruch, CENG-OFF | Larry Goen, CENG-OFF |
| 6 | 10/31/12 | Improvements, SSI need not include other inspections, strengthened CM-CE approval. | Tobin Oruch, CENG-OFF | Larry Goen, CENG-OFF |
| 7 | 9/24/13 | Moved TIP info out to new Att I template for same. Became Att versus App. | Tobin Oruch, ES-DO | Larry Goen, ES-DO |
| 8 | 5/22/14 | Clarified SI role, template editing, roofing as special case. | Tobin Oruch, ES-DO | Mel Burnett, ES-DO |

# Footnotes

1704.1.2. Goal is to not have any open discrepancies that are turned over to the facility unless it can be shown that the LBO and the engineer-of-record are aware of them and will accept them.