SECTION 01 3545

WATER DISCHARGE REQUIREMENTS

*************************************************************************************************************

LANL MASTER SPECIFICATION

This template must be edited for each project.  In doing so, specifier must add job-specific requirements.  Brackets are used in the text to indicate designer choices or locations where text must be supplied by the designer.  Once the choice is made or text supplied, remove the brackets.  The specifications must also be edited to delete specification requirements for processes, items, or designs that are not included in the project -- and specifier’s notes such as these.   To seek a variance from requirements in the specifications that are applicable, contact the Engineering Standards Manual (ESM) General POC. Please contact POC with suggestions for improvement as well.

When assembling a specification package, include applicable specifications from all Divisions, especially Division 1, General requirements.

Specification developed for ML-4 projects.  For ML-1, 2, and 3 applications, additional requirements and independent reviews should be added if increased confidence in procurement or execution is desired; see ESM Chapter 1, Section Z10 Specifications and Quality sections.

These notes and terminology changed April 2008 administratively (no revision) for ML level and to improve clarity. *************************************************************************************************************

GENERAL

SECTION INCLUDES

Requirements of Subcontractor and LANL Subcontract Technical Representative (STR) when there is a planned or accidental discharge of water, including those not covered by a NPDES permit, Ground Water Discharge Plan, or approved Notice of Intent (NOI).

RELATED SECTIONS

Section 22 0816, Disinfection of Potable Water Piping

DEFINITIONS

Discharge: Release of water to environment or sanitary sewer system due to an accidental spill or planned construction activity, e.g., flushing, piping disinfection, chemical water treatment of piping systems, hydrostatic piping tests, etc.

Best Management Practices (BMPs): Schedules of activities, prohibition of practices, maintenance procedures, and other management practices to prevent or reduce pollution of waters of the United States.  BMPs also include treatment requirements, operating procedures, and practices to control facility site runoff, spillage or leaks, sludge or waste disposal, or drainage from raw material storage. Physical practices to control facility site runoff can be, but are not limited to silt fences, graveled construction area entry/exit points, straw bales, dikes, berms, wattles, ground cover, reduced discharge rates, armoring, or other such methods emplaced to eliminate erosion or transport by water of soil or other contaminants.

SubCONTRACTOR REQUIREMENTS

Discharges to environment:

Discharges shall not cause or have the reasonable potential to cause or contribute to a violation of a water quality standard.

Employ Best Management Practices (BMPs) to prevent erosion from discharge of water.

Chlorinated water used for disinfection shall be dechlorinated with a neutralizing agent per Section 22 0816 prior to discharge.  If discharge is not to a watercourse (e.g., flat ground), then total chlorine concentration shall be reduced to less than 1 ppm (part per million) -- typically the same as that in the Safe Drinking Water Act.

Discharges to a watercourse shall have a total chlorine concentration not greater than 0.011 mg/L (11 parts per billion). (This value is based on 1999 changes in the New Mexico stream standards that dropped chlorine limit from 1 ppm to 11 ppb).

For discharges of less than 5000 gallons, notify LANL STR  at least 48 hours (2 working days) in advance of planned discharge.

For discharges of 5000 gallons or more, notify LANL STR at least 4 working days in advance of planned discharge.

Sanitary Sewer Discharges:

Notify LANL STR prior to any discharge.

Volumes greater than 1000 gallons shall not be discharged into the sanitary sewer systems without special approval by Sanitary Wastewater System (SWWS) Operations (5-7855) obtained via LANL STR.

Properly characterize discharges through LANL waste profile form (WPF) process http://enterprise.lanl.gov/forms/1346.pdf and meet the SWWS Plant Waste Acceptance Criteria (WAC), especially Ch 19.  
http://swo.lanl.gov/Waste%20Acceptance%20Criteria/PLAN-WASTEMGMT-002,R.4.1%20LANL%20Waste%20Acceptance%20Criteria.pdf

a. 	WAC limits for total chlorine concentration are 3 mg/L (3 ppm).  De-chlorinate water used for disinfection in excess of 20 gallons with neutralizing agent per Section 22 0816 prior to discharge.

Notify LANL STR immediately in the event of any accidental discharge.

LANL Subcontract Technical Representative REQUIREMENTS

Discharges to the environment:

Keep a written record of each discharge by project.  Submit records to the LANL Water Quality Group each fiscal year by September 15th, or at closeout of project if sooner.

For discharge of less than 1000 gallons, notify the LANL Water Quality Group (5-0453) 24 hours (1 working day) prior to discharge.

For discharges of 1000 to 5000 gallons, notify the LANL Water Quality Group (5-0453) at least 48 hours (2 working days) in advance for approval of planned discharge.

For discharge of 5000 gallons or more, notify the LANL Water Quality Group (5-0453) at least 72 hours (3 working days) in advance for approval of planned discharge. WQH will coordinate ENV-ECO review for potential impacts to critical habitat and Threatened and Endangered Species.

If project is not covered under a NPDES general permit for storm water discharges for construction activities in Region 6, complete and return attached form “General Discharge Record” to the LANL Water Quality Group.  (Attachment 1)

Sanitary Sewer:

Assist Subcontractor with characterizing discharges using LANL Waste Profile Form (WPF) process and meeting the SWWS Plant Waste Acceptance Criteria (WAC) described in 1.3 above.

Notify SWWS Plant Supervisor (5-7855) at least 48 hours (2 working days) in advance for approval of planned discharge into sanitary waste water system.

Notify the LANL Water Quality Group (5-0453) immediately in the event of any accidental discharge.

PRODUCTS

Not used.

EXECUTION

Not used.

END OF SECTION

*********************************************************

Do not delete the following reference information:

*********************************************************

FOR LANL USE ONLY

This project specification is based on LANL Master Specification 01 3545, Rev. 2, dated April 14, 2008.

## Attachment 1

# SECTION  01 3545

WATER DISCHARGE REQUIREMENTS

### GENERAL DISCHARGE RECORD

|  | LOCATION/ TA: |  | BLDG: |  |  |
| --- | --- | --- | --- | --- | --- |
|  | FIRE HYDRANT # or PIPE: |  |  |
|  | FMU/USER GROUP: |  | CONTACT PERSON: |  |  |
|  | PHONE: |  | PAGER: |  |  |
|  | PERSON CONDUCTING FIRE PROTECTION ACTIVITY: |  |  |
|  | DATE and TIME of DISCHARGE: |  | / |  | AM PM |  |
|  | DURATION of DISCHARGE: |  | / |  |  |
|  | LANL WATER QUALITY CONTACT: |  |  |
|  | DESCRIPTION of DISCHARGE: |  |  |
|  | CANYON AFFECTED: |  |  |
|  | SAMPLES TAKEN: | YES: |  | NO: |  |  |  |
|  | COMMENTS: |  |  |
|  | REVIEWED BY: |  |  |  |  |  |  |
|  |  | Printed Name /LANL Water Quality |  | Signature |  | Date |  |

Revised 07/12/06