SECTION 01 8113

SUSTAINABLE DESIGN

*************************************************************************************************************

LANL MASTER SPECIFICATION

This template must be edited for each project.  In doing so, specifier must add job-specific requirements.  Brackets are used in the text to indicate designer choices or locations where text must be supplied by the designer.  Once the choice is made or text supplied, remove the brackets.  The specifications must also be edited to delete specification requirements for processes, items, or designs that are not included in the project — and specifiers’ notes such as these.  Additional tailoring requirements are contained in ESM Chapter 1 Section Z10 Att. F, Specifications.

To seek a variance from requirements in the specifications that are applicable, contact the Engineering Standards Manual Architectural POC. Please contact POC with suggestions for improvement as well.

This specification applies to projects of Total Estimated Cost > $5 million, in accordance with ESM Chapter 14, or any other project having sustainability goals involved. It should be edited to reflect the project’s general sustainability requirements with specific requirements identified in the individual specification sections.

Specification developed for ML-4 projects.  For ML-1, 2, and 3 applications, additional requirements and independent reviews should be added if increased confidence in procurement or execution is desired; see ESM Ch 1 Section Z10 Specifications and Quality Sections.

*************************************************************************************************************

PART 1 – GENERAL

  - SUMMARY

This Section includes requirements for construction quality assurance and quality control driven, in part, by Engineering Standards Manual Chapter 14 Sustainable Design of Facilities. http://engstandards.lanl.gov/ESM_Chapters.shtml#esm14

- Section includes general requirements and procedures for compliance with certain prerequisites and credits needed for Project to obtain "LEED Version 4 for Building Design and Construction" (LEED v4 BD+C) [Certified] [Silver] [Gold] [Platinum] certification based on USGBC's LEED v4 BD+C.

  - Specific requirements for LEED and sustainable design are also included in other Sections.

  - Some LEED prerequisites and credits needed to obtain LEED certification depend on product selections and may not be specifically identified as LEED requirements. Compliance with requirements needed to obtain LEED prerequisites and credits may be used as one criterion to evaluate substitution requests and comparable product requests.

  - A copy of the LEED Project checklist is attached at the end of this Section for information only.

  - Some LEED prerequisites and credits needed to obtain the indicated LEED certification depend on Architect's design and other aspects of Project that are not part of the Work of the Contract.

  - DEFINITIONS

- LEED: USGBC's "LEED Version 4 for Building Design and Construction."

- Definitions that are a part of "LEED Version 4 for Building Design and Construction" (LEED v4 BD+C) apply to this Section.

- Chain-of-Custody Certificates: Certificates signed by manufacturers certifying that wood used to make products was obtained from forests certified by an FSC-accredited certification body to comply with FSC US Forest Management Standard. Certificates shall include evidence that manufacturer is certified for chain of custody by an FSC-accredited certification body.

- Regional Materials: Materials that have been extracted, harvested, or recovered, as well as manufactured, within 100 miles of Project site. If only a fraction of a product or material is extracted/harvested/recovered and manufactured locally, then only that percentage (by weight) shall contribute to the regional value.

- Recycled Content: The recycled content value of a material assembly shall be determined by weight. The recycled fraction of the assembly is then multiplied by the cost of assembly to determine the recycled content value.

- "Postconsumer" material is defined as waste material generated by households or by commercial, industrial, and institutional facilities in their role as end users of the product, which can no longer be used for its intended purpose.

- "Preconsumer" material is defined as material diverted from the waste stream during the manufacturing process. Excluded is reutilization of materials, such as rework, regrind, or scrap, generated in a process and capable of being reclaimed within the same process that generated it.

  - REFERENCES

- ASTM International:

- ASTM D 5149 - Standard Test Method for Ozone in the Atmosphere: Continuous Measurement by Ethylene Chemiluminescence

- Forest Stewardship Council (FSC) – US Forest Management Standard, Version 1.0.

- United States Green Building Council’s Leadership in Energy and Environmental Design (USGBC’s LEED).

  - ADMINISTRATIVE REQUIREMENTS

- Respond to questions and requests from Architect and the USGBC regarding LEED credits that are the responsibility of the Subcontractor, that depend on product selection or product qualities, or that depend on Subcontractor's procedures until the USGBC has made its determination on the Project's LEED certification application. Document responses as informational submittals.

- Submit documentation to USGBC and respond to questions and requests from USGBC regarding LEED credits that are the responsibility of the Subcontractor, that depend on product selection or product qualities, or that depend on Subcontractor's procedures until the USGBC has made its determination on the Project's LEED certification application.

- Document correspondence with USGBC as informational submittals.

  - CONFLICTING REQUIREMENTS

- General:  If compliance with two or more standards is specified and the standards establish different or conflicting requirements for minimum quantities or quality levels, comply with the most stringent requirement.  Refer uncertainties and requirements that are different, but apparently equal, to STR for a decision before proceeding.

*************************************************************************************************************

Include only sustainable design submittals that are appropriate for the project’s sustainable design goals.

*************************************************************************************************************

  - ACTION SUBMITTALS

  - General: Submit additional sustainable design submittals required by LEED.

  - Sustainable design submittals are in addition to other submittals.

  - If submitted item is identical to that submitted to comply with other requirements that are listed for each individual specification, include an additional copy with other submittal as a record copy of compliance with indicated LEED requirements instead of separate sustainable design submittal. Mark additional copy "Sustainable design submittal."

- Sustainable Design Documentation Submittals:

  - Environmental Product Declarations complying with LEED requirements.

  - Documentation for products that comply with LEED requirements for multi-attribute optimization.

  - Include documentation for regional materials, indicating location and distance from Project of material manufacturer and point of extraction, harvest, or recovery for each raw material and costs of regional materials.

  - Sustainability reports for products that comply with LEED requirements for raw material and source extraction reporting.

  - Documentation for products that comply with LEED requirements for leadership extraction practices. Include the following:

    - Product data and certification letter from product manufacturers, indicating participation in an extended producer responsibility program and statement of costs.

    - Product data and certification for bio-based materials, indicating that they comply with requirements. Include statement of costs.

    - Product data and chain-of-custody certificates for products containing certified wood. Include statement of costs.

    - Receipts for salvaged and refurbished materials used for Project, indicating sources and costs.

    - Product data and certification letter from product manufacturers, indicating percentages by weight of postconsumer and pre-consumer recycled content for products having recycled content. Include statement of costs.

    - Documentation for regional materials, indicating location and distance from Project of material manufacturer and point of extraction, harvest, or recovery for each raw material and costs of regional materials.

  - Material ingredient reports for products that comply with LEED requirements for material ingredient reporting.

  - Documentation for products that comply with LEED requirements for material ingredient optimization.

  - Documentation for products that comply with LEED requirements for product manufacturer supply chain optimization.

    - Include documentation for regional materials, indicating location and distance from Project of material manufacturer and point of extraction, harvest, or recovery for each raw material and costs of regional materials.

  - Product data for adhesives and sealants used inside the weatherproofing system, indicating VOC content and laboratory test reports showing compliance with requirements for low-emitting materials.

  - Product data for paints and coatings used inside the weatherproofing system, indicating VOC content and laboratory test reports showing compliance with requirements for low-emitting materials.

  - Laboratory test reports for flooring, indicating compliance with requirements for low-emitting materials.

  - Laboratory test reports for products containing composite wood or agrifiber products or wood glues, indicating compliance with requirements for low-emitting materials.

  - Laboratory test reports for ceilings, walls, and thermal insulation, indicating compliance with requirements for low-emitting materials.

  - Construction Indoor-Air-Quality (IAQ) Management:

    - Construction IAQ management plan.

    - Product data for temporary filtration media.

    - Product data for filtration media used during occupancy.

    - Construction Documentation: Six photographs at three different times during the construction period, along with a brief description of the SMACNA approach employed, documenting implementation of the IAQ management measures, such as protection of ducts and on-site stored or installed absorptive materials.

  - IAQ Assessment:

    - Signed statement describing the building air flush-out procedures, including the dates when flush-out was begun and completed and statement that filtration media was replaced after flush-out.

    - Product data for filtration media used during flush-out and occupancy.

    - Report from testing and inspecting agency indicating results of IAQ testing and documentation showing compliance with IAQ testing procedures and requirements.

  - INFORMATIONAL SUBMITTALS

- Qualification Data: For LEED coordinator.

- Project Materials Cost Data: Provide statement indicating total cost for materials used for Project. Costs exclude labor, overhead, and profit. Include breakout of costs for the following categories of items:

  - Plumbing.

  - Mechanical.

  - Electrical.

  - Specialty items, such as elevators and equipment.

- Sustainable Design Action Plans: Provide preliminary submittals within [30] <Insert number> days of date established for commencement of the Work, indicating how the following requirements will be met:

  - List of proposed products with Environmental Product Declarations.

  - List of proposed products complying with requirements for multi-attribute optimization.

  - List of proposed products complying with requirements for raw material and source extraction reporting.

  - List of proposed products complying with requirements for leadership extraction practices.

  - List of proposed products complying with requirements for material ingredient reporting.

  - List of proposed products complying with requirements for material ingredient optimization.

  - List of proposed products complying with requirements for product manufacturer supply chain optimization.

  - Waste management plan.

  - Construction IAQ management plan.

- Sustainable Design Progress Reports: Concurrent with each Application for Payment, submit reports comparing actual construction and purchasing activities with sustainable design action plans.

  - QUALITY ASSURANCE

- LEED Coordinator: Engage an experienced LEED-accredited professional to coordinate LEED requirements. LEED coordinator may also serve as waste management coordinator.

PART 2 – PRODUCTS

  - MATERIALS

- Provide products and procedures necessary to obtain LEED credits required in this Section. Although other Sections may specify some requirements that contribute to these LEED credits, the Subcontractor shall provide additional materials and procedures necessary to obtain LEED credits indicated.

- At least 20 different products from at least five different manufacturers shall have Environmental Product Declarations that comply with LEED requirements. Industry-wide (generic) Environmental Product Declarations shall be valued as one-half of a product.

- At least 50 percent, by cost, of the permanently installed products for the Project shall comply with LEED requirements for multi-attribute optimization.

- At least 20 different products from at least five different manufacturers shall have publically released reports that comply with LEED requirements for raw material source and extraction reporting. Self-declared reports by manufacturers shall be valued as one-half of a product.

- At least 20 different products from at least five different manufacturers shall comply with LEED requirements for material ingredient reporting.

- At least 25 percent, by cost, of the permanently installed products for the Project shall comply with LEED requirements for material ingredient optimization.

- At least 25 percent, by cost, of the permanently installed products for the Project shall comply with LEED requirements for product manufacturer supply chain optimization.

- Not less than 25 percent of building materials, by cost, shall comply with LEED requirements for leadership extraction practices.

  - Structure and enclosure materials shall not be more than 30 percent, by cost, of the materials used to comply with this requirement.

- Extended Producer Responsibility Program: Not less than <Insert number> percent of building materials, by cost, shall be manufactured by a participant in an extended producer responsibility program.

- Recycled Content: Building materials shall have recycled content such that postconsumer recycled content plus one-half of pre-consumer recycled content for Project constitutes a minimum of <Insert number> percent of cost of materials used for Project.

  - Cost of postconsumer recycled content plus one-half of pre-consumer recycled content of an item shall be determined by dividing weight of postconsumer recycled content plus one-half of pre-consumer recycled content in the item by total weight of the item and multiplying by cost of the item.

  - Do not include [furniture,] plumbing, mechanical and electrical components, and specialty items, such as elevators and equipment, in the calculation.

- Certified Wood: Not less than <Insert number> percent, by cost, of wood-based materials shall be produced from wood obtained from forests certified by an FSC-accredited certification body to comply with FSC US Forest Management Standard.

  - LOW-EMITTING MATERIALS

- Paints and Coatings: For field applications [that are inside the weatherproofing system], paints and coatings shall comply with VOC content limits of authorities having jurisdiction and the following VOC content limits:

  - Flat Paints and Coatings: 50 g/L.

  - Nonflat Paints and Coatings: 50 g/L.

  - Dry-Fog Coatings: 150 g/L.

  - Primers, Sealers, and Undercoaters: 100 g/L.

  - Rust-Preventive Coatings: 100 g/L.

  - Zinc-Rich Industrial Maintenance Primers: 100 g/L.

  - Pretreatment Wash Primers: 420 g/L.

  - Clear Wood Finishes, Varnishes: 275 g/L.

  - Clear Wood Finishes, Lacquers: 275 g/L.

  - Floor Coatings: 50 g/L.

  - Shellacs, Clear: 730 g/L.

  - Shellacs, Pigmented: 550 g/L.

  - Stains: 100 g/L.

- Paints and Coatings: For field applications that are inside the weatherproofing system, 90 percent of paints and coatings shall comply with the requirements of the California Department of Public Health's "Standard Method for the Testing and Evaluation of Volatile Organic Chemical Emissions from Indoor Sources Using Environmental Chambers."

- Adhesives and Sealants: For field applications [that are inside the weatherproofing system], adhesives and sealants shall comply with VOC content limits of authorities having jurisdiction and the following VOC content limits:

  - Wood Glues: 30 g/L.

  - Metal-to-Metal Adhesives: 30 g/L.

  - Adhesives for Porous Materials (Except Wood): 50 g/L.

  - Subfloor Adhesives: 50 g/L.

  - Plastic Foam Adhesives: 50 g/L.

  - Carpet Adhesives: 50 g/L.

  - Carpet Pad Adhesives: 50 g/L.

  - VCT and Asphalt Tile Adhesives: 50 g/L.

  - Cove Base Adhesives: 50 g/L.

  - Gypsum Board and Panel Adhesives: 50 g/L.

  - Rubber Floor Adhesives: 60 g/L.

  - Ceramic Tile Adhesives: 65 g/L.

  - Multipurpose Construction Adhesives: 70 g/L.

  - Fiberglass Adhesives: 80 g/L.

  - Contact Adhesives: 80 g/L.

  - Structural Glazing Adhesives: 100 g/L.

  - Wood Flooring Adhesives: 100 g/L.

  - Structural Wood Member Adhesives: 140 g/L.

  - Single-Ply Roof Membrane Adhesives: 250 g/L.

  - Special-Purpose Contact Adhesives (That Are Used to Bond Melamine-Covered Board, Metal, Unsupported Vinyl, Rubber, or Wood Veneer 1/16 Inch or Less in Thickness to Any Surface): 250 g/L.

  - Top and Trim Adhesives: 250 g/L.

  - Plastic Cement Welding Compounds: 250 g/L.

  - ABS Welding Compounds: 325 g/L.

  - CPVC Welding Compounds: 490 g/L.

  - PVC Welding Compounds: 510 g/L.

  - Adhesive Primer for Plastic: 550 g/L.

  - Sheet-Applied Rubber Lining Adhesives: 850 g/L.

  - Aerosol Adhesive, General-Purpose Mist Spray: 65 percent by weight.

  - Aerosol Adhesive, General-Purpose Web Spray: 55 percent by weight.

  - Special-Purpose Aerosol Adhesives (All Types): 70 percent by weight.

  - Other Adhesives: 250 g/L.

  - Architectural Sealants: 250 g/L.

  - Nonmembrane Roof Sealants: 300 g/L.

  - Single-Ply Roof Membrane Sealants: 450 g/L.

  - Other Sealants: 420 g/L.

  - Sealant Primers for Nonporous Substrates: 250 g/L.

  - Sealant Primers for Porous Substrates: 775 g/L.

  - Modified Bituminous Sealant Primers: 500 g/L.

  - Other Sealant Primers: 750 g/L.

- Adhesives and Sealants: For field applications that are inside the weatherproofing system, 90 percent of adhesives and sealants shall comply with the requirements of the California Department of Public Health's "Standard Method for the Testing and Evaluation of Volatile Organic Chemical Emissions from Indoor Sources Using Environmental Chambers."

- Flooring: Flooring shall comply with the requirements of the California Department of Public Health's "Standard Method for the Testing and Evaluation of Volatile Organic Chemical Emissions from Indoor Sources Using Environmental Chambers."

- Composite Wood: Composite wood, agrifiber products, and adhesives shall be made using ultra-low-emitting formaldehyde resins as defined in the California Air Resources Board's "Airborne Toxic Control Measure to Reduce Formaldehyde Emissions from Composite Wood Products" or shall be made with no added formaldehyde.

- Ceilings, Walls, and Thermal Insulation: Ceilings, walls, and thermal insulation shall comply with the requirements of the California Department of Public Health's "Standard Method for the Testing and Evaluation of Volatile Organic Chemical Emissions from Indoor Sources Using Environmental Chambers."

PART 3 - EXECUTION

  - NONSMOKING BUILDING

- Smoking is not permitted within the building or within 25 feet (8 m) of entrances, operable windows, or outdoor-air intakes.

  - CONSTRUCTION IAQ MANAGEMENT

- Comply with SMACNA's "SMACNA IAQ Guideline for Occupied Buildings under Construction."

  - If LANL authorizes use of permanent heating, cooling, and ventilating systems during construction period install MERV 8 filter media at each return-air inlet for the air-handling system used during construction.

  - Replace air filters immediately prior to occupancy.

  - IAQ ASSESSMENT

- Flush-Out:

  - After construction ends, prior to occupancy and with all interior finishes installed, perform a building flush-out by supplying a total volume of 14,000 cu. ft. of outdoor air per sq. ft. of floor area while maintaining an internal temperature of at least 60 deg F and a relative humidity no higher than 60 percent.

  - If occupancy is desired prior to flush-out completion, the space may be occupied following delivery of a minimum of 3500 cu. ft. of outdoor air per sq. ft. of floor area to the space. Once a space is occupied, it shall be ventilated at a minimum rate of 0.30 cfm per sq. ft. of outside air or the design minimum outside-air rate, whichever is greater. During each day of the flush-out period, ventilation shall begin a minimum of three hours prior to occupancy and continue during occupancy. These conditions shall be maintained until a total of 14,000 cu. ft. /sq. ft. of outside air has been delivered to the space.

- Air-Quality Testing: [Engage] [LANL will provided] testing agency to perform the following:

  - Conduct baseline IAQ testing, after construction ends and prior to occupancy, using testing protocols consistent with the EPA's "Compendium of Methods for the Determination of Air Pollutants in Indoor Air," and as additionally detailed in the USGBC's "LEED Reference Guide for Building Design and Construction."

  - Demonstrate that the contaminant maximum concentrations listed below are not exceeded:

    - Formaldehyde: 27 ppb.

    - Particulates (PM10): 50 micrograms/cu. m.

    - Ozone: 0.075 ppm, according to ASTM D 5149.

    - Total Volatile Organic Compounds: 500 micrograms/cu. m.

    - 4-Phenylcyclohexene (4-PH): 6.5 micrograms/cu. m.

    - Carbon Monoxide: 9 ppm and no greater than 2 ppm above outdoor levels.

    - Target Chemicals in California Department of Public Health "Standard Method for the Testing and Evaluation of Volatile Organic Chemical Emissions from Indoor Sources Using Environmental Chambers," Table 4-1 (except formaldehyde): Allowable concentrations in California Department of Public Health "Standard Method for the Testing and Evaluation of Volatile Organic Chemical Emissions from Indoor Sources Using Environmental Chambers," Table 4-1.

  - For each sampling point where the maximum concentration limits are exceeded, take corrective action until requirements have been met.

  - Air-sample testing shall be conducted as follows:

    - All measurements shall be conducted prior to occupancy but during normal occupied hours, and with building ventilation system starting at the normal daily start time and operated at the minimum outside-air flow rate for the occupied mode throughout the duration of the air testing.

    - Building shall have all interior finishes installed, including, but not limited to, millwork, doors, paint, carpet, and acoustic tiles. Non-fixed furnishings, such as workstations and partitions, are encouraged, but not required, to be in place for the testing.

    - Number of sampling locations varies depending on the size of building and number of ventilation systems. For each portion of building served by a separate ventilation system, the number of sampling points shall not be less than one per 5000 sq. ft. [For large open spaces, one sampling point per 50,000 sq. ft. may be used.]

    - Air samples shall be collected between 3 and 6 feet from the floor to represent the breathing zone of occupants, and over a minimum four-hour period.

END OF SECTION

************************************************************************************************************

Do not delete the following reference information:

*************************************************************************************************************

THE FOLLOWING REFERENCE IS FOR LANL USE ONLY

This project specification is based on LANL Master Specification 01 8113.13, Rev. 0, dated March 1, 2017.