SECTION 03 3001

REINFORCED CONCRETE

*************************************************************************************************************

LANL MASTER SPECIFICATION

Word file at http://engstandards.lanl.gov

This section applies to structural concrete for buildings that are designed in accordance with ACI 318, facilities classified as Natural Phenomena Hazards Performance Category (PC) 1 or 2 facilities, and ML-3 and ML-4 projects.  In general, this section does not apply to nuclear facilities.  This section may apply to nuclear facilities that, because of the low amount of material at risk, are classified as PC-2.

For nuclear facilities, ML-1 / ML-2 projects (and ML-3 potentially), and PC-3 and 4, this specification must be further amplified and developed.  This would include considering design requirements from DOE STD-1020, ACI 349 as well as ACI 318, and “Quality Assurance Requirements” from 10CFR830.120-122 and 830.200-203, “Safety Basis Requirements.”  Also, use additional quality assurance requirements from DOE G 414.1-1A as applicable.  Independent review would also be required.

When editing to suit project, author shall add job-specific requirements and delete only those portions that in no way apply to the activity (e.g., a component that does not apply).  Note:  Items in brackets are to be added or omitted according to job specific requirements.  To seek a variance from applicable requirements, contact the Engineering Standards Manual (ESM) Structural Specs POC.  Please contact POC with suggestions for improvement as well.

When assembling a specification package, include applicable specifications from all Divisions, especially Division 1, General Requirements.

Delete information within and including “stars” during editing.

*************************************************************************************************************

GENERAL

sECTION INCLUDES

Formwork, shoring, bracing, and anchorage.

Concrete reinforcing and accessories.

Cast-in-place concrete.

Control, expansion, and contraction joint devices associated with concrete work.

DEFINITIONS

“Cementitious material” as used herein shall include all Portland cement, pozzolan, fly ash, [ground iron blast-furnace slag, and silica fume].

Reinforced concrete is structural concrete reinforced with no less than the minimum amounts of prestressing steel or non-prestressed reinforcement specified in ACI 318 Chapters 1 through 21 and Appendices A through C.

Plain concrete is structural concrete with no reinforcement or with less reinforcement than the minimum amount specified for reinforced concrete.  Specifications for plain concrete are presented in Section 03 3053, Miscellaneous Cast-in-Place Concrete.

Engineer-of-record and Architect/Engineer are synonymous and indicate the responsible engineer for the overall design of the facility or project.

REFERENCES

References noted in these specifications form a part of these specifications to the extent applicable.  The publications are referred to in the text by the basic designation only.  The related publishing organizations are stipulated in Section 01 4200, References.

All concrete work, products and materials shall conform to ACI 301 and other specific referenced publications and standards except where otherwise specified herein. The submittals listed in the attached Submittal Tables are those specific submittals that the subcontractor shall provide to LANL.

SUBMITTALS

Submittals that are required to be submitted to LANL are included in the attached Submittal Tables as they apply (including submittals times, unless the LANL Subcontract Technical representative (STR) authorizes changes to the submittal times). Note: All submittals require engineer-of-record approval.  For design-build subcontracts, this approval must occur prior to submittal to LANL.

QUALITY ASSURANCE

- Follow ACI 301, 318, and 347; ACI SP-66; CRSI 63, 65 and Manual of Practice; ANSI/ASTM A184; and DOE Order 414.1 latest version with the exception of those alternatives identified in this specification.

- The work shall be subject to inspection at all times by the Owner and Owner’s Independent Testing Agency for the purpose of determining that the work is properly executed in accordance with this specification.  Failure to detect defective workmanship or material during any interim inspection shall not constitute acceptance of workmanship and materials.

- Acquire cement, aggregate, and fly ash from same source as used to produce the specific mix design for all work.  Formally notify LANL of any material source changes prior to concrete delivery including the test agency test documentation. The subcontractor must provide LANL a certificate of conformance prior to the initial delivery that confirms the source of the constituents, that tests confirm compliance, and that these sources are the same for the mix design testing and the delivered mix.

- Conform to ACI 305R when concreting during hot weather, 306R during cold weather.

- Testing Agency Qualifications:  Testing agencies that perform concrete related testing shall be nationally accredited in accordance with ASTM C1077 and testing agencies that perform reinforcing steel testing shall meet ASTM E329. For field and laboratory testing agencies and testing personnel request approval by the LANL Building Official, or designee, in accordance with the provisions of the IBC and the LANL Engineering Standards Manual Chapter 16.

- Comply with the provisions of ASTM A615 and ASTM A-706 (as applicable) to assure that the manufacturer’s tags have the heat number or test number and these tags are traceable to the associated CMTR(s). In addition, unless specifically authorized by the government, foreign reinforcing steel is not allowed.

- The batch plant must be certified (and maintain current certification) under the NRMCA (National Ready Mix Concrete Association) process.

delivery, storage and handling

Do not deliver concrete until vapor barrier, forms (including confirmation of approved calculations for formwork when required), reinforcement, embedded items, chamfer strips, and any other prerequisites specified in the job specific “Test and Inspection Plan” are in place and ready for concrete placement.  Job site storage of materials shall be in accordance with ACI 301.  Protect materials from contaminants such as grease, oil, and dirt.  Ensure materials can be accurately identified after bundles are broken and tags removed.

Inspection/Documentation Verification Hold Point: Product and raw material inspection shall be performed at time of delivery to site receiving area and prior to off-loading and incorporation into the work.  Verify conformance with specified requirements and project environmental, safety and health (ES&H) and radiological requirements through inspection of material, shipping documentation, material safety data sheets (MSDS) documentation, data sheets, test documentation and other shipping manifest information.  Material not passing inspection shall be marked and prevented from entering the site or placed in an off-site quarantine area until the inspection and verification process is satisfactorily completed.

Reinforcement: Store reinforcement of different sizes and shapes in separate piles on racks raised above the ground (to avoid excessive rusting).  Protect from contaminants such as grease, oil, and dirt.  Ensure bar sizes can be accurately identified after bundles are broken and tags removed. Painting on reinforcement must be approved in writing by the engineer-of-record.

PRODUCTS and materials

  - general

All concrete work, projects and materials shall conform to applicable provisions of ACI 301 except as otherwise specified herein.

FORM MATERIALS AND ACCESSORIES

Smooth-Formed Finished Concrete: Form-facing panels that will provide continuous, true, and smooth concrete surfaces.  Furnish in largest practicable sizes to minimize number of joints

Plywood, metal, or other approved panel materials.

Metal form surfaces shall not contain irregularities, dents, or sags.

Exterior-grade plywood panels, suitable for concrete forms, complying with DOC PS 1, and as follows:

          - High-density overlay, Class 1 or better.

Medium density overlay, Class 1 or better; mill-release agent treated and edge sealed.

Structural 1, B-B or better; mill oiled and edge sealed.

B-B (Concrete Form), Class 1 or better; mill oiled and edge sealed.

AHA A135.4, hardboard for smooth form lining.

Prefabricated forms.

Preformed Steel Forms: Minimum 16 gage matched, tight fitting, stiffened to support weight of concrete without deflection detrimental to tolerances and appearance of finished surfaces.

Glass Fiber Fabric Reinforced Plastic Forms: Matched, tight fitting, stiffened to support weight of concrete without deflection detrimental to tolerances and appearance of finished concrete surfaces.

Pan Type: Glass fiber of size and profile required.

Tubular Column Type: Round, spirally wound laminated fiber material, surface treated with release agent, non-reusable, of sizes required.

Void Forms: Moisture resistant treated paper faces, biodegradable, structurally sufficient to support weight of wet concrete mix until initial set; 2 inch thick.

Rough-Formed Finished Concrete: Plywood, lumber, metal or another approved material.  Provide lumber dressed on at least two edges and one side for tight fit.

Form Ties: Snap-off type, galvanized metal cone type with waterproofing washer free of defects that could leave holes larger than 1 in. in concrete surface.

Form Release Agent: Colorless mineral oil which will not stain concrete, absorb moisture, or impair natural bonding or color characteristics of coating intended for use on concrete.

Corners: Chamfered, wood strip type; ¾ x ¾ in. size.

Dovetail Anchor Slot: Galvanized steel, 22 gage thick, foam filled, release tape sealed slots, anchors for securing to concrete formwork.

Flashing Reglets: Galvanized steel, 22 gage thick, longest possible lengths, with alignment splines for joints, foam filled, release tape sealed slots, anchors for securing to concrete formwork.

Nails, Spikes, Lag Bolts, Through Bolts, Anchorages: Size as required, of sufficient strength and character to maintain formwork in place while placing concrete.

Waterstops: Polyvinyl chloride, minimum 1750 psi tensile strength, minimum -50 degrees F to plus 175 degrees F working temperature range, maximum possible lengths, ribbed profile, preformed corner sections. Waterstop shall be installed in accordance with the manufacturer’s recommendations for installation.

REINFORCING AND ACCESSORIES

Reinforcing Steel: ASTM A 615, grade 60 deformed bars and stirrups; and ties unless otherwise specified by the engineer.  Reinforcing steel that is resisting earthquake-induced flexural and axial forces in frame members and in structural wall boundary elements shall comply with ASTM A706.  ASTM A 615 Grade 60 shall be permitted in these members if the actual yield strength of the reinforcing steel meets the strength requirements in ACI 318, Para 21.1.5.2.   Manufacturer’s CMTRs are required for each delivery.  See 1.5.F above for additional requirements.

Welded Steel Wire Fabric: ASTM A185 Plain type in flat sheets.

Fabricate concrete reinforcing in accordance with CRSI Manual of Practice.

Locate reinforcing splices not indicated on Drawings at points of minimum stress. Vertical splices for column steel and other applications shall be installed with the required stagger specified by ACI 318 unless otherwise approved by the engineer-of-record.

Welding of reinforcing bars will be permitted only with approval of LANL.  Welding, if approved, shall conform to ACI 301 Para 5.4 and AWS D.1.4 and shall meet the requirements of Section 01 4455, Onsite Welding and Joining Requirements.  Filler material CMTRs are required.  Reinforcing steel cannot be used for filler metal, gap filler, lightning grounding, or other uses that involve welding.

Chairs, Bolsters, Bar Supports, Spacers: Size and shape for strength and support of reinforcement during concrete placement conditions including load bearing pad on bottom to prevent vapor barrier puncture.  Special chairs, bolsters, bar supports, spacers adjacent to weather exposed concrete surfaces to be plastic coated steel type; size and shape as required. Note: concrete “dobie” blocks used to hold up and position rebar must have documentation to show that they are at least the PSI compression strength of the concrete used for the placement.

Tie Wire:  Minimum 16 gage annealed type.

CONCRETE MATERIALS

Cement: ASTM C 150, Type I or Type II.

Fine and Coarse Aggregates: Conform to ASTM C 33.

Water: Potable water that is clean and not detrimental to concrete.

Fly Ash: Conform to ASTM C 618, type F.  Fly ash, 20% to 30% of combined weight of fly ash and cement shall be used for the LANL standard concrete mix.  For alternate acceptable means of reducing ASR, see Part 1, Para 1.4.B.1 above.

ADMIXTURES

Air Entrainment: Conform to ASTM C260.

Chemical: Conform to ASTM C494.

ACCESSORIES

Bonding Agent: Polymer resin emulsion.

Vapor Barrier: 6 mil clear polyethylene film of type recommended for below grade application.

Non-Shrink Grout: Premixed compound consisting of non-metallic aggregate, cement, water reducing and plasticizing agents; capable of developing minimum compressive strength of 2400 psi in 48 hours and 7000 psi in 28 days.

Joint Filler: ASTM D 1751; asphalt impregnated fiberboard or felt, 1/4 in. thick.

CONCRETE MIX

STANDARD MIX DESIGN

The standard mix design for LANL shall contain from 20% to 30% by weight of total cementitious material Type F fly ash conforming to ASTM C 618 for mitigating the deleterious effects of alkali-silica reaction in concrete that is common with the silicious nature of aggregates found in northern New Mexico.  Pre-approved mix designs shown in 2.7.H may be used as long as the materials, their sources, and their properties remain constant and as long as the aggregate correction factor is verified by testing per ASTM C 231.

*************************************************************************************************************

Note: Alkali silica reaction is the reaction between the alkali hydroxide in Portland cement and certain silicious rocks and minerals present in the aggregates, such as opal, chert, chalcedony, trydymite, cristobalite, strained quartz, etc.  The products of this reaction often result in significant expansion and cracking of the concrete, and ultimately failure of the concrete structure, including significant potential for foreign object damage.

EPA recommends that procuring agencies use concrete and other cementitious materials containing coal fly ash (pozzolan).  Include the limits on soluble alkalies for Portland cement and for pozzolan whenever there is a possibility of alkali-aggregate reactive aggregates being furnished.

*************************************************************************************************************

ALTERNATE MIX DESIGNS

Alternate means for mitigating alkali-silica reaction, including use of ground slag, silica fume, or lithium compound admixtures will be acceptable if appropriate tests and documentation are submitted (per the Submittal Attachment) in advance to LANL and approved. Note: Mix designs intended to provide more flexibility than the ranges [slump, air-content, water cement ratio, etc.] must obtain a formal variance to the specification.

Where aggregates are provided which are demonstrated through appropriate tests to have acceptable ASR levels (less than 0.1%), mix designs may be provided without the fly ash or other ingredients as noted in Para. 2.7.B.1, above.  Tests required are ASTM C1260 or AASHTO T 303-00 (or other pre-approved alternate).

Demonstrate acceptable ASR resistance for concrete with fly ash using ASTM C 1260 or AASHTO T 303-00.  Also see Para 1.4.B.1 above.

Select proportions for normal weight concrete in accordance with ACI 301, proportioning on the basis of previous field experience or trial mixtures method, for

fcr = the larger of:

f cr ( f ’ c + 1.34s, or

f cr ( f ’ c + 2.33s - 500, where:

f cr = required average compressive strength of concrete mix design, psi

f ’c = specified design compressive strength of concrete, psi

s = standard deviation, psi

If a suitable record of tests is not available to establish a standard deviation, use the following:

f cr ( f ’ c + n, where:

n = additional required strength, psi, for a specified f ’ c :

n = 1000 psi for f ’ c = less than 3000 psi.

n = 1200 psi for f ’ c = 3000 to 5000 psi.

n = 1400 psi for f ’ c = over 5000 psi.

Concrete Mix Designs shall be original work performed by the supplier’s testing agency (pre-approval of the testing agency by the LANL Building Official is required).  Mix designs extrapolated from pre-selected data are not permitted.  Configuration mix designs -- i.e., those already in use by the supplier -- are also not permitted, except for those shown in 2.7.H.  All mix designs will be established through the process of trial batch determination of the compressive strengths at the various water-cement ration trial points for each concrete class, and shall adhere to the requirements of this Section.

Trial design batches, mixture proportioning studies, and testing requirements for various classes and types of concrete specified shall be the responsibility of the Subcontractor.  Mixture proportions shall be based on compressive strength (as noted above) as determined by test specimens fabricated in accordance with ASTM C 192 and tested in accordance with ASTM C 39.  Samples of all materials used in mixture proportioning studies shall be representative of those proposed for use in the project and shall be accompanied by the manufacturer’s or producer’s test report indicating compliance with these specifications.  Trial mixtures having proportions, consistencies, and air content suitable for the work shall be made based on methodology described in ACI 211.1.  Note that the use of fly ash may require an increase of air entraining admixture to attain specified air content of concrete.  The trial mixture shall use at least three different water-cement ratios for each type of mixture, which will produce a range of strength encompassing those required for each class and type of concrete required on the project.  The maximum water-cement ratio required will be based on equivalent water-cement ratio calculations as determined by the conversion from the weight ratio of water to cement plus pozzolan, [silica fume,] and ground granulated blast-furnace slag by weight equivalency method.  Laboratory trial mixture shall be designed for maximum permitted slump and air content.  Each combination of materials proposed for use shall have a separate trial mixture, except accelerators or retarders can be used without separate trial mixtures.  The temperature of concrete in each trial batch shall be reported.  For each water-cement ratio, at least three test cylinders for each test age shall be made and cured in accordance with ASTM C 192 and tested in accordance with ASTM C 39 for 7 and 28 days.  From these results, a curve shall be plotted showing the relationship between water-cement ratio and strength for each set of trial mix studies.  In addition a curve shall be plotted showing the relationship between 7 and 28 day strengths.

Provide concrete meeting the following criteria:

*************************************************************************************************************

The Structural Engineer shall specify the required 28 day concrete strength, f ’ c, in accordance with the Structural Standards.

To increase the likelihood of good quality control, limit the number of mix designs used on a project to as few as necessary.

*************************************************************************************************************

Exterior concrete exposed to freezing and thawing.

Compressive strength, f ’ c : [3,000 psi @ 28 days].

Maximum nominal aggregate size: [0.75 in.]

Maximum water / cement ratio: [0.44]

Slump: [4 inch]

Air content: [5] percent.

Exterior concrete exposed to freezing and thawing.

Compressive strength, f ’ c : [4,000 psi @ 28 days].

Maximum nominal aggregate size: [0.75 in.]

Maximum water / cement ratio: [0.44].

Slump: [4 inch].

Air content: [5] percent.

Exterior concrete to be pumped, exposed to freezing and thawing.

Compressive strength, f ’ c : [4,000 psi @ 28 days].

Maximum nominal aggregate size: [0.75 in.]

Maximum water / cement ratio: [0.38].

Slump: [6 inch] at discharge of truck.

Slump: [3 to 7 ½ inch] at pump discharge.

Air content: [5] percent.

***********************************************************************

Caution - 5000 psi concrete is prone to hairline cracking.

***********************************************************************

Exterior concrete exposed to freezing and thawing.

Compressive strength, f ’ c : [5000 psi, at 28 days].

Maximum nominal aggregate size: [0.75 inch].

Maximum water/cement ratio: [0.34].

Slump: [4 inch].

Air Content: [5] percent.

Interior concrete not exposed to freezing and thawing.

Compressive strength, f ’ c : [3,000 psi at 28 days].

Maximum nominal aggregate size: [0.75 inch].

Maximum water/cement ratio: [0.44].

Slump: [4 inch.]

Air content: [3] percent.

Interior concrete not requiring air entraining agent.

Compressive strength, f ’ c : [3,000 psi, @ 28 days.]

Maximum nominal aggregate size: [0.75 in.]

Maximum water/cement ratio: [0.51].

Slump: [4 inch].

Air Content: None specified

Interior concrete not exposed to freezing and thawing.

Compressive strength, f ’ c : [4,000 psi @ 28 days].

Maximum nominal aggregate size: [0.75 in.]

Maximum water/cement ratio: [0.44].

Slump: [4 inch]

Air content: [3] percent.

In designing concrete mixes with fly ash and ASR aggregates, consider effects on workability, set times, times for strength development and curing, and other characteristics.  Make appropriate adjustments in construction activities, for example, times for removing forms or shoring.

Use accelerating admixtures in cold weather only when submitted and approved as a constituent of the design mix prior to use.  Use of admixtures will not relax cold weather placement requirements.

Do not use calcium chloride as an admixture.

Use set retarding admixtures during hot weather only when submitted and approved as a constituent of the design mix prior to use.

Pre-approved Concrete Design Mixes (Ref: Amec Project No. 4-519-003279).  These mix designs can be used as long as material properties remain constant.  Submit (per the Submittal Attachment) source documentation and component analyses to verify compliance of the batching materials used for pre-approved mix design.

- LATM Mix No. 19 -- Exterior, 4000 psi concrete, 4" slump, 5% air (use aggregate correction factor of 0.3 for ML-3 and ML-4 concrete) (7), 20% fly ash (Proportions per CY):

Type I-II Cement: Gcc Rio Grande, Tijeras	 656 lbs

Class F, Fly Ash: Salt River Materials, 4-Corners	 164 lbs

Water						 295 lbs

Washed Concrete Sand:  El Guique Quarry	1079 lbs

Sz#67 Coarse Aggregate: El Guique Quarry	1630 lbs

Water Reducer:  Mb poly heed 997		     41 oz(1)

Air Entraining Agent: MB Micro Air,		    8.2 oz(2)

- LATM Mix No. 44 -- Exterior, 4000 psi concrete to be pumped, 6" slump, 5% air (use aggregate correction factor of 0.3 for ML-3 and ML-4 concrete)(7), 20% fly ash (Proportions per CY):

Type I-II Cement: Gcc Rio Grande, Tijeras	 656 lbs

Class F, Fly Ash: Salt River Materials, 4-Corners	 164 lbs

Water						 295 lbs

Washed Concrete Sand:  El Guique Quarry	1079 lbs

Sz#67 Coarse Aggregate: El Guique Quarry	1630 lbs

Water Reducer, Mb poly heed 997		 57.4 oz(1)

Air Entraining Agent: MB Micro Air,		   8.2 oz(2)

- LATM Mix No. 21 -- Interior, 4000 psi concrete, 4" slump, 3% air (use aggregate correction factor of 0.3 for ML-3 and ML-4 concrete) (7), 20% fly ash (Proportions per CY):

Type I-II Cement: Gcc Rio Grande, Tijeras	 520 lbs

Class F, Fly Ash: Salt River Materials, 4-Corners	 130 lbs

Water						 280 lbs

Washed Concrete Sand:  El Guique Quarry	1243 lbs

Sz#67 Coarse Aggregate: El Guique Quarry	1750 lbs

Water Reducer:  Mb poly heed 997		     25.7 oz(3)

Air Entraining Agent: MB Micro Air,		    4.6 oz(4)

- LATM Mix No. 20 -- Interior, 3000 psi concrete, 4" slump, 3% air (use aggregate correction factor of 0.3 for ML-3 and ML-4 concrete) (7), 20% fly ash (Proportions per CY):

Type I-II Cement: Gcc Rio Grande, Tijeras	 417 lbs

Class F, Fly Ash: Salt River Materials, 4-Corners	 104 lbs

Water						 268 lbs

Washed Concrete Sand:  El Guique Quarry	1378 lbs

Sz#67 Coarse Aggregate: El Guique Quarry	1765 lbs

Water Reducer, Mb poly heed 997		 20.8 oz(5)

Air Entraining Agent: MB Micro Air,		   2.6 oz(6)

Note (1): Temperature and slump variation may require adjustment in dosage within the range of 24.6 fl oz / cy to 57.4 fl oz / cy

Note (2):  Temperature and slump variation may require adjustment in dosage within the range of 1.025 fl oz / cy to 12.3 fl oz / cy

Note (3): Temperature and slump variation may require adjustment in dosage within the range of 19.5 fl oz / cy to 45.5 fl oz / cy

Note (4):  Temperature and slump variation may require adjustment in dosage within the range of 0.8 fl oz / cy to 9.75 fl oz / cy

Note (5): Temperature and slump variation may require adjustment in dosage within the range of 15.6 fl oz / cy to 36.5 fl oz / cy

Note (6):  Temperature and slump variation may require adjustment in dosage within the range of 0.65 fl oz / cy to 7.8 fl oz / cy

Note (7):  When this mix is used in an ML-1 or ML-2 application, the aggregate correction factor must be determined by testing in accordance with ASTM C 231

EXECUTION

  - general

Conform to applicable provision of ACI 301 unless otherwise specified herein.

Mix, test, and deliver concrete, along with test records in accordance with ASTM C 94. Mixing water must be added with the use of a calibrated measuring device, such as a mechanical water meter.  Tank sight glasses are not acceptable.

EXAMINATION

Verify lines, levels, and centers before proceeding with formwork.  Ensure that dimensions agree with the Drawings. Verify “Square” for slabs, floors, and walls. “Square” specifically means a 90 degree corner or connection, whether horizontal or vertical, such as a floor, wall or ceiling.  Note: all required preliminary activities, such as geotechnical and soil compaction/moisture testing, must be confirmed in order to be considered completed.

Verify that anchors, seats, plates, reinforcement and other items to be cast into concrete are accurately placed, positioned securely, and will not cause hardship in placing concrete.

Inspect erected formwork, shoring, and bracing to ensure that work is in accordance with formwork design, and that supports, fastenings, wedges, ties, and items are secure.

Do not use wood formwork more than three times for concrete surfaces to be exposed to view.  Do not patch formwork.

Verify that concrete cover for reinforcement conforms to the drawings and to Para 3.4.C below.

FORMWORK

Hand trim sides and bottom of earth forms.  Remove loose soil prior to placing concrete.

Erect formwork, shoring and bracing to achieve design requirements and maintain tolerances in accordance with requirements of ACI 301 and ACI 347(or more stringent design requirements).  Camber structural slabs and beams in accordance with ACI 301.  Contact surfaces of the formwork should be carefully installed to produce neat and symmetrical joint patterns, unless otherwise specified.  Joints should be vertical or horizontal and, where possible, should be staggered to maintain structural continuity.

Provide bracing to ensure stability of formwork.  Shore or strengthen formwork subject to overstressing by construction loads.

Arrange and assemble formwork to permit dismantling, stripping and removal of remaining principal shores.  Do not damage concrete during stripping.

Align joints and make watertight.  Keep form joints to a minimum.

Obtain approval from the Engineer-of-Record for all construction joint locations not shown on the drawings and before framing openings (in structural members) which are not detailed on Drawings.

Provide chamfer strips on external corners of beams, joists, columns, and walls.

Apply form release agent prior to placement of reinforcing steel, anchoring devices, and embedded items.

Install void forms in accordance with manufacturer’s recommendations.  Protect forms from moisture or crushing.

Do not apply form release agent where concrete surfaces receive special finishes or applied coverings which are affected by agent.  Soak inside surfaces of untreated forms with clean water.  Keep surfaces coated prior to placement of concrete.

Provide formed openings where required for items to be embedded in or passing through concrete work.

Locate and set in place items which cast directly into concrete.

Clean formed cavities of debris prior to placing concrete.  Clean and remove foreign matter as erection proceeds.

Install accessories in accordance with manufacturer’s instructions, straight, level, and plumb.  Ensure items are not disturbed during concrete placement.

Install waterstops continuous without displacing reinforcement.

Provide temporary ports or openings in formwork where required to facilitate cleaning and inspection.  Locate openings at bottom of forms to allow flushing water to drain.

Close temporary openings with tight fitting panels, flush with inside face of forms, and neatly fitted so joints will not be apparent in exposed concrete surfaces.

During cold weather, remove ice and snow from within forms.  Do not use deicing salts or water to clean out forms.  Use compressed air or other means to remove foreign matter.  Ensure that water and debris drain to exterior through clean-out ports.

Do not remove forms or bracing until concrete has gained sufficient strength to carry its own weight and other imposed loads without excessive deflection or creep. Perform form removal in accordance with the recommendations of ACI 347.

Loosen forms carefully.  Do not wedge pry bars, hammers, or tools against finish concrete surfaces scheduled for exposure to view.

Store removed forms in manner to avoid any damage to form surfaces that will later be in contact with fresh concrete.  Discard damaged forms.

After formwork removal, place construction or equipment loads on reinforced concrete only after cylinder break results indicate strengths meet specified requirements. Exceptions to this requirement must be approved in writing by the engineer of record.

REINFORCING PLACEMENT

Place, support and secure reinforcement against displacement.  Do not deviate from required position.

Do not displace or damage vapor barrier.

Maintain minimum concrete cover around reinforcing as follows:

| Item | Minimum cover, in. |
| --- | --- |
| Slabs and Joists: Top and Bottom bars for dry conditions No. 11 bars and smaller No. 14 and 18 bars | ¾ 1-½ |
| Formed Concrete Surfaces Exposed to Earth/Water Weather: No. 5 bars and smaller, W31 or D31 wire and smaller No. 6 through No. 18 bars, W45 or D45 wire | 1-½ 2 |
| Formed Beams and Columns: Dry conditions – Stirrups and ties Principal reinforcement Exposed to earth, water, weather – Stirrups and ties Principal reinforcement | 1-½ 2 2 2-½ |
| Walls: Dry Conditions – No. 11 bars and smaller No. 14 and 18 bars Exposed to earth, water, weather – All bars | ¾ 1-½ 2 |
| Footings and Base Slabs: At formed surfaces and bottoms bearing on concrete workmat At unformed surfaces and bottoms in contact with earth Top of footings Over top of piles | 2 3 Same as slabs 2 |

PREPARATION

Prepare previously placed concrete by cleaning with steel brush, pressure washing, or other acceptable means to fully remove any laitance to assure that a “roughened” surface exists for bonding with the new concrete.  When authorized by the engineer-of-record, apply bonding agent in accordance with the manufacturer's recommendations. Laitance is a weak layer of cement and aggregate fins on a concrete surface that is usually caused by an overwet mixture, overworking the mixture, improper or excessive finishing or combination thereof.  Note: The more stringent of this paragraph, ACI 318, and ACI 301 apply.

In locations shown on the design drawings where new concrete is to be dowelled to existing work, unless noted otherwise on the design drawings, drill holes in existing concrete; insert steel dowels to the specified depth and pack solid with non-shrink grout that meets or exceeds the concrete minimum strength. Note: Non-shrink grout must be mixed, applied, and cured per the manufacturer’s requirements.

PLACING CONCRETE

Place concrete in accordance with ACI 301. Consolidate concrete by internal vibration per ACI 309R-2005 or latest edition; whichever is more stringent, unless otherwise directed by the engineer-of-record.

Notify the LANL STR a minimum of 24 hours prior to commencement of concrete operations.

Ensure that reinforcement, inserts, embedded parts, formed joint fillers, joint devices, and formwork are not disturbed during concrete placement.

Install vapor barrier under interior slabs on grade.  Lap joints minimum 6 in. and seal watertight by sealant applied between overlapping edges and ends or taping edges and ends.

Repair vapor barrier damaged during placement of concrete reinforcing.

Install joint filler, primer and sealant in accordance with manufacturer’s instructions.

Separate slabs on grade from vertical surfaces with ¼ in. thick joint filler.

Extend joint filler from bottom of slab to within ¼ in. of finished slab surface.

Install joint devices in accordance with manufacturer’s instructions.

Place concrete continuously between predetermined expansion, control, and construction joints.

Unless noted otherwise on the design drawing(s), screed floors and slabs on grade level, maintaining surface flatness of maximum 1/4 inches in 10 ft.

CONCRETE FINISHING

Provide formed concrete surfaces to be left exposed with smooth rubbed finish.

Finish concrete floor surfaces in accordance with ACI 301.

Finishes shall meet the requirements of ACI 301 section 5.3.4.2 and tolerances shall conform to ACI 117.

Tolerances for floors, slabs, and floor finishes shall be confirmed by measuring in conformance with ACI 301 section 5.3.4.3.

Wood-float surfaces which will receive tile with full bed setting system.

Steel trowel surfaces which will receive carpeting, resilient flooring, seamless flooring, or thin set tile.

Steel trowel surfaces which are scheduled to be exposed.

Provide a broom finish on exterior sidewalks and paving.

In areas with floor drains, maintain floor elevation at walls; pitch surfaces uniformly to drains at 1/8 in. per foot, minimum.

CURING AND PROTECTION

General

Immediately after placement, protect concrete from premature drying, excessively hot or cold temperatures and mechanical injury.

Use all applicable practices and recommendations:  for hot weather concrete application, from ACI 305R; for cold weather concrete applications from ACI 306R; for curing from ACI 308. Note: ACI 301 applies for any conditions not specifically addressed by one of these noted standards.

Hot Weather Applications

These practices (ACI 305R) shall be used when ambient daytime temperature at any time is 75 degrees F or more.

All applicable practices (ACI 305R) for production control and delivery including but not limited to temperature control, water content, slump, admixtures, and batching and mixing shall be employed.

Protection shall be provided from the sun and wind and all practice from ACI 305R Chapter 4 shall be followed in placing and curing.

Curing shall be by water curing methods per ACI 308.1 Sections 4, 5, 6, and/or 7.

Alternate means of curing will be allowed only if pre-approved by LANL.  If approved, liquid membrane curing must strictly follow manufacturer’s recommendations for application including volume of coverage per square foot.  Application shall follow ACI 308.1 Section 3.

Protection and curing of concrete shall conform to provisions of ACI 301 Paragraph 5.3.6.

Cold Weather Applications

Use applicable provisions from ACI 306R and meet the requirements of ACI 306.1.  Comply with recommended concrete temperatures “as mixed” and “as placed and maintained” from Table 3.1 of ACI 306.R.  Comply with Para 4.2.2.8 of ACI 301 for temperatures of delivered concrete.

Curing shall be in accordance with ACI 306R Paragraphs 8.2 and 8.3, ACI 306.1 Paragraphs 3.3 and 3.4, ACI 308.1, and other applicable provisions.

Control/contraction joints

While the concrete is still plastic (i.e., within several hours after placement), provide joints in slabs at no more than 10 feet on center in each direction.  The depth of each joint will be at least one-quarter of the slab thickness, but not less than one inch.

FIELD QUALITY CONTROL

Provide a certified testing agency to perform field testing in accordance with ACI 301.  Testing laboratory certification may be obtained through AASHTO or another nationally recognized accreditation service as allowed by ASTM C 1077. National accreditations must be specific to the specific facility and/or mobile unit. The engineer-of-record and the LANL Building Official, or designee must approve the test agency prior to performance any work. See LANL Engineering Standards Manual (ESM) Chapter 16 for additional details/requirements.

Testing agencies for performing testing services on concrete materials shall meet the requirements of ASTM 1077.

Field testing of concrete shall be performed by an ACI Certified Concrete Field Testing Technician – Grade I.

Laboratory testing of concrete shall be done by ACI-Certified concrete laboratory technician-grade 1 or equivalent per ASTM C 1077

Inform the LANL STR 48 hours in advance of field testing to allow for witnessing of testing.

*************************************************************************************************************

The Structural Engineer shall determine the frequency and type of field and laboratory testing.  The batch plant that supplies concrete to LANL currently produces concrete with a standard deviation of 700 psi for 4000 psi air entrained concrete.

*************************************************************************************************************

The Testing Agency shall perform the following tests and collect strength cylinders on one batch in every 50 cu. yds. of concrete placed or once a day when less than 50 cu. yds. is placed.  Samples for Acceptance Testing are to be taken at the discharge from the transit mixer (and into a wheel barrow per ASTM C 172.), except when using concrete pumps or conveyors to transport concrete to its final placement location.  When pumps or conveyors are used, the samples for acceptance tests shall be taken at the end of the pipe or last conveyor belt. Pumping of concrete should follow ACI 304.2R. Note: The tests below shall always be performed whenever concrete test specimens are taken.  All concrete is to be tested.

Sample concrete in accordance with ASTM C 172.

Record temperature of concrete in accordance with ASTM C 1064.

Perform slump test in accordance with ASTM C 143.

Perform air content test in accordance with ASTM C 231, pressure method.

Perform density testing in accordance with ASTM C 138 when required by ASTM C94.

Take 4 concrete strength test cylinders in accordance with ASTM C 31.

The Testing Agency shall test the strength test cylinders in accordance with ASTM C 39 at 7 days and 28 days. Strength test cylinders must be picked-up at the job site between 8 and 48 hours after molding.

Coordinate the sequencing of concrete construction to schedule LANL concrete special inspection per the requirements of IBC Chapter 17.  Provide 48 hour notification to schedule special inspectors.

*************************************************************************************************************

Mixes incorporating fly ash cement replacement typically show higher long-term strength (90 days) and an initial slower strength gain than for regular mixes without fly ash.  Fly ash mixes typically show that the compressive s strength at 28 days with Class F fly ash cement replacement is between 80% and 95% of the strength without replacement.

*************************************************************************************************************

CONCRETE ACCEPTANCE CRITERIA

Fresh Concrete

Temperature - Less than 90 degrees F.

Slump - per paragraph 2.7. Note: Slump that is lower than the minimum slump may be placed when the LANL inspector determines that the concrete is workable and can be vibrated. (This does not authorize low slump for other reasons such as concrete being placed beyond the time limit.) The LANL inspector will note the low slump in the inspection report but will not generate an NCR unless the concrete strength report indicates that it is unacceptable.

Air content - per paragraph 2.7. Note: High air-content beyond the specified range becomes a factor that can impact strength but not durability. The LANL inspector will note the high air-content the inspection report but will not generate an NCR unless the concrete strength report indicates that it is unacceptable.

Drum revolution counter - 300 maximum revolutions within 1-1/2 hours after initial mixing for Central-Mixed concrete or 100 to 300 revolutions within 1-1/2 hours after initial mixing for Shrink-Mixed and Truck-Mixed concrete.

Strength

Concrete strength is satisfactory if the average of all sets of 3 consecutive strength test results equal or exceed the specified 28 day strength f ’ c  and no individual strength test result falls below the specified 28 day strength f ’ c  by more than 500 psi.

Appearance

Free from honeycombs, embedded debris, and dimensional variance beyond ACI 301 and its references.

Construction requirements

Conforming to required lines, details, dimensions and tolerances specified for construction.

DEFECTIVE CONCRETE

Defective concrete is concrete not conforming to acceptance criteria in paragraph 3.11.

Do not accept or place defective concrete that is not in conformance with acceptance criteria.  Return the fresh concrete to the supplier.

Replace defective concrete not meeting strength criteria, at Subcontractor’s expense.  The Subcontractor may, at its expense, evaluate the concrete’s in-place strength by testing 3 core samples for each strength test where LANL cured cylinders were more than 500 psi below f ’ c in accordance with ACI 301 and ASTM C42.  Fill core holes in accordance with ACI 301.

Replace defective concrete not meeting appearance criteria, at Subcontractor’s expense.  The STR may allow repair of defective concrete at Subcontractor’s expense.

Replace concrete not in conformance with details, tolerances, and other construction requirements at Subcontractor’s expense.

ATTACHMENT 1 
SUBMITTAL TABLES

Subcontractor is responsible for full compliance to all of ACI 301 and this specification. The submittals listed in these Submittal Tables (and any others in the body of the specification) are those specific submittals that LANL must receive from the Subcontractor.

Other potential submittals associated with the various codes and standards and required by the engineer of record remain the responsibility of the Subcontractor.

The items below must be submitted by the Construction Subcontractor to the LANL STR within the time frame noted in the “timeframe” column to the right of the submittal item.  The submittal time frames may be adjusted for individual projects by Subcontract or the LANL STR.  The LANL STR will obtain the review and approval of the engineer-of-record and any other authority and notify the Subcontractor after approval is granted for each submittal.

In addition, the Subcontractor must schedule and manage any sub-tiers to ensure that the proper approach and scheduling is used to obtain all necessary approvals and tests of concrete constituents that make up new mix designs.

Table 1.A submittals are always required.  Submittals in Table 1.B (“LANL-Approved Variance and Alternate”) are only required when the subject matter of/ in the requirement is applicable.  For example, the reason ACI-301 paragraph 1.7.1.4 is included in Table 1.B is that proposed repair methods, materials, and modifications are needed to repair the concrete work to meet the requirements of Subcontract Documents. Submittals in Table 1.B are not required if the concrete work meets the requirements of the Subcontract Documents (i.e., repair is not necessary / applicable).  Finally, because the need for them will be rare, these 1B submittals are not included in the Subcontract Exhibit I Attachment B listing of submittals, but are nevertheless required when needed.

The submittal reviews should be generally consistent with the following schedule:

- 2 days for the STR to give the submittal to the A/E

- 10 days for the A/E to approve the submittal.

- 2 days for the STR to return the approved submittal

- 5 - 10 days for the Subcontractor to act on the approval

- 5 days for the Subcontractor to correct any submittals for re-review followed by a 5-day review period

(A mature process will take approximately 5 weeks if the submittal is not returned unapproved).

Note 1: Design-build Subcontractors shall obtain their engineer-of-record approvals before submitting the submittals to the LANL STR (differs from Para 3 above).

Note 2: Additional items may need to be added for nuclear or radiological projects or specialty construction (i.e., high-density concrete, self-consolidating concrete, etc.).

Note 3:  The term “engineer-of-record” is synonymous with the term “architect/engineer (i.e., as applicable to project in question).”

Note 4:  Source:  Requirement source is ACI 301-05 unless noted otherwise

TABLE 1.A  SUBMITTALS ALWAYS REQUIRED

| No. | SUBMITTAL | TIMING | SOURCE |
| --- | --- | --- | --- |
|  | General |  |  |
|  | Documentation that testing agencies have been accepted by the engineer-of-record before performing any testing work. | 4 months before performing any work. Includes A/E acceptance and LANL LBO acceptance. | 1.6.3.1 |
|  | Documentation that testing agencies have been approved by the LANL Building Official (LBO) prior to performing any work. Important note: This also applies to subtier concrete fabricators and batch plants. This places a premium on planning to assure that the testing agencies are properly approved before all of the required concrete constituent / material testing is begun to support any alternate mix design(s) which have to be submitted for LANL engineering approval 30 days before using the concrete mix. The best alternative is to choose from the list of LBO-approved test agencies from Chapter 16 of the ESM (Engineering Services Manual). Using a testing agency on the approved list will save time by having the LBO approval in advance and then there is only the engineer-of-record’s approval to obtain. | 2 months before performing any work. Note: LANL will normally require that the subcontractor hire the test agency(s). If LANL provides the test agency(s) then this submittal only applies to the subcontractor when they contract the engineer-of-record. | IBC Chapter 17 and ESM Chapter 16 |
|  | Documentation that quality control program of the concrete supplier is accepted by A/E. | 3 months before the initial placement. | 1.6.3.2.f |
|  | The testing agency shall report test and inspection results that pertain to the Work to the engineer-of-record, construction Subcontractor, and concrete supplier within 7 days after tests and inspections are performed. For timing for submittals to LANL in column to the right. | Within 2 days for the initial slump and air content and within 7 days for each specified break report sequence (i.e., 7, 14, and 28 day breaks). | 1.6.4.1.c |
|  | Data on form-facing materials proposed for smooth-form finish if not specified in the design media: Rough-form finish on concrete surfaces not exposed to public view; and Smooth-form finish on concrete surfaces exposed to public view. | 15 work days (or 3 weeks) before form installation. | 2.2.1.1 |
|  | Data on formwork release agent or formwork liners. | 15 work days (or 3 weeks) before form work installation start | 2.1.2.1.f and spec. 2.2.D |
|  | Design calculations per ACI 347 indicating arrangement of forms, sizes and grades of supports (lumber), panels, and related components (design forms for full liquid static head of concrete). Formwork drawings showing details of formwork including; joints, supports, studding and shoring, and sequence of form and shoring removal, prepared by or under supervision of a Professional Engineer detailing fabrication, assembly, and support of formwork. For shoring and re-shoring methods proposed for floor and roof slabs, spandrel beams, and other horizontal concrete members, Drawings and calculations prepared by or under supervision of a Professional Engineer. | 15 working days before formwork installation begins | Specification and ACI-301 para. 2.1.2.2.a and b |
|  | Data and sample of attachment accessories and form ties. | 15 work days (or 3 weeks) before form work installation start | 2.1.2.2.c, 5.1.2.3.f |
|  | Data and sample of expansion joint materials (sealer and filler) | 15 work days (or 3 weeks) before form work installation start | 2.1.2.2.d |
|  | Data and sample of waterstop. | 15 work days (or 3 weeks) before form work installation start | 2.1.2.2.e and spec. 2.2.I |
|  | Alternative locations and details for formed construction and contraction joints. | 1.5 months before form work installation | 2.2.2.5.d |
|  | Product data on admixtures, materials for coring concrete, vapor retarder and barriers, [epoxy bonding compound,] |  |  |
|  | Reinforcing Material |  |  |
|  | Rebar manufacturer’s certified test report (CMTRs) traceable to the heat# or test identification # on the shipping tags. | 15 work days (or 3 weeks) before the planned shipment date | 3.1.1.1a, codes, and ASTM A615 / A706 |
|  | Shop drawings indicating bar sizes, spacing, locations, piece numbers, and quantities of reinforcing steel and welded wire fabric, bending and cutting schedules, supporting and spacing devices. Identify all lap splice lengths | 1 month before re-enforcement placement | 3.1.1.1.b |
|  | List of splices and request to use splices not indicated in Subcontract Documents. | 1 month before re-enforcement placement | 3.1.1.1.c |
|  | Request to use mechanical splices not shown on the project drawings. In addition, submit the ICC Evaluation Report(s) showing the requested mechanical splices to meet the requirements of ACI 318/ACI 355.2 for the IBC year edition applicable for the project. ACI 301-[2005] paragraph 3.1.1.1.d (and ACI 355.2 section 12) requiring objective evidence that ICC (the evaluation agency) has approved the mechanical splice for use under IBC (year edition applicable). http://www.icc-es.org/reports/index.cfm?csi_num=03151&view_details=yes | 1 month before re-enforcement placement | 3.1.1.1.d, ACI 355.2, and IBC Sections 1704.1 and 1704.13 |
|  | Request and procedure to field bend or straighten reinforcement partially embedded in concrete. | 15 work days (or 3 weeks) before placement of reinforcement | 3.1.1.1.f and 3.3.2.8 |
|  | For epoxy coated reinforcement, copy of current CRSI Plant Certification for any reinforcement manufacturer’s plant. | 15 work days (or 3 weeks) before the planned shipment date. | 3.1.1.1.g |
|  | If coated reinforcement is required, description of reinforcement supports and materials for fastening coated reinforcement not described in 3.3.2.4 of ACI 305-05 (later edition if applicable) | 15 work days (or 3 weeks) before placement of reinforcement | 3.1.1.2.b |
|  | Submittal to obtain engineer-of-record approval to field-cut reinforcing steel. | 15 work days (or 3 weeks) before cutting any reinforcing steel | 3.3.2.9 |
|  | CMTRs for each rebar delivery traceable to the rebar bundle tags. Must be included with delivery of the rebar at the site. | Upon receipt |  |
|  | When rebar is to be welded, filler material CMTRs. Rebar welding must be pre-approved by LANL. | 15 work days (or 3 weeks) before welding |  |
|  | Certified copies of CMTRs for reinforcing and other construction materials such as form savers, cadwelds, etc. Mechanical splices must be supported by ICC evaluation reports showing full compliance to the applicable IBC code of record for the project. |  |  |
|  | Concrete and Concrete Materials –Spec (Pre-Approved) Mix Designs |  |  |
|  | Source documentation and component analyses to verify compliance of concrete batch materials to the pre-approved mix design. The laboratory test reports shall include manufacturers’ certified material test report(s) and all other tests for cement, fly ash [slag], [silica fume], aggregates, and admixtures. Provide maximum nominal aggregate size, gradation analysis, percentage retained and passing sieve, and a graph of percentage retained versus sieve size. | Prior to first concrete placement for either of the two pre-approved LATM exterior concrete | 03 3001 Section 2.7.H |
|  | [In ML-1 or ML-2 applications only, test reports of aggregate correction factor determination per ASTM C 231.] | Prior to first concrete placement for either of the two pre-approved LATM exterior concrete | ASTM C 231 |
|  | Concrete and Concrete Materials – Alternate Mix Designs |  |  |
|  | Reminder: The LANL Building Official must approve the Test Agency (ies) prior to performing the necessary tests. The engineer-of-record must also approve all test agencies and those test result submittals required by ACI 301. |  |  |
|  | Mix design for each strength and type of concrete to LANL’s Chief Civil/Structural engineer for approval. A complete list of materials including type; brand; source and amount of cement, fly ash, pozzolans, [silica fume], ground slag, and admixtures; and applicable reference specifications shall be included in the mix design submittal. In addition, the documentation provided shall include cementitious materials producers’ names, and plant locations; and, for aggregates, types, pit, quarry locations, producer’s names, gradings, and properties required by ASTM C33. Except for admixtures and water, test results confirming conformance with applicable specifications shall not be more than 90 days old. Test results for aggregate soundness, abrasion, and reactivity may be older than 90 days, but not older than 1 year, provided test results for the other properties specified in ASTM C 33 indicate that the aggregate quality has not changed. Note that the use of fly ash may require an increase of air entraining admixture to maintain air content of concrete within specified levels. Provide mix proportion data using at least three different water-cement ratios for each type of mixture, which will produce a range of strength encompassing those required for each class and type of concrete required. If source material changes, resubmit mix proportion data using revised source material. No material shall be provided unless proven by trial mix studies to meet the requirements of this specification, and approved in writing by LANL. Clearly indicate where each mix design will be used when more than one mix design is submitted. Submit additional data regarding concrete aggregates if the source of aggregate changes. In addition, copies of the fly ash, [silica fume], and pozzolan test results shall be submitted. The approval of fly ash, [silica fume], and pozzolan test results shall have been within 6 months of submittal date. Obtain acknowledgement of LANL’s approval of the concrete mix design prior to concrete placement. Note, design mixes intended to provide more flexibility than the stated ranges [slump, air content, water cement ratio, etc.] must obtain a formal variance to the specification. Submit separate mix design for: Each concrete strength Each specified or range of air content Each specified or range of slump Each nominal maximum aggregate size Concrete to be pumped Concrete with identifiable admixtures Include the following information with each design: Quantity of Water Type, brand, certification, and quantity of cement Source, certification, and quantity of each nominal maximum size of aggregate Type, brand, sources, certification and quantity of admixture, if used Type, source, certification and quantity of fly ash Water/cement ratio Air-content Slump Aggregate-correction factor to meet ASTM C 231. Test Reports for each design: Concrete mix tests including strength in accordance with ACI 301, ASR resistance for mix (in accordance with ASTM C 1260 or AASHTO T 303-00), air content, weight and yield (ASTM C 138). All mix designs (except pre-approved LATM mix designs –see paragraph 2.7.H) shall be tested for durability in accordance with ASTM C 666. Copies of laboratory test reports showing that the mix has been successfully tested to produce concrete with the properties specified and that mix will be suitable for the job conditions. The laboratory test reports shall include manufacturer’s certified material test and all other tests for cement, fly ash [slag], [silica fume], aggregates, and admixtures. Provide maximum nominal aggregate size, gradation analysis, percentage retained and passing sieve, and a graph of percentage retained verses sieve size. Test reports shall be submitted along with any new concrete mix design. Obtain approval from LANL before concrete placement. Fly ash and other pozzolans: ASTM C 618. Ground blast furnace slag, where used, ASTM C 989. Aggregates, petrographic analysis, ASTM C 295 and potential ASR use ASTM C 1260 (with no additives such as fly ash) or one of several other ASTM tests for ASR (ASTM C 227, ASTM C 289, or ASTM C 1293). Unless otherwise stated, the time restrictions associated with the above tests shall comply with ACI 301. | 30 days prior to use of the concrete mix | 03 3001 2.7 and ACI-301 paragraph 4.1.2.3 |
|  | Mixture proportions and characteristics: Evidence that mixture proportions conform to the requirements of 4.2.2 for cementitious material content, water-to-cementitious material ratio, slump, nominal maximum size of coarse aggregate, air content, admixtures, and chloride-ion concentration, as well as compressive strength and yield. | Approximately 15 work days (or 3 weeks) before the planned placement | 4.1.2.1 |
|  | Method and test data used to establish mixture proportions: Several different methods can be used to select mixture proportions to produce the necessary placeability, density, strength, and durability of the concrete. Field experience of concrete mixtures previously used under similar conditions provides the best assurance that the proposed concrete mixture can be used satisfactorily and will have the specified properties. If there is no field experience, ACI 211.1 provides guidance for selection of the initial quantities of materials based on material properties and specified concrete properties. When a field test record is not available, ACI 211.1 recommends that mixture characteristics be checked by trial batches in the laboratory or in the field. Blending aggregates to meet criteria for a combined grading is another proportioning method that can be used. Listed below are some of the different procedures that have been used to determine proportions of blended aggregates: • Combined fineness modulus; • 8 to 18% retained on each of the standard sieves; • Coarseness factor chart; and • 0.45 power chart. When one of the above or other similar proportioning methods is used, submit the specific combined grading to which aggregate is to be blended, along with the tolerances for control. This proportioning method also requires concrete characteristics to be checked by trial batches. | Approximately 15 work days (or 3 weeks) before the planned placement | 4.1.2.2, 4.2.3.4.a |
|  | Materials, mixture proportions, and field strength-test data used for proportioning. | To support mix design sequence | 4.1.2.4. |
|  | Requests for adjustments to mixture proportions. | Two weeks before use in a placement | 4.1.2.5 |
|  | Evaluation and test results required in 4.2.2.1 verifying the adequacy of concrete to be placed in floors if the cementitious materials content is less than the minimum specified in Table 4.2.2.1 of ACI 301 [2005]. | 15 days before the initial placement. | 4.1.2.6 |
|  | Handling, Placing, and Constructing |  |  |
|  | Description of conveying equipment. | 15 days before the initial placement. | 5.1.2.1.b |
|  | Proposed method of measuring concrete surface temperature changes. | 15 days before the initial placement. | 5.1.2.1.c |
|  | Proposed method for removal of stains, rust, efflorescence, and surface deposits. | 15 days before performing the work | 5.1.2.1.d |
|  | Qualifications of finishing Subcontractor and flatwork finishers (ACI flatwork certification). | 15 days before the initial placement. | 5.1.2.1.e |
|  | Shop drawings of placing, handling, and constructing methods. | 15 days before the initial placement. | 5.1.2.2.a |
|  | Advance notification of forthcoming placement. Arrange for tests and inspection to be properly coordinated. | 48 hours notice for first placement and 24 hours for all other placements | 5.1.2.2.b |
|  | Request for acceptance of pre-placement activities to ensure the pre-placement activities are properly inspected, if necessary. | 48 hours notice before placement | 5.1.2.2.c |
|  | Proposed wet-weather protection activities. | 48 hours notice before placement | 5.1.2.2.d, 5.3.2.1.a |
|  | [Sample finish] | 15 days before the initial placement. | 5.1.2.2.f |
|  | Specification and manufacturer’s data for surface retarder used in producing exposed-aggregate finish along with method of use. | Approximately 15 days before the initial placement. | 5.1.2.2.g, 5.3.4.2.i |
|  | Bonding agents other than cement grout for two-course slabs. | 15 days before the initial placement. | 5.1.2.3.b and spec. 2.6.A |
|  | [Proposed method for underwater placement.] | 15 days before the initial placement. | 5.1.2.3.c, 5.3.2.4 |
|  | Batch Tickets Two legible copies of the batch ticket for each load of concrete to LANL’s STR, field engineer, or inspector. Conform to the requirements for batch tickets in accordance with ASTM C 94. Include the following information: Name of ready-mix batch plant. Serial number of ticket. Date. Truck number. Name of purchaser. Specific designation of job (name and location). Specific class or designation (pre-approved design mix number) of the concrete in conformance with that employed in job specifications. Amount of concrete in cubic yards (or cubic meters). Time loaded or of first mixing of cement and aggregates. Water added by receiver of concrete and his initials. Note: any water added to the truck must also be witnessed by the LANL field engineer or inspector. Reading of revolution counter at the first addition of water. Type and brand, and amount of cement. Type and brand, and amount of admixtures. Class, brand, and amount of coal fly ash, raw or calcined natural pozzolans [grade, brand and amount of ground granulated blast-furnace slag]. Information necessary to calculate the total mixing water. Total mixing water includes free water on the aggregates, water, and ice batched at the plant, and water added by the truck operator from the mixer tank (must be witnessed by LANL representative). Maximum size of aggregate. Weights of fine and coarse aggregate. Ingredients certified as being previously approved. Water /cement ratio Amount of water that can be added at the jobsite without exceeding the water/cement ratio. Signature or initials of ready-mix representative. 1. Record on each, the location where placed in structure and time of placement. | At the completion of each day’s concrete placement(s) At the completion of each days concrete placement(s) | 03 3001 |
|  | Test and inspection records. Note: This applies to the Subcontractor when the test agency reports to them contractually. | Within 30 days after the placement | 5.1.2.1.a |
|  | *********************************************************** Author: Retain only those concrete subtypes below that apply in this Table, delete those that do not. *********************************************************** |  |  |
|  | [Architectural Concrete] |  |  |
|  | Shop drawings and fabricating drawings of formwork for architectural concrete. These drawings should show jointing of facing panels; locations and details of form ties and recesses; details of joints, anchorages, and other accessories; and any necessary alignment bracing. Obtain engineer-of-record review and approval of drawings for condition of finished surface, jointing, location of form tie holes and their treatment, types of form ties, location and details of rustication strips, leak-tightness, assembly, and removal. | 30 days before installation of formwork | 6.1.2.1.a |
|  | Request for the proposed location of full-scale mock-ups at the project site. | 2 months before mock-up start | 6.1.2.2.a |
|  | Mock-ups or sample panels of aggregate transfer and other special finishes. | 30 days before installation of formwork | 6.1.2.2.b |
|  | When an exposed-aggregate finish is required, obtain engineer-of-record review and approval of the method (such as blasting, bushhammering, or use of a surface retarder) the Subcontractor desires to use to expose aggregate. | 30 days before installation of formwork | 6.1.2.2.c |
|  | [Lightweight Concrete] |  |  |
|  | Test results or calculations correlating equilibrium density to the required fresh bulk density. Submit test results and correlation for review and approval by LANL. | 15 days before the placement. | 7.2.3.1 |
|  | [Mass Concrete] |  |  |
|  | Documentation and test data on cementitious material, aggregates, admixtures, and water. If the Subcontractor deems it necessary to use a retarding, accelerating, or other admixture in mass concrete, obtain engineer-of-record review and approval of the manufacturer’s data on the admixture and the Subcontractor’s test results on the admixture with the other project materials. | 30 days before the placement. | 8.1.2 |
|  | [Prestresssed Concrete] |  |  |
|  | Installation drawings and data on: • Sizes and heights of tendon support bars and chairs; • Tendon locations; • Size, details, location, materials, and stress grade (where applicable) for tendons and accessories; • Jacking procedures, stressing sequence, and tensioning forces; • Wobble and curvature coefficients and anchorage set data; and • Details of reinforcement to prevent busting and spalling. | 30 days before the initial placement. | 9.1.2.1.a |
|  | Gauge pressures and calibration curves for the rams and gauges. | 48 hours before the initial placement. | 9.1.2.1.b |
|  | Grout mixture proportions and test data demonstrating compliance with 9.2.2.2 of ACI 301 [2005]. | 30 days before the placement. | 9.1.2.1.c |
|  | Test data substantiating the expected coefficient and anchorage set. | 30 days before the placement. | 9.1.2.2.a |
|  | Results of tests required in 9.1.3.1 of ACI 301 [2005]. | 30 days before the placement. | 9.1.2.2.b |
|  | Jack clearances. | 48 hours before the placement. | 9.1.2.2.c |
|  | Certified mill tests for a sample taken from the production lot of the prestressing tendon that will be used in the Work. Documentation must maintain traceability to delivered tendons. | 15 days before the placement. | 9.1.2.3.a |
|  | Stressing and elongation records. | 30 days after the placement. | 9.1.2.3.b |
|  | Proposed locations of couplers at locations other than as indicated on the Contract Documents. | 15 days before the placement. | 9.2.1.7 |
|  | Data on coating material for tendons extending outside the concrete or otherwise specified to receive an additional coating. | 30 days before the placement. | 9.3.2.1.d |
|  | Records of measured elongation and gauge pressure readings for the prestressing force. | 30 days after the placement. | 9.3.4.3 |
|  | [Shrinkage-Compensating Concrete] |  |  |
|  | Expansion test results for the proposed concrete mixtures. | 30 days before the placement. | 10.1.3.2 10.2.3.2 |
|  | Proposed sequences of concrete placements. It is critical that the concrete be placed in such manner that will permit the placement to expand. Consult ACI 223 for guidance. | 15 days before the placement. | 10.1.3.3 |
|  | Request to use silica fume. | 15 days before the placement. | 10.2.1.1.c |
|  | Proportions and expansion test results for revised mixture proportions. | 30 days before the placement. | 10.2.3.3 |

TABLE 1.B  SUBMITTALS FOR LANL-APPROVED VARIANCES AND ALTERNATE METHODS

| No. | SUBMITTAL | TIMING | SOURCE |
| --- | --- | --- | --- |
|  | General |  |  |
|  | Proposed repair methods, materials, and modifications to the work. | 1 month before performing any work. | 1.7.1.4 |
|  | Description of repair work to be performed to bring strength-deficient concrete into compliance with the Subcontract Documents. | Provide subcontractor NCR with recommended repair disposition and allow sufficient time for LANL approval. LANL approval must be obtained before the work is started. | 1.7.4.2.e |
|  | Description of repair performed to bring potentially nondurable concrete into compliance with the contract documents. | Provide subcontractor NCR with recommended repair disposition and allow sufficient time for LANL approval. LANL approval must be obtained before the work is started. | 1.7.5.2.e |
|  | Location of construction and contraction joints proposed if different from those indicated in the Contract Documents. | 15 work days (or 3 weeks) before form installation. | 2.1.2.1.b |
|  | Correlation data for alternative methods of determining strength of concrete for formwork removal. See ACI 228.1R for recommendations on developing suitable correlation data. | 15 work days (or 3 weeks) before initial placement | 2.1.2.1.c |
|  | Detailed plan for formwork removal at a low compressive strength than specified. | 15 work days (or 3 weeks) before initial placement | 2.1.2.1.d |
|  | Plan and procedures for installation and removal of re-shoring and back-shoring. See ACI 347 for guidance on items to consider. | 15 work days (or 3 weeks) before form work installation start | 2.1.2.1.e |
|  | Earth cuts as form surfaces. | 15 work days (or 3 weeks) before form work installation start | 2.2.2.3 |
|  | Alternative locations and details of construction joints. | 1.5 months before form work installation | 2.2.2.5.b |
|  | Detailed plan for formwork removal at lower compressive strength than f ’c. | 15 work days (or 3 weeks) before form work installation start | 2.3.2.5 |
|  | Submit request to place column dowels without the use of templates. | 15 work days (or 3 weeks) before placement of reinforcement | 3.1.1.1.e |
|  | Submit description of reinforcement weld locations, welding procedures, and welder certification when welding is permitted by the engineer-of-record via approved design media. | 15 work days (or 3 weeks) before placement of reinforcement | 3.1.1.2.a |
|  | When the Subcontractor finds it necessary to move reinforcement beyond the specified placing tolerances to avoid interference with other reinforcement, conduits, or embedded items, review they must submit a design change request. | Obtain design change request written approval prior to embedment in concrete | 3.1.1.3.a and as stated in this req’ment |
|  | Submit, for engineer-of-record approval, the inspection and quality-control program of plants applying epoxy coating if proposed plant is not certified in accordance with the CRSI Certification Program. | 15 work days (or 3 weeks) before the planned shipment date | 3.1.1.3.b |
|  | Requests for adjustments to mixture proportions. Requests to adjust mixture proportions necessary for workability or consistency. If the Subcontractor desires to decrease the cementitious materials content of the concrete mixture after having satisfied the requirements of 4.2.3.6, obtain engineer-of-record review and approval of the proposed revised mixture with a lower cementitious material(s) content on a trial basis. If the Subcontractor finds it necessary to increase the cementitious materials content, obtain engineer-of-record review and approval` of the proposed revised mixture with a higher cementitious material(s) content on a trial basis. Confirm adequacy of modified proportions has been verified from a set of new field test data. | 1 month before the initial placement. | 4.2.3.5 |
|  | Request to use calcium chloride. | 15 days before the initial placement. | 4.1.2.7 |
|  | Request to use the volumetric batching method. | 15 days before the initial placement. | 4.1.2.8, 4.3.1.1 |
|  | Requests to exceed the ASTM C 94/C 94M required time of discharge. | 15 days before the initial placement. | 4.1.2.9 |
|  | Requests to use cementitious materials other than ASTM C 150 Type I or Type II. When ASTM C 595 or C 1157 cements are used in structures that will be subjected to deicing chemicals, verify compliance of the concrete with Table 4.2.2.9 of ACI 301 [2005]. | 15 days before the initial placement. | 4.2.1.1 |
|  | Request to use alternative sources of water. | 15 days before the initial placement. | 4.2.1.3 |
|  | Request to use admixtures. | 15 days before the initial placement. | 4.2.1.4 |
|  | Request to change materials and data verifying that properties of the concrete mixture conform to the requirements of 4.2.2 of ACI 301 [2005]. | 1 month before the initial placement. | 4.2.1.5 |
|  | Request to use a lower cementitious material content. | 1 month before the initial placement. | 4.2.2.1 |
|  | Request to use a slump other than that specified. | 15 days before the initial placement. | 4.2.2.2 |
|  | Revised mixture proportions based on revised value of f ’cr. | 1 month before the initial placement. | 4.2.3.6.c |
|  | Proposed precautions for placement of concrete hotter than 90 °F. | 48 hours notice before placement | 5.1.2.2.e 5.3.2.1.c |
|  | Proposed location and treatment of construction joints not shown on the project drawings. Obtain engineer-of-record review and approval of the proposed methods for preparing the surface and the use of portland-cement grout. | 15 days before the initial placement. | 5.1.2.3.a |
|  | Proposed methods of curing other than those of 5.3.6.4 of ACI 301 [2005]. Note: Per Spec 03 3001, non-water-curing methods must be pre-approved by LANL. | 15 days before the initial placement. | 5.1.2.3.e |
|  | Specification and data and methods of use for any proposed repair material other than site-mixed portland-cement mortar described in 5.3.7.5 (see 5.3.7.6). For patches in exposed concrete, exercise caution when using the materials described in 5.3.7.6, particularly with regard to both possible color changes from weathering and delamination due to differing coefficients of thermal expansion. Ensure that the material, including ASTM type or class, is appropriate for the moisture and thermal conditions of exposure. | 30 days before work start | 5.1.2.3.g 5.2.1.3, 5.3.7.6 |
|  | Proposed materials and methods to prepare the concrete surface to achieve bond. | 15 days before the placement. | 5.3.2.6 |
|  | Request to use bonding agents other than cement grout. | 15 days before the placement. | 5.3.4.2.f |
|  | Detailed plan for alternative saw-cutting method, such as shallow-cut and dry-cut method. See ACI 302.1R for further guidance. | 15 days before planned work | 5.3.5 |
|  | Proposed methods of curing other than those listed in 5.3.6.4.a through e of ACI 301 [2005]. | 15 days before the placement. | 5.3.6.4 |
|  | Request for alternate pre-wetting methods or times for lightweight aggregate. | 15 days before the placement. | 7.1.3.1 |
|  | Batching and mixing procedure that varies from the specified requirements in Section 4 of ACI 301 [2005]. | 15 days before the placement. | 7.2.4.1 |
|  | If the Subcontractor needs additional water or air entrainment to bring the concrete to the specified slump, obtain engineer-of-record review and approval of the request and quantities to be added. Do not exceed water-cement ratio limits. | 15 days before the placement. | 7.2.4.4 |
|  | Request to use an accelerating admixture. As a general rule, accelerating admixtures should not be used in mass concrete because they contributed to early undesirable heat development. On rare occasions, such as when early formwork removal is critical, accelerating admixtures may be needed to accelerate strength development in reinforced mass concrete during winter conditions. Calcium chloride, if used, should not be permitted in excess of 1% by weight of cement. The engineer-of-record must accept the use of any accelerating admixture. | 15 days before the placement. | 8.2.1.2.a |
|  | Requests to use a slump greater than 3 in. for plain mass concrete or a slump differing from the requirements of 4.2.2.2 for reinforced mass concrete. | 15 days before the placement. | 8.2.2.2 |
|  | Requests to allow limits on concrete temperature at placement to exceed 70 °F or to be less than 35 °F. | 15 days before the placement. | 8.3.1.1 |
|  | Request to use different grout mixtures. | 30 days before the placement. | 9.2.2.2.a |
|  | Data on corrosion protection material for tendons ungrouted for more than 28 days after tendon placement. | 30 days before the placement. | 9.3.2.1.f |
|  | Proportions and expansion test results for revised mixture proportions. | 30 days before the placement. | 10.2.3.3 |

END OF SECTION

********************************************************

Do not delete the following reference information:

********************************************************

FOR LANL USE ONLY

This project specification is based on LANL Master Specification 03 3001 Rev. 4, dated November 1, 2010.