SECTION 03 3001

REINFORCED CONCRETE

*************************************************************************************************************

LANL MASTER SPECIFICATION

Word file at http://engstandards.lanl.gov

This section applies to structural concrete for buildings that are designed in accordance with ACI 318, facilities classified as Natural Phenomena Hazards Performance Category (PC) 1 or 2 facilities, and ML-3 and ML-4 projects.  In general, this section does not apply to nuclear facilities.  This section may apply to nuclear facilities that, because of the low amount of material at risk, are classified as PC-2.

For nuclear facilities, ML-1 / ML-2 projects (and ML-3 potentially), and PC-3 and 4, this specification must be further amplified and developed.  This would include considering design requirements from DOE STD-1020, ACI 349 as well as ACI 318, and “Quality Assurance Requirements” from 10CFR830.120-122 and 830.200-203, “Safety Basis Requirements.”  Also, use additional quality assurance requirements from DOE G 414.1-1A as applicable.  Independent review would also be required.

When editing to suit project, author shall add job-specific requirements and delete only those portions that in no way apply to the activity (e.g., a component that does not apply).  Note:  Items in brackets are to be added or omitted according to job specific requirements.  To seek a variance from applicable requirements, contact the Engineering Standards Manual (ESM) Structural Specs POC.  Please contact POC with suggestions for improvement as well.

When assembling a specification package, include applicable specifications from all Divisions, especially Division 1, General Requirements.

Delete information within and including “stars” during editing.

*************************************************************************************************************

GENERAL

SECTION INCLUDES

Formwork, shoring, bracing, and anchorage.

Concrete reinforcing and accessories.

Cast-in-place concrete.

Control, expansion, and contraction joint devices associated with concrete work.

DEFINITIONS

“Cementitious material” as used herein shall include all Portland cement, pozzolan, fly ash, [ground iron blast-furnace slag, and silica fume].

Reinforced concrete is structural concrete reinforced with no less than the minimum amounts of prestressing steel or non-prestressed reinforcement specified in ACI 318 Chapters 1-21 and Appendices A-C.

Plain concrete is structural concrete with no reinforcement or with less reinforcement than the minimum amount specified for reinforced concrete.  Specifications for plain concrete are presented in Section 03 3053, Miscellaneous Cast-in-Place Concrete.

Engineer-of-record and Architect/Engineer are synonymous and indicate the responsible engineer for the overall design of the facility or project.

REFERENCES

References noted in these specifications form a part of these specifications to the extent applicable.  The publications are referred to in the text by the basic designation only.  The related publishing organizations are stipulated in Section 01 4200, References.

Work, products, and materials shall conform to ACI 301 and other specific referenced publications and standards except where otherwise specified herein.

SUBMITTALS

- Submittals that are required to be submitted to LANL are included in the attached Submittal Table as they apply (including submittals times, unless the LANL Subcontract Technical Representative (STR) authorizes changes to the submittal times).  Note: All submittals require engineer-of-record approval.  For design-build subcontracts, this approval must occur prior to submittal to LANL.

QUALITY ASSURANCE

- Unless stated otherwise herein, the work shall comply with the most stringent of the following documents:  the version of ACI-318 and ACI 301 referenced by the applicable edition of the IBC that the project/job is required to comply with; and the latest versions of CRSI Manual of Standard Practice and Placing Reinforcing Bars, ACI Manual of Concrete Practice, ANSI/ASTM A184, and DOE Order 414.1.

- The work shall be subject to inspection at all times by the Owner and Owner’s Independent Testing Agency for the purpose of determining that the work is properly executed in accordance with this specification.  Failure to detect defective workmanship or material during any interim inspection shall not constitute acceptance of workmanship and materials.

- Acquire cement, aggregate, and fly ash from same source as used to produce the specific mix design for all work.  Formally notify LANL of any material source changes prior to concrete delivery including the test agency test documentation. The subcontractor must provide LANL a certificate of conformance (C of C prior to the initial delivery that confirms the source of the constituents, that tests confirm compliance, and that these sources are the same for the mix design testing and the delivered mix.

- The engineer of record shall use ACI 305R when concreting during hot weather, or 306R during cold weather, to develop the required hot / cold weather plan. See section 3.8 for details of plan and plan development.

- Testing Agency Qualifications:  Testing agencies that perform concrete related testing shall be nationally accredited in accordance with ASTM C1077 and testing agencies that perform reinforcing steel testing shall meet ASTM E329. For field and laboratory testing agencies and testing personnel request approval by the LANL Building Official, or designee, in accordance with the provisions of the IBC and the LANL Engineering Standards Manual Chapter 16.

- Reinforcing steel shall comply with the provisions of ASTM A 615 and ASTM A 706 (as applicable) In addition, the rebar fabricator shall maintain Heat Number Traceability for all rebar to assure heat numbers for the rebar are traceable to the rebar delivered. These heat numbers (or lot numbers if they correlate to the heat numbers on the CMTR documentation) must be identified on the tags attached to the rebar bundles and traceable to the associated CMTR(s).  Once the tags on the rebar bundles are confirmed to match the associated CMTRs by the appropriate receiving inspection; the bundles may be broken and the rebar located as required. Note: Unless specifically authorized by the government, foreign reinforcing steel is not allowed.

- The batch plant must be certified (and maintain current certification) under the NRMCA (National Ready Mix Concrete Association) process.

- Devices used for acceptance or testing, including all levels of sub-tiers, must be calibrated within recognized tolerances specified by the engineer-of record and calibrated to NIST or other recognized national standards. The devices must be suitably marked for traceability to the calibration documentation with recalibration due dates marked on each device. The users must maintain a usage log and identify any “as-found/as-received” out of tolerance devices to the appropriate LANL STR within 3 working days along with where the device(s) were used.

DELIVERY, STORAGE AND HANDLING

Do not deliver concrete until vapor barrier, forms (including confirmation of approved calculations for formwork when required), reinforcement, embedded items, chamfer strips, and any other prerequisites specified in the job specific “Test and Inspection Plan” are in place and ready for concrete placement.  Job site storage of materials shall be in accordance with ACI 301.  Protect materials from contaminants such as grease, oil, and dirt.  Ensure materials can be accurately identified after bundles are broken and tags removed.

Inspection/Documentation Verification Hold Point: Product and raw material inspection shall be performed at time of delivery to site receiving area and prior to off-loading and incorporation into the work.  Verify conformance with specified requirements and project environmental, safety and health (ES&H) and radiological requirements through inspection of material, shipping documentation, material safety data sheets (MSDS) documentation, data sheets, test documentation and other shipping manifest information.  Material not passing inspection shall be marked and prevented from entering the site or placed in an off-site quarantine area until the inspection and verification process is satisfactorily completed.

Reinforcement: Store reinforcement of different sizes and shapes in separate piles on racks raised above the ground (to avoid excessive rusting).  Protect from contaminants such as grease, oil, and dirt.  Ensure bar sizes can be accurately identified after bundles are broken and tags removed. Painting on reinforcement must be approved in writing by the engineer-of-record.

Definitions

- Certificate of Conformance (C of C): A document signed or otherwise authenticated by an authorized individual certifying the degree to which items or services meet specified requirements.

- Certified Material Test Report (CMTR). A written and signed document that is approved by a qualified party and contains data and information that attests to the actual properties of an item and the actual results of all required tests.

- National Institute of Standards and Testing (NIST).

PRODUCTS and materials

  - general

All concrete work, projects and materials shall conform to applicable provisions of ACI 301 except as otherwise specified herein.

FORM MATERIALS AND ACCESSORIES

Smooth-Formed Finished Concrete: Form-facing panels that will provide continuous, true, and smooth concrete surfaces.  Furnish in largest practicable sizes to minimize number of joints

Plywood, metal, or other approved panel materials.

Metal form surfaces shall not contain irregularities, dents, or sags.

Exterior-grade plywood panels, suitable for concrete forms, complying with APA PS 1, and as follows:

High-density overlay, Class 1 or better.

Medium density overlay, Class 1 or better; mill-release agent treated and edge sealed.

Structural 1, B-B or better; mill oiled and edge sealed.

B-B (Concrete Form), Class 1 or better; mill oiled and edge sealed.

AHA A135.4, hardboard for smooth form lining.

Prefabricated forms.

Preformed Steel Forms: Minimum 16 gage matched, tight fitting, stiffened to support weight of concrete without deflection detrimental to tolerances and appearance of finished surfaces.

Glass Fiber Fabric Reinforced Plastic Forms: Matched, tight fitting, stiffened to support weight of concrete without deflection detrimental to tolerances and appearance of finished concrete surfaces.

Pan Type: Glass fiber of size and profile required.

Tubular Column Type: Round, spirally wound laminated fiber material, surface treated with release agent, non-reusable, of sizes required.

Void Forms: Moisture resistant treated paper faces, biodegradable, structurally sufficient to support weight of wet concrete mix until initial set; 2 inch thick.

Rough-Formed Finished Concrete: Plywood, lumber, metal or another approved material.  Provide lumber dressed on at least two edges and one side for tight fit.

Form Ties: Snap-off type, metal cone type with waterproofing washer free of defects that could leave holes larger than 1 in. in concrete surface. Galvanized or other EOR-approved coatings must be used on snap-ties when reinforcing steel is epoxy coated.

Form-Release Agent: Colorless mineral oil which will not stain concrete, absorb moisture, or impair natural bonding or color characteristics of coating intended for use on concrete.

Corners: Chamfered, wood strip type; ¾ x ¾ in. size.

Dovetail Anchor Slot: Galvanized steel, 22 gage thick, foam filled, release tape sealed slots, anchors for securing to concrete formwork.

Flashing Reglets: Galvanized steel, 22 gage thick, longest possible lengths, with alignment splines for joints, foam filled, release tape sealed slots, anchors for securing to concrete formwork.

Nails, Spikes, Lag Bolts, Through Bolts, Anchorages: Size as required, of sufficient strength and character to maintain formwork in place while placing concrete.

Waterstops: Polyvinyl chloride, minimum 1750 psi tensile strength, minimum 50 degrees F to plus 175 degrees F working temperature range, maximum possible lengths, ribbed profile, preformed corner sections. Waterstop shall be installed in accordance with the manufacturer’s recommendations for installation. A C of C from the manufacturer is required as confirmation that the waterstops meets the requirements in this paragraph.

REINFORCING AND ACCESSORIES

*************************************************************************************************************

Note: Verify reinforcing steel type and requirements prior to editing subparagraph A.  ASTM A706 reinforcing steel is intended for applications where controlled tensile properties, or chemical composition restrictions to enhance weldability, or both, are required.

This distinction is highlighted by the fact that IBC and ACI 318 have additional requirements pertaining to ASTM A 615 reinforcing steel used to resist seismic forces and / or is to be welded, but ASTM A 706 does not have these restrictions.

- For the seismic requirements, ref. IBC 1708.2 and ACI 318, 21.1.5.

- For the welding requirements, ref. IBC 1708.2 and ACI 318, 3.5.2.

*************************************************************************************************************

Reinforcing Steel: [ASTM A 615, grade [60]] [ASTM A 706] deformed bars and stirrups; and ties.  Manufacturer’s CMTRs are required for each delivery and they must be traceable to the reinforcing steel tag bundles via the lot or heat number. Once the documentation is confirmed to be adequate and traceable by the responsible receiving inspection personnel, the bundles may be broken and no further traceability is required.  Other construction materials such as, pre-stress strands, Form Savers, cadwelds, mechanical splices, etc. must be supported by ICC evaluation reports showing full compliance to the applicable IBC code of record for the project.

Note:  When Reinforcing steel is authorized to be welded, a welding procedure must be utilized that has been approved by the EOR and the LANL-Welding POC.

    - Welded Steel Wire Fabric: ASTM A185 Plain type in flat sheets

    - Fabricate concrete reinforcing in accordance with CRSI Manual of Standard Practice.

*************************************************************************************************************

Note: ACI 318, Ch. 1 requires location and length of lap splices to be “shown.”  It also requires the type and location of mechanical and welded splices to be “shown.”  Statements on the project drawings, and /or in the project spec, like, Splices shall be in accordance with ACI 318, are NOT acceptable.

*************************************************************************************************************

Locate and install reinforcing splices as indicated on Drawings.

Welding of reinforcing bars will be permitted only with approval of LANL.  Welding, if approved, shall conform to ACI 301 Sect. 3 and AWS D.1.4 and shall meet the requirements of Section 01 4455, Onsite Welding and Joining Requirements.  Filler material CMTRs are required.  Reinforcing steel cannot be used for filler metal, gap filler, lightning grounding, or other uses that involve welding.

Chairs, Bolsters, Bar Supports, Spacers: Size and shape for strength and support of reinforcement during concrete placement conditions including load bearing pad on bottom to prevent vapor barrier puncture.  Special chairs, bolsters, bar supports, spacers adjacent to weather exposed concrete surfaces to be plastic coated steel type; size and shape as required. Note: concrete “dobie” blocks used to hold up and position rebar must have documentation to show that they are at least the PSI compression strength of the concrete used for the placement.

Tie Wire:  Minimum 16 gage annealed type.

CONCRETE MATERIALS

Cement: ASTM C 150, Type I or Type II.

Fine and Coarse Aggregates: Conform to ASTM C 33.

Water: Potable water that is clean and not detrimental to concrete.

Fly Ash: Conform to ASTM C 618, type F.  Fly ash, 20% to 30% of combined weight of fly ash and cement shall be used for the LANL standard concrete mix.  For alternate acceptable means of reducing ASR, see Para. 2.7.B.

ADMIXTURES

Air Entrainment: Conform to ASTM C260.

Chemical: Conform to ASTM C494.

ACCESSORIES

Bonding Agent: Polymer resin emulsion.

Vapor Barrier: 6 mil clear polyethylene film of type recommended for below grade application.

Non-Shrink Grout:  Refer to Section 03 6000, Grout.

Joint Filler: ASTM D 1751; asphalt impregnated fiberboard or felt

CONCRETE MIX

Standard Mix Design

The standard mix design for LANL shall contain from 20% to 30% by weight of total cementitious material Type F fly ash conforming to ASTM C 618 for mitigating the deleterious effects of alkali-silica reaction in concrete that is common with the siliceous nature of aggregates found in Northern New Mexico.  (The pre-approved LATM mixes at Para. 2.7.H meet this standard mix design).

*************************************************************************************************************

Note: Alkali silica reaction is the reaction between the alkali hydroxide in Portland cement and certain siliceous rocks and minerals present in the aggregates, such as opal, chert, chalcedony, trydymite, cristobalite, strained quartz, etc.  The products of this reaction often result in significant expansion and cracking of the concrete, and ultimately failure of the concrete structure, including significant potential for foreign object damage.

EPA recommends that procuring agencies use concrete and other cementitious materials containing coal fly ash (pozzolan).  Include the limits on soluble alkalies for Portland cement and for pozzolan whenever there is a possibility of alkali-aggregate reactive aggregates being furnished.

*************************************************************************************************************

Alternative Mix Designs

Alternate means for mitigating alkali-silica reaction, including use of ground slag, silica fume, or lithium compound admixtures will be acceptable if appropriate tests and documentation are submitted (per the Submittal Attachment) in advance to LANL and approved. Note: Mix designs intended to provide more flexibility than the ranges (e.g., slump, air-content, water cement ratio, etc.) must obtain a formal variance to the specification.

Where aggregates are provided which are demonstrated through appropriate tests to have acceptable reactivity levels (i.e., less than 0.1%), mix designs may be provided without the fly ash required by Para. 2.7.A.1.  Test required is ASTM C1260 (or other pre-approved alternate).

Demonstrate acceptable ASR resistance for concrete with fly ash using ASTM C 1567 (i.e., less than 0.1%).

Select proportions for normal weight concrete in accordance with ACI 301, proportioning on the basis of previous field experience or trial mixtures method, for

fcr = the larger of:

f cr ( f ’ c + 1.34s, or

f cr ( f ’ c + 2.33s - 500, where:

f cr = required average compressive strength of concrete mix design, psi

f ’c = specified design compressive strength of concrete, psi

s = standard deviation, psi

If a suitable record of tests is not available to establish a standard deviation, use the following:

f cr ( f ’ c + n, where:

n = additional required strength, psi, for a specified f ’ c :

n = 1000 psi for f ’ c = less than 3000 psi.

n = 1200 psi for f ’ c = 3000 to 5000 psi.

n = 1400 psi for f ’ c = over 5000 psi.

Concrete Mix Designs shall be original work performed by the supplier’s testing agency (pre-approval of the testing agency by the LANL Building Official is required).  Mix designs extrapolated from pre-selected data are not permitted.  Configuration mix designs -- i.e., those already in use by the supplier -- are also not permitted, except for those shown in 2.7.H.  All mix designs will be established through the process of trial batch determination of the compressive strengths at the various water-cement ratio trial points for each concrete class, and shall adhere to the requirements of this Section.

Trial design batches, mixture proportioning studies, and testing requirements for various classes and types of concrete specified shall be the responsibility of the Subcontractor.  Mixture proportions shall be based on compressive strength (as noted above) as determined by test specimens fabricated in accordance with ASTM C 192 and tested in accordance with ASTM C 39.  Samples of all materials used in mixture proportioning studies shall be representative of those proposed for use in the project and shall be accompanied by the manufacturer’s or producer’s test report indicating compliance with these specifications.  Trial mixtures having proportions, consistencies, and air content suitable for the work shall be made based on methodology described in ACI 211.1.  Note that the use of fly ash may require an increase of air entraining admixture to attain specified air content of concrete.  The trial mixture shall use at least three different water-cement ratios for each type of mixture, which will produce a range of strength encompassing those required for each class and type of concrete required on the project.  The maximum water-cement ratio required will be based on equivalent water-cement ratio calculations as determined by the conversion from the weight ratio of water to cement plus pozzolan, [silica fume,] and ground granulated blast-furnace slag by weight equivalency method.  Laboratory trial mixture shall be designed for maximum permitted slump and air content.  Each combination of materials proposed for use shall have a separate trial mixture, except accelerators or retarders can be used without separate trial mixtures.  The temperature of concrete in each trial batch shall be reported.  For each water-cement ratio, at least three test cylinders for each test age shall be made and cured in accordance with ASTM C 192 and tested in accordance with ASTM C 39 for 7 and 28 days.  From these results, a curve shall be plotted showing the relationship between water-cement ratio and strength for each set of trial mix studies.  In addition a curve shall be plotted showing the relationship between 7 and 28 day strengths.

Provide concrete meeting the following criteria:

*************************************************************************************************************

The Structural Engineer shall specify the required 28 day concrete strength, f ’ c, in accordance with the Structural Standards, keeping in mind both strength AND durability.

ACI 318, Ch. 4, Durability, requires the EOR to “…assign exposure classes based on the severity of the anticipated exposure of structural concrete members for each exposure category according to Table 4.2.1.”  The typical exposure category in Table 4.2.1 of concern at LANL is F, Freezing and Thawing, and the typical upper-bound severity of exposure is Severe, F2.

Given the above, the default values for min. f’c, nominal max. aggregate size, max. water / cementitious materials ratio, and air content that appear in the “Exterior’ subparagraphs below are based on achieving ‘F2’ concrete.  An added benefit of this is that such concrete also meets the ‘low-permeability’ requirements of Ch. 4 (i.e., P1).

For projects that involve F3 exposure class; or Sulfate (S) and /or Corrosion (C) exposure categories, use of solely the criteria for ‘exterior’ concrete (i.e., listed in subparas. 1-3 below), whether or not the default values (described above) are used, will NOT ensure that the resulting concrete meets the durability requirements of Ch. 4.

To increase the likelihood of good quality control, limit the number of mix designs used on a project to as few as necessary.

*************************************************************************************************************

Exterior concrete exposed to freezing and thawing:

Minimum compressive strength, f ’ c : [4,500 psi @ 28 days].

Maximum nominal aggregate size: [0.75 in.]

Maximum water / cement ratio: [0.45]

Slump: [4 inch]

Air content: [6] percent.

Exterior concrete to be pumped, exposed to freezing and thawing(1):

Minimum compressive strength, f ’ c : [4,500 psi @ 28 days].

Maximum nominal aggregate size: [0.75 in.]

Maximum water / cement ratio: [0.38].

Slump: [6 inch] at discharge of truck.

Slump: [3 to 7 ½ inch] at pump discharge.

Air content: [6] percent.

***********************************************************************

Caution - 5000 psi concrete is prone to hairline cracking.

***********************************************************************

Exterior concrete exposed to freezing and thawing:

Compressive strength, f ’ c : [5000 psi, at 28 days].

Maximum nominal aggregate size: [0.75 inch].

Maximum water/cement ratio: [0.34].

Slump: [4 inch].

Air Content: [6] percent.

Note (1):  In addition to meeting slump criteria at pump discharge, paragraph 3.10.C herein requires strength, temperature , and air-content criteria to be met at pump discharge (i.e., samples for testing are taken at the placement-end of the pipe / hose).  This requirement does not change / alter the ACI tolerances for the criteria (i.e., the tolerances apply to test results on samples taken at the placement-end of pipe / hose).  For example, test results from 4.5% to 7.5% for air content will be deemed acceptable since the criteria is 6% and the ACI tolerance is +1.5%.

Interior concrete not exposed to freezing and thawing:

Compressive strength, f ’ c : [3,000 psi at 28 days].

Maximum nominal aggregate size: [0.75 inch].

Maximum water/cement ratio: [0.44].

Slump: [4 inch.]

Air content: [3] percent.

Interior concrete not requiring air-entraining agent:

Compressive strength, f ’ c : [3,000 psi, @ 28 days.]

Maximum nominal aggregate size: [0.75 in.]

Maximum water/cement ratio: [0.51].

Slump: [4 inch].

Air Content: None specified

Interior concrete not exposed to freezing and thawing

Compressive strength, f ’ c : [4,000 psi @ 28 days].

Maximum nominal aggregate size: [0.75 in.]

Maximum water/cement ratio: [0.44].

Slump: [4 inch]

Air content: [3] percent.

In designing concrete mixes with fly ash and ASR aggregates, consider effects on workability, set times, times for strength development and curing, and other characteristics.  Make appropriate adjustments in construction activities, for example, times for removing forms or shoring.

Use accelerating admixtures in cold weather only when submitted and approved as a constituent of the design mix prior to use.  Use of admixtures will not relax cold-weather-placement requirements.

Do not use calcium chloride as an admixture.

Use set-retarding admixtures during hot weather only when submitted and approved as a constituent of the design mix prior to use.

- Pre-approved LATM Design Mixes (Ref: AMEC Project No. 4-519-003279).

            - Several Los Alamos Transit Mix (LATM) design mixes are pre-approved by LANL Design Engineering (DE).

            - DE will provide quality assurance of the concrete as follows:  LATM will provide DE with test results from a LANL Building Official-approved test agency every 90 days for aggregate (fine and coarse) gradations to comply with the current ASTM C 33.  In addition, LATM will provide aggregate soundness, abrasion, and reactivity test results to DE every 12 months.  DE will re-evaluate each LATM pre-approved concrete mix every 24 months. These test results and other evaluations will be documented and any required actions will be identified and implemented as necessary.

            - The pre-approved mixes are:

a.	LATM Mix No. 19 -- Exterior, 4000 psi concrete, 4" slump, 5% air (use aggregate correction factor of 0.3 for ML-3 and ML-4 concrete) (7), 20% fly ash (proportions per CY):

Type I-II Cement: Gcc Rio Grande, Tijeras 	656 lbs

Class F, Fly Ash: Salt River Materials, 4-Corners	 164 lbs

Water	295 lbs

Washed Concrete Sand:  El Guique Quarry	1079 lbs

Sz#67 Coarse Aggregate: El Guique Quarry	1630 lbs

Water Reducer:  Mb poly heed 997    	 41 oz(1)

Air Entraining Agent: MB Micro Air,    	8.2 oz(2)

  - LATM Mix No. 44 -- Exterior, 4000 psi concrete to be pumped, 6" slump, 5% air (use aggregate correction factor of 0.3 for ML-3 and ML-4 concrete)(7), 20% fly ash (proportions per CY) (8):

Type I-II Cement: Gcc Rio Grande, Tijeras	 656 lbs

Class F, Fly Ash: Salt River Materials, 4-Corners	 164 lbs

Water	 295 lbs

Washed Concrete Sand:  El Guique Quarry	1079 lbs

Sz#67 Coarse Aggregate: El Guique Quarry	1630 lbs

Water Reducer, Mb poly heed 997	 57.4 oz(1)

Air Entraining Agent: MB Micro Air,	   8.2 oz(2)

  - LATM Mix No. 21 -- Interior, 4000 psi concrete, 4" slump, 3% air (use aggregate correction factor of 0.3 for ML-3 and ML-4 concrete) (7), 20% fly ash (proportions per CY):

Type I-II Cement: Gcc Rio Grande, Tijeras	 520 lbs

Class F, Fly Ash: Salt River Materials, 4-Corners	 130 lbs

Water	 280 lbs

Washed Concrete Sand:  El Guique Quarry	1243 lbs

Sz#67 Coarse Aggregate: El Guique Quarry	1750 lbs

Water Reducer:  Mb poly heed 997	     25.7 oz(3)

Air Entraining Agent: MB Micro Air,	    4.6 oz(4)

  - LATM Mix No. 20 -- Interior, 3000 psi concrete, 4" slump, 3% air (use aggregate correction factor of 0.3 for ML-3 and ML-4 concrete) (7), 20% fly ash (proportions per CY):

Type I-II Cement: Gcc Rio Grande, Tijeras	 417 lbs

Class F, Fly Ash: Salt River Materials, 4-Corners	 104 lbs

Water	 268 lbs

Washed Concrete Sand:  El Guique Quarry	1378 lbs

Sz#67 Coarse Aggregate: El Guique Quarry	1765 lbs

Water Reducer, Mb poly heed 997	 20.8 oz(5)

Air Entraining Agent: MB Micro Air,	   2.6 oz(6)

Note (1): Temperature and slump variation may require adjustment in dosage within the range of 24.6 fl oz / cy to 57.4 fl oz / cy

Note (2):  Temperature and slump variation may require adjustment in dosage within the range of 1.025 fl oz / cy to 12.3 fl oz / cy

Note (3): Temperature and slump variation may require adjustment in dosage within the range of 19.5 fl oz / cy to 45.5 fl oz / cy

Note (4):  Temperature and slump variation may require adjustment in dosage within the range of 0.8 fl oz / cy to 9.75 fl oz / cy

Note (5): Temperature and slump variation may require adjustment in dosage within the range of 15.6 fl oz / cy to 36.5 fl oz / cy

Note (6):  Temperature and slump variation may require adjustment in dosage within the range of 0.65 fl oz / cy to 7.8 fl oz / cy

Note (7):  When this mix is used in an ML-1 or ML-2 application, the aggregate correction factor must be determined by testing in accordance with ASTM C 231

Note (8):  Paragraph 3.10.C herein requires strength, slump and air-content criteria to be met at pump discharge (i.e., samples for testing are taken at the placement- end of the pipe / hose). This requirement does not change / alter the ACI tolerances for the criteria (i.e., the tolerances apply to test results on samples taken at the placement-end of pipe / hose).  For example, test results from 3.5% to 6.5% for air content will be deemed acceptable since the criteria is 5% and the ACI tolerance is +1.5%.

EXECUTION

  - general

Work shall conform to applicable provision of ACI 301 unless otherwise specified herein.

Mix, test, and deliver concrete, along with test records in accordance with ASTM C 94.  Concrete acceptance for slump shall be based on testing in accordance with ASTM C 94 and compared to the requirements established in the design documents.

For ML-3/4 concrete, adding water in the field is only permitted if the ready-mix producer held back water at the batch plant and the slump after transport is less than that specified in the design documents. Care shall be taken to avoid exceeding the water-cement ratio. To adjust for measuring technique accuracy, the amount of water that can be added shall be reduced by 10% from the maximum calculated water-holdback volume. In addition, mixing water added in the field to adjust slump is permitted only when the water measuring device used is as follows:

- A LANL approved measuring device; or

- The ready-mix truck sight glass may be used if the following conditions are met:

a.   	The trucks must have a current NRMCA certification

b. 	There must be a pass (i.e. “P”) entry on the NRMCA Fleet Inspection Reporting Spreadsheet - Truck Mixers under Section/Column 5.1.6, Water Gage or Meter.  The aforementioned spreadsheet shall be part of a current NRMCA certification of the ready-mix producer and its facilities and its trucks.

For ML-1/2 concrete, adding mixing water in the field is only permitted if the ready-mix producer held back water at the batch plant and the slump after transport is less than that specified in the design documents.

Care must be taken not to exceed the water-cement ratio. To adjust for measuring technique accuracy, the amount of water that can be added shall be reduced by 10% from the maximum calculated water holdback volume.

In addition, mixing water added in the field to adjust slump is permitted only when the water measuring device used is as follows:

- A LANL approved mechanical calibrated device; or

- The ready mix truck sight glass may be used if the following condition is met:

  - The water-measuring device shall be manually verified prior to the addition of water. This requirement need not exceed one verification per set of water additions by a given truck in a given project-site visit. The intent of the verification to ensure that the measuring device is accurate within a tolerance of + 5%. This can be accomplished by dispensing water in a graduated cylinder/container and the measuring device reading compared to the graduation marks in the cylinder/ container. The amount of water added to the concrete mix is adjusted in accordance with the results of the verification.

EXAMINATION

Verify lines, levels, and centers before proceeding with formwork.  Ensure that dimensions agree with the Drawings. Verify “square” for slabs, floors, and walls. “Square” specifically means a 90 degree corner or connection, whether horizontal or vertical, such as a floor, wall or ceiling.  Note: all required preliminary activities, such as geotechnical and soil compaction/moisture testing, must be confirmed in order to be considered completed.

Verify that anchors, seats, plates, reinforcement and other items to be cast into concrete are accurately placed, positioned securely, and will not cause hardship in placing concrete.

Inspect erected formwork, shoring, and bracing to ensure that work is in accordance with formwork design, and that supports, fastenings, wedges, ties, and items are secure.

Do not use wood formwork more than three times for concrete surfaces to be exposed to view.  Do not patch formwork.

Verify that concrete cover for reinforcement conforms to the drawings and to Para 3.4.C below.

FORMWORK

Hand trim sides and bottom of earth forms.  Remove loose soil prior to placing concrete.

Erect formwork, shoring and bracing to achieve design requirements and maintain tolerances in accordance with requirements of ACI 301 and ACI 347 (or more stringent design requirements).  Camber structural slabs and beams in accordance with ACI 301.  Contact surfaces of the formwork should be carefully installed to produce neat and symmetrical joint patterns, unless otherwise specified.  Joints should be vertical or horizontal and, where possible, should be staggered to maintain structural continuity.

Provide bracing to ensure stability of formwork.  Shore or strengthen formwork subject to overstressing by construction loads.

Arrange and assemble formwork to permit dismantling, stripping and removal of remaining principal shores.  Do not damage concrete during stripping.

Align joints and make watertight.  Keep form joints to a minimum.

Obtain approval from the Engineer-of-Record for all construction joint locations not shown on the drawings and before framing openings (in structural members) which are not detailed on Drawings.

Provide chamfer strips on external corners of beams, joists, columns, and walls.

Apply form release agent prior to placement of reinforcing steel, anchoring devices, and embedded items.

Install void forms in accordance with manufacturer’s recommendations.  Protect forms from moisture or crushing.

Do not apply form release agent where concrete surfaces receive special finishes or applied coverings which are affected by agent.  Soak inside surfaces of untreated forms with clean water.  Keep surfaces coated prior to placement of concrete.

Provide formed openings where required for items to be embedded in or passing through concrete work.

Locate and set in place items which cast directly into concrete.

Clean formed cavities of debris prior to placing concrete.  Clean and remove foreign matter as erection proceeds.

Install accessories in accordance with manufacturer’s instructions, straight, level, and plumb.  Ensure items are not disturbed during concrete placement.

Install waterstops continuous without displacing reinforcement.

Provide temporary ports or openings in formwork where required to facilitate cleaning and inspection.  Locate openings at bottom of forms to allow flushing water to drain.

Close temporary openings with tight fitting panels, flush with inside face of forms, and neatly fitted so joints will not be apparent in exposed concrete surfaces.

During cold weather, remove ice and snow from within forms.  Do not use deicing salts or water to clean out forms.  Use compressed air or other means to remove foreign matter.  Ensure that water and debris drain to exterior through clean-out ports.

Do not remove forms or bracing until concrete has gained sufficient strength to carry its own weight and other imposed loads without excessive deflection or creep. Perform form removal in accordance with the recommendations of ACI 347.

Loosen forms carefully.  Do not wedge pry bars, hammers, or tools against finish concrete surfaces scheduled for exposure to view.

Store removed forms in manner to avoid any damage to form surfaces that will later be in contact with fresh concrete.  Discard damaged forms.

After formwork removal, place construction or equipment loads on reinforced concrete only after cylinder break results indicate strengths meet specified requirements. Exceptions to this requirement must be approved in writing by the engineer of record.

REINFORCING PLACEMENT

Place, support and secure reinforcement against displacement.  Do not deviate from required position.

Do not displace or damage vapor barrier.

****************************************************************************************************

NOTE:  The following minimum cover requirements come from ACI 318 Ch. 7 and are applicable ONLY in instances in which greater cover is not required by corrosion and /or fire-protection requirements of Ch. 7.

****************************************************************************************************

Maintain minimum concrete cover around reinforcing as follows:

| Row | Item | Minimum cover, in. |
| --- | --- | --- |
| 1 | Slabs and Joists: Top and Bottom bars for dry conditions No. 11 bars and smaller No. 14 and 18 bars | ¾ 1-½ |
| 2 | Formed Concrete Surfaces Exposed to Earth/Water Weather: No. 5 bars and smaller, W31 or D31 wire and smaller No. 6 through No. 18 bars, W45 or D45 wire | 1-½ 2 |
| 3 | Formed Beams and Columns: Dry conditions – Primary reinforcement, stirrups, spirals and ties Exposed to earth, water, weather | 1-½ See row 2 |
| 4 | Walls: Dry Conditions – No. 11 bars and smaller No. 14 and 18 bars Exposed to earth, water, weather | ¾ 1-½ See row 2 |
| 5 | Footings and Base Slabs: At formed surfaces and bottoms bearing on concrete workmat At unformed surfaces and bottoms in contact with earth Top of footings Over top of piles | 2 3 See row 1 2 |

PREPARATION

Prepare previously placed concrete by cleaning with steel brush, pressure washing, or other acceptable means to fully remove any laitance*.  When new concrete is to be bonded to existing concrete, ensure that a “roughened” surface exists in accordance with ACI 318, Ch. 11 (i.e., intentionally roughened to a full amplitude of approximately ¼ inch).  When authorized by the engineer-of-record, apply bonding agent in accordance with the manufacturer's recommendations.

*Laitance is a weak layer of cement and aggregate fins on a concrete surface that is usually caused by an overwet mixture, overworking the mixture, improper or excessive finishing or combination thereof.

In locations shown on the design drawings where new concrete is to be dowelled to existing work, unless noted otherwise on the design drawings, drill holes in existing concrete; insert steel dowels to the specified depth and pack solid with non-shrink grout that meets or exceeds the concrete minimum strength.

Note:  All aspects of this grouting/grout work must comply with Section 03 6000, Grout.

Prior to placement of concrete, ensure that the Project Geotechnical Investigation report has been read and understood, soils inspections have been performed with satisfactory results, and soils testing documentation has been completed and the results are satisfactory.*

* For a variety of reasons, some /all of these items might not be applicable to a given project.  Refer to Sheet S-0001 of the Project structural drawings, and the Test and Inspection Plan, in order to determine which items are applicable to a given project.

PLACING CONCRETE

Place concrete in accordance with ACI 301. Consolidate concrete by internal vibration per ACI 309R; whichever is more stringent, unless otherwise directed by the engineer-of-record.

Notify the LANL STR a minimum of 24 hours prior to commencement of concrete operations.

Ensure that reinforcement, inserts, embedded parts, formed joint fillers, joint devices, and formwork are not disturbed during concrete placement.

Install vapor barrier under interior slabs on grade.  Lap joints minimum 6 in. and seal watertight by sealant applied between overlapping edges and ends or taping edges and ends.

Repair vapor barrier damaged during placement of concrete reinforcing.

Install joint filler, primer and sealant in accordance with manufacturer’s instructions.

Separate slabs on grade from vertical surfaces with ¼ in. thick joint filler.

Extend joint filler from bottom of slab to within ¼ in. of finished slab surface.

Install joint devices in accordance with manufacturer’s instructions.

Place concrete continuously between predetermined expansion, control, and construction joints.

Unless noted otherwise on the design drawing(s), screed floors and slabs on grade level, maintaining surface flatness of maximum 1/4 inches in 10 ft.

CONCRETE FINISHING

Provide formed concrete surfaces to be left exposed with smooth rubbed finish.

Finish concrete floor surfaces in accordance with ACI 301.

Finishes shall meet the requirements of ACI 301 section 5.3.4.2.

Tolerances for floors, slabs, and floor finishes shall be confirmed by measuring in conformance with ACI 301 section 5.3.4.3.

Wood-float surfaces which will receive tile with full bed setting system.

Steel trowel surfaces which will receive carpeting, resilient flooring, seamless flooring, or thin-set tile.

Steel trowel surfaces which are scheduled to be exposed.

Provide a broom finish on exterior sidewalks and paving.

In areas with floor drains, maintain floor elevation at walls; pitch surfaces uniformly to drains at 1/8 in. per foot, minimum.

CURING AND PROTECTION

General

Immediately after placement, protect concrete from premature drying, excessively hot or cold temperatures and mechanical injury.

When concrete must be placed in cold weather as defined by ACI 306R, or hot weather as defined in this specification, the Contractor (self-performed work) or Subcontractor must develop a detailed “Cold-Weather Implementation Plan” / “Hot-Weather Implementation Plan” (as applicable) and obtain the project’s engineer-of-record (EOR) approval. This approval shall account for those recommendations addressed in ACI 305R or 306R and ACI 308 (curing) as appropriate and any elements required for worker safety. This cold-weather plan shall cover:

      - the production,

      - transportation,

      - placement,

      - protection,

      - curing (ACI 308) and

      - temperature monitoring of concrete during cold weather; in the submittal, include procedures to be implemented upon abrupt changes in weather conditions or equipment failures.

Do not begin hot or cold weather concreting until these procedures have been approved by the Engineer of Record and submitted to and approved by the LANL STR (Subcontractor Technical Representative).

Note: ACI 301 applies for any conditions not specifically addressed by one of the standards / guides noted.

### 3.  	Protection may be removed when the concrete surface temperature is within 20ºF of the ambient temperature measured with a calibrated measuring device.

Hot Weather Applications

These practices (ACI 305R) shall be used when ambient daytime temperature at any time at the job-site is 80 degrees F or more.

Use the project-approved “Hot-Weather Implementation Plan” (Para. 3.8.A) for implementation.

Cold Weather Applications

Use the project-approved “Cold-Weather Implementation Plan” (Para. 3.8.A) for implementation.

Control/contraction joints

While the concrete is still plastic (i.e., within several hours after placement), provide joints in slabs at no more than 10 feet on center in each direction.  The depth of each joint will be at least one-quarter of the slab thickness, but not less than one inch.

FIELD QUALITY CONTROL

Provide a certified testing agency to perform field testing in accordance with ACI 301.  Testing laboratory certification may be obtained through AASHTO or another nationally recognized accreditation service as allowed by ASTM C 1077. National accreditations must be specific to the specific facility and/or mobile unit. The engineer-of-record and the LANL Building Official, or designee must approve the test agency prior to performance of any work. See LANL Engineering Standards Manual (ESM) Chapter 16 for additional details/requirements.

Testing agencies for performing testing services on concrete materials shall meet the requirements of ASTM C 1077.

Field testing of concrete shall be performed by an ACI Certified Concrete Field Testing Technician – Grade I.

Laboratory testing of concrete shall be done by ACI-Certified concrete laboratory technician-grade 1 or equivalent per ASTM C 1077

Inform the LANL STR 48 hours in advance of field testing to allow for witnessing of testing.

*************************************************************************************************************

The Engineer-of-Record shall determine the frequency and type of field and laboratory testing.  The batch plant that supplies concrete to LANL currently produces concrete with a standard deviation of 700 psi for 4000 psi air-entrained concrete.

*************************************************************************************************************

The Testing Agency shall perform the following tests and collect strength cylinders on one batch in every 50 cu. yds. of concrete placed or once a day when less than 50 cu. yds. is placed.  Samples for Acceptance Testing are to be taken at the discharge from the transit mixer (and into a wheel barrow per ASTM C 172), except when using concrete pumps or conveyors to transport concrete to its final placement location.  When pumps or conveyors are used, the samples for acceptance tests shall be taken at the end of the pipe or last conveyor belt. Pumping of concrete should follow ACI 304.2R and belt conveying ACI-304.4R. Note: The tests below shall always be performed whenever concrete test specimens are taken.  All concrete is to be tested.

Sample concrete in accordance with ASTM C 172.

Record temperature of concrete in accordance with ASTM C 1064.

Perform slump test in accordance with ASTM C 143.

Perform air content test in accordance with ASTM C 231, pressure method.

Perform density testing in accordance with ASTM C 138 when required by ASTM C 94.

Take 4 concrete strength test cylinders in accordance with ASTM C 31.

The Testing Agency shall test the strength test cylinders in accordance with ASTM C 39 at 7 days and 28 days. Strength test cylinders must be picked-up at the job site between 8 and 48 hours after molding.

Coordinate the sequencing of concrete construction to schedule LANL special inspection per the requirements of IBC Chapter 17.  Provide 48 hour notification to schedule special inspectors.

*************************************************************************************************************

Mixes incorporating fly ash cement replacement typically show higher long-term strength (90 days) and an initial slower strength gain than for regular mixes without fly ash.  Fly ash mixes typically show that the compressive s strength at 28 days with Class F fly ash cement replacement is between 80% and 95% of the strength without replacement.

*************************************************************************************************************

CONCRETE ACCEPTANCE CRITERIA

Fresh Concrete

Temperature - Less than 90 degrees F.

Slump - per paragraph 2.7. Note: Slump that is lower than the minimum slump may be placed when the LANL inspector determines that the concrete is workable and can be vibrated. (This does not authorize low slump for other reasons such as concrete being placed beyond the time limit.) The LANL inspector will note the low slump in the inspection report but will not generate an NCR unless the concrete strength report indicates that it is unacceptable.

Air content - per paragraph 2.7. Note: High air-content beyond the specified range becomes a factor that can impact strength but not durability. The LANL inspector will note the high air-content the inspection report but will not generate an NCR unless the concrete strength report indicates that it is unacceptable.

Drum revolution counter: 300 maximum revolutions within 1-1/2 hours after initial mixing for Central-Mixed concrete or 100 to 300 revolutions within 1-1/2 hours after initial mixing for shrink-mixed and truck-mixed concrete.

Strength

Concrete strength is satisfactory if the average of all sets of 3 consecutive strength test results equal or exceed the specified 28 day strength f ’ c  and no individual strength test result falls below the specified 28 day strength f ’ c  by more than 500 psi.

Appearance

Free from honeycombs, embedded debris, and dimensional variance beyond ACI 301 and its references.

Construction requirements

Conforming to required lines, details, dimensions and tolerances specified for construction.

DEFECTIVE CONCRETE

Defective concrete is concrete not conforming to acceptance criteria in para 3.11.

### NOTE:  At the discretion of LANL Building Official, concrete that has not been placed in accordance with the applicable portions of Para. 3.8 can be considered defective due to the potential for such concrete to not be durable (e.g., concrete that is not placed properly in ‘cold/hot weather’ is subject to poor long-term performance, etc.).

Do not accept or place defective concrete that is not in conformance with acceptance criteria.  Return the fresh concrete to the supplier.

Replace defective concrete not meeting strength criteria, at Subcontractor’s expense.  The Subcontractor may, at its expense, evaluate the concrete’s in-place strength by testing 3 core samples for each strength test where LANL cured cylinders were more than 500 psi below f ’ c in accordance with ACI 301 and ASTM C 42.  Fill core holes in accordance with ACI 301.

Replace defective concrete not meeting appearance criteria, at Subcontractor’s expense.  The STR may allow repair of defective concrete at Subcontractor’s expense.

Replace concrete not in conformance with details, tolerances, and other construction requirements at Subcontractor’s expense.

Concrete that has been determined to be potentially defective regarding durability (ref. Para. 3.12.A.1) will either be replaced at Subcontractor’s expense, or tested (to try to prove concrete will be durable) at Subcontractor’s expense.

If Subcontractor chooses to test the concrete in question, the test method will be ASTM C 457.  If the test results indicate a maximum air-void spacing factor (Ḹ) of 0.008, on average, and with no single value exceeding 0.010, the concrete will be considered to have been proven to be durable.  Otherwise, the concrete will be replaced at Subcontractor’s expense.

ATTACHMENT 1 
SUBMITTAL TABLE

Subcontractor is responsible for full compliance to all of ACI 301 and this specification. The submittals listed in the Submittal Table below (and any others in the body of the specification) are those specific submittals that LANL must receive from the Subcontractor.

Other potential submittals associated with the various codes and standards and required by the engineer of record remain the responsibility of the Subcontractor.

The items below must be submitted by the Construction Subcontractor to the LANL STR within the time frame noted in the “timeframe” column to the right of the submittal item.  The submittal time frames may be adjusted for individual projects by Subcontract or the LANL STR.  The LANL STR will obtain the review and approval of the engineer-of-record and any other authority and notify the Subcontractor after approval is granted for each submittal.

In addition, the Subcontractor must schedule and manage any sub-tiers to ensure that the proper approach and scheduling is used to obtain all necessary approvals and tests of concrete constituents that make up new mix designs.

The submittal reviews should be generally consistent with the following schedule:

- 2 days for the STR to give the submittal to the A/E

- 10 days for the A/E to approve the submittal.

- 2 days for the STR to return the approved submittal

- 5 - 10 days for the Subcontractor to act on the approval

- 5 days for the Subcontractor to correct any submittals for re-review followed by a 5-day review period

(A mature process will take approximately 5 weeks if the submittal is not returned unapproved).

Note 1: Design-build Subcontractors shall obtain their engineer-of-record approvals before submitting the submittals to the LANL STR (differs from Para 3 above).

Note 2: Additional items may need to be added for nuclear or radiological projects or specialty construction (i.e., high-density concrete, self-consolidating concrete, etc.).

Note 3:  The term “engineer-of-record” is synonymous with the term “architect/engineer (i.e., as applicable to project in question).”

Note 4:  Source:  Requirement source is ACI 301-05 unless noted otherwise

TABLE 1  REQUIRED SUBMITTALS

| No. | SUBMITTAL | TIMING | SOURCE |
| --- | --- | --- | --- |
|  | General |  |  |
|  | Documentation that testing agencies have been accepted by the engineer-of-record before performing any testing work. * * Not required for LANL pre-approved mix designs | 4 months before performing any work. Includes A/E acceptance and LANL LBO acceptance. | 1.6.3.1 |
|  | Documentation that testing agencies have been approved by the LANL Building Official (LBO) prior to performing any work. Important note: This also applies to subtier concrete fabricators and batch plants. This places a premium on planning to assure that the testing agencies are properly approved before all of the required concrete constituent / material testing is begun to support any alternate mix design(s) which have to be submitted for LANL engineering approval 30 days before using the concrete mix. The best alternative is to choose from the list of LBO-approved test agencies from Chapter 16 of the ESM (Engineering Services Manual). Using a testing agency on the approved list will save time by having the LBO approval in advance and then there is only the engineer-of-record’s (EOR) approval to obtain. * * Not required for LANL pre-approved mix designs for cast-in-place concrete | 2 months before performing any work. Note: LANL will normally require that the Subcontractor hire the test agency(s). If LANL provides the test agency(s) then this submittal only applies to the Subcontractor when they contract the EOR | IBC Chapter 17 and ESM Chapter 16 |
|  | Documentation that quality control program of the concrete supplier is accepted by A/E. | 3 months before the initial placement. | 1.6.3.2.f |
|  | The testing agency shall report test and inspection results that pertain to the Work to the engineer-of-record, construction Subcontractor, and concrete supplier within 7 days after tests and inspections are performed. For timing for submittals to LANL in column to the right. | Within 2 days for the initial slump and air content and within 7 days for each specified break report sequence (i.e., 7, 14, and 28 day breaks). | 1.6.4.1.c |
|  | Data on form-facing materials proposed for smooth-form finish if not specified in the design media: Rough-form finish on concrete surfaces not exposed to public view; and Smooth-form finish on concrete surfaces exposed to public view. | 15 work days (or 3 weeks) before form installation. | 2.2.1.1 |
|  | Data on formwork release agent or formwork liners. | 15 work days (or 3 weeks) before form work installation start | 2.1.2.1.f and spec. 2.2.D |
|  | Design calculations per ACI 347 indicating arrangement of forms, sizes and grades of supports (lumber), panels, and related components (design forms for full liquid static head of concrete). Formwork drawings showing details of formwork including; joints, supports, studding and shoring, and sequence of form and shoring removal, prepared by or under supervision of a Professional Engineer detailing fabrication, assembly, and support of formwork. For shoring and re-shoring methods proposed for floor and roof slabs, spandrel beams, and other horizontal concrete members, Drawings and calculations prepared by or under supervision of a Professional Engineer. | 15 working days before formwork installation begins | Specification and ACI 301-10, Para. 2.1.2.2.a and b |
|  | Submit engineer-of-record approved “Cold-Weather Plan” prior to placing concrete in cold weather |  | Specification 3.8.A |
|  | Data and sample of expansion joint materials (sealer and filler) | 15 work days (or 3 weeks) before form work installation start | ACI 301 2.1.2.2.d |
|  | Data sheet on waterstop and waterstop splices | 15 work days (or 3 weeks) before form work installation start | ACI 301 2.1.2.2.e |
|  | Alternative locations and details for formed construction and contraction joints. | 1.5 months before form work installation | ACI 301 2.1.2.1.b |
|  | Product data on admixtures, materials for curing concrete, vapor retarder and barriers, [epoxy bonding compound,] | 5 working days prior to concrete delivery |  |
|  | Reinforcing Material |  |  |
|  | Rebar manufacturer’s certified test report (CMTRs) traceable to the heat# or test identification # on the shipping tags. | 15 work days (or 3 weeks) before the planned shipment date | ACI 301 3.1.1.1a; codes; and ASTM A 615 / A 706 |
|  | Shop drawings indicating bar sizes, spacing, locations, piece numbers, and quantities of reinforcing steel and welded wire fabric, bending and cutting schedules, supporting and spacing devices. Identify all lap splice lengths | 1 month before re-enforcement placement | ACI 301, 3.1.1.1.b |
|  | List of splices and request to use splices not indicated in Subcontract Documents. | 1 month before re-enforcement placement | ACI 301, 3.1.1.1.c |
|  | Request to use mechanical splices not shown on the project drawings. In addition, submit the ICC Evaluation Report(s) showing the requested mechanical splices to meet the requirements of ACI 318/ACI 355.2 for the IBC year edition applicable for the project. ACI 301-[2005] paragraph 3.1.1.1.d (and ACI 355.2 section 12) requiring objective evidence that ICC (the evaluation agency) has approved the mechanical splice for use under IBC (year edition applicable). http://www.icc-es.org/reports/index.cfm?csi_num=03151&view_details=yes | 1 month before re-enforcement placement | ACI 301, 3.1.1.1.d; ACI 355.2 |
|  | Request and procedure to field bend or straighten reinforcement partially embedded in concrete. | 15 work days (or 3 weeks) before placement of reinforcement | ACI 301, 3.1.1.1.f and 3.3.2.8 |
|  | Copy of current CRSI Plant Certification for epoxy coated rebar manufacturer’s plant. If the epoxy coated rebar facility is not CRSI certified then the inspection and quality control program of the plant applying the epoxy coating. | 15 work days (or 3 weeks) before the planned shipment date. |  |
|  | If coated reinforcement is required, submit description of reinforcement supports and materials for fastening coated reinforcement not described in 3.3.2.4 of ACI 305-05 (or later edition if applicable) | 15 work days (or 3 weeks) before placement of reinforcement | ACI 301, 3.1.1.2.b |
|  | Submittal to obtain engineer-of-record approval to field-cut reinforcing steel. | 15 work days (or 3 weeks) before cutting any reinforcing steel | ACI 301, 3.3.2.9 |
|  | CMTRs for each rebar delivery traceable to the rebar bundle tags. Must be included with delivery of the rebar at the site. | Upon receipt | Specification 1.5.F |
|  | When rebar is to be welded, filler material CMTRs. Rebar welding must be pre-approved by LANL. | 15 work days (or 3 weeks) before welding | Specification 2.3.B and D |
|  | Certified copies of CMTRs for reinforcing and other construction materials such as, pre-stress strands, Form Savers, cadwelds, etc. Mechanical splices must be supported by ICC evaluation reports showing full compliance to the applicable IBC code of record for the project. | At receiving inspection | Specification 2.3.B |
|  | Concrete and Concrete Materials –Spec (Pre-Approved) Mix Designs |  |  |
|  | Test reports of aggregate correction factor determination per ASTM C 231.] | Prior to first concrete placement | ASTM C 231 |
|  | Concrete and Concrete Materials – Alternate Mix Designs |  |  |
|  | Reminder: The LANL Building Official must approve the Test Agency(ies) prior to performing the necessary tests. The engineer-of-record must also approve all test agencies and those test result submittals required by ACI 301. |  | ESM Chapter 16 |
|  | Mix design for each strength and type of concrete to LANL’s Chief Civil/Structural engineer for approval. A complete list of materials including type; brand; source and amount of cement, fly ash, pozzolans, [silica fume], ground slag, and admixtures; and applicable reference specifications shall be included in the mix design submittal. In addition, the documentation provided shall include cementitious materials producers’ names, and plant locations; and, for aggregates, types, pit, quarry locations, producer’s names, gradings, and properties required by ASTM C33. Except for admixtures and water, test results confirming conformance with applicable specifications shall not be more than 90 days old. Test results for aggregate soundness, abrasion, and reactivity may be older than 90 days, but not older than 1 year, provided test results for the other properties specified in ASTM C 33 indicate that the aggregate quality has not changed. Note that the use of fly ash may require an increase of air entraining admixture to maintain air content of concrete within specified levels. Provide mix proportion data using at least three different water-cement ratios for each type of mixture, which will produce a range of strength encompassing those required for each class and type of concrete required. If source material changes, resubmit mix proportion data using revised source material. No material shall be provided unless proven by trial mix studies to meet the requirements of this specification, and approved in writing by LANL. Clearly indicate where each mix design will be used when more than one mix design is submitted. Submit additional data regarding concrete aggregates if the source of aggregate changes. In addition, copies of the fly ash, [silica fume], and pozzolan test results shall be submitted. The approval of fly ash, [silica fume], and pozzolan test results shall have been within 6 months of submittal date. Obtain acknowledgement of LANL’s approval of the concrete mix design prior to concrete placement. Note, design mixes intended to provide more flexibility than the stated ranges [slump, air content, water cement ratio, etc.] must obtain a formal variance to the specification. Submit separate mix design for: Each concrete strength Each specified or range of air content Each specified or range of slump Each nominal maximum aggregate size Concrete to be pumped Concrete with identifiable admixtures Include the following information with each design: Quantity of Water Type, brand, certification, and quantity of cement Source, certification, and quantity of each nominal maximum size of aggregate Type, brand, sources, certification and quantity of admixture, if used Type, source, certification and quantity of fly ash Water/cement ratio Air-content Slump Aggregate-correction factor to meet ASTM C 231. Test Reports for each design: Concrete mix tests including strength in accordance with ACI 301, ASR resistance for mix (in accordance with ASTM C 1260 (C1567 w/ fly ash) or AASHTO T 303-00), air content, weight and yield (ASTM C 138). All mix designs (except pre-approved LATM mix designs –see paragraph 2.7.H) shall be tested for durability in accordance with ASTM C 666. Copies of laboratory test reports showing that the mix has been successfully tested to produce concrete with the properties specified and that mix will be suitable for the job conditions. The laboratory test reports shall include manufacturer’s certified material test and all other tests for cement, fly ash [slag], [silica fume], aggregates, and admixtures. Provide maximum nominal aggregate size, gradation analysis, percentage retained and passing sieve, and a graph of percentage retained verses sieve size. Test reports shall be submitted along with any new concrete mix design. Obtain approval from LANL before concrete placement. Fly ash and other pozzolans: ASTM C 618. Ground blast furnace slag, where used, ASTM C 989. Aggregates, petrographic analysis, ASTM C 295 and potential ASR use ASTM C 1260 (with no additives such as fly ash) or one of several other ASTM tests for ASR (ASTM C 227, ASTM C 289, ASTM C 1293, or ASTM C 1567). Unless otherwise stated, the time restrictions associated with the above tests shall comply with ACI 301. | 30 days prior to use of the concrete mix | 03 3001 2.7 and ACI 301 4.1.2.3 |
|  | Mixture proportions and characteristics: Evidence that mixture proportions conform to the requirements of 4.2.2 for cementitious material content, water-to-cementitious material ratio, slump, nominal maximum size of coarse aggregate, air content, admixtures, and chloride-ion concentration, as well as compressive strength and yield. | Approximately 15 work days (or 3 weeks) before the planned placement | ACI 301 4.1.2.1 |
|  | Method and test data used to establish mixture proportions: Several different methods can be used to select mixture proportions to produce the necessary placeability, density, strength, and durability of the concrete. Field experience of concrete mixtures previously used under similar conditions provides the best assurance that the proposed concrete mixture can be used satisfactorily and will have the specified properties. If there is no field experience, ACI 211.1 provides guidance for selection of the initial quantities of materials based on material properties and specified concrete properties. When a field test record is not available, ACI 211.1 recommends that mixture characteristics be checked by trial batches in the laboratory or in the field. Blending aggregates to meet criteria for a combined grading is another proportioning method that can be used. Listed below are some of the different procedures that have been used to determine proportions of blended aggregates: • Combined fineness modulus; • 8 to 18% retained on each of the standard sieves; • Coarseness factor chart; and • 0.45 power chart. When one of the above or other similar proportioning methods is used, submit the specific combined grading to which aggregate is to be blended, along with the tolerances for control. This proportioning method also requires concrete characteristics to be checked by trial batches. | Approximately 15 work days (or 3 weeks) before the planned placement | ACI 301 4.1.2.2, 4.2.3.4.a |
|  | Materials, mixture proportions, and field strength-test data used for proportioning. | To support mix design sequence | ACI 301, 4.1.2.4. |
|  | Requests for adjustments to mixture proportions. | Two weeks before use in a placement | ACI 301 4.1.2.6 |
|  | Evaluation and test results required in 4.2.2.1 verifying the adequacy of concrete to be placed in floors if the cementitious materials content is less than the minimum specified in Table 4.2.2.1 of ACI 301 [2005]. | 15 days before the initial placement. | ACI 301 4.1.2.7 |
|  | Handling, Placing, and Constructing |  |  |
|  | Test and inspection records. Note: This applies to the Subcontractor when the test agency reports to them contractually. | Within 30 days after the placement | ACI 301 5.1.2.1.a |
|  | Description of conveying equipment. | 15 days before the initial placement. | ACI 301 5.1.2.2.b |
|  | Proposed method of measuring concrete surface temperature changes. | 15 days before the initial placement. | ACI 301 5.1.2.1.b |
|  | Proposed method for removal of stains, rust, efflorescence, and surface deposits. | 15 days before performing the work | 5.1.2.2.b |
|  | Qualifications of finishing Subcontractor and flatwork finishers (ACI flatwork certification). The supervisor for the subcontractor responsible for the concrete finishing (or at least one finisher) must have a current ACI-flatwork certification unless otherwise specifically approved by the engineer-of-record in writing | 15 days before the initial placement. | ACI 301 5.1.2.1.c 5.3.4.1 |
|  | Shop drawings of placing, handling, and constructing methods. | 15 days before the initial placement. | ACI 301 5.1.2.1.d |
|  | Advance notification of forthcoming placement. Arrange for tests and inspection to be properly coordinated. | 48 hours notice for first placement and 24 hours for all other placements | ACI 301 5.1.2.1.e |
|  | Request for acceptance of pre-placement activities to ensure the pre-placement activities are properly inspected, if necessary. | 48 hours notice before placement | ACI 301 5.1.2.1.f. |
|  | Proposed wet-weather protection activities. | 48 hours notice before placement | ACI 301 5.1.2.2.c, 5.3.2.1.a |
|  | Specification and manufacturer’s data for surface retarder used in producing exposed-aggregate finish along with method of use. | Approximately 15 days before the initial placement. | ACI 301 5.1.2.2.g, 5.3.4.2.i |
|  | Bonding agents other than cement grout for two-course slabs. | 15 days before the initial placement. | ACI 301 5.1.2.3.b and spec. 2.6.A |
|  | Batch Tickets One legible copy of the batch ticket for each load of concrete to LANL’s STR Provide batch tickets in accordance with following information: Name of ready-mix batch plant. Serial number of ticket. Date. Truck number. Name of purchaser. Specific designation of job (name and location). Specific class or designation (pre-approved design mix number) of the concrete in conformance with that employed in job specifications. Amount of concrete in cubic yards (or cubic meters). Time loaded or of first mixing of cement and aggregates. Water added by receiver of concrete and his initials. Note: any water added to the truck must also be witnessed by the LANL field engineer or inspector. Reading of revolution counter at the first addition of water. Type and brand, and amount of cement. Type and brand, and amount of admixtures. (Not required for LANS pre-approved mix designs) Class, brand, and amount of coal fly ash, raw or calcined natural pozzolans [grade, brand and amount of ground granulated blast-furnace slag].(Not required for LANS pre-approved Information necessary to calculate the total mixing water. Total mixing water includes free water on the aggregates, water, and ice batched at the plant, and water added by the truck operator from the mixer tank (must be witnessed by LANL representative). Maximum size of aggregate. Weights of fine and coarse aggregate. Ingredients certified as being previously approved. ].(Not required for LANS pre-approved Water /cement ratio Amount of water that can be added at the jobsite without exceeding the water/cement ratio. | At the completion of each day’s concrete placement(s) * At the completion of each days concrete placement(s)* Submittal time to LANS shall be set by the LANS STR | 03 3001 |
|  | *********************************************************** Author: Retain only those concrete subtypes below that apply in this Table, delete those that do not. *********************************************************** |  |  |
|  | [Architectural Concrete] |  |  |
|  | Shop drawings and fabricating drawings of formwork for architectural concrete. These drawings should show jointing of facing panels; locations and details of form ties and recesses; details of joints, anchorages, and other accessories; and any necessary alignment bracing. Obtain engineer-of-record review and approval of drawings for condition of finished surface, jointing, location of form tie holes and their treatment, types of form ties, location and details of rustication strips, leak-tightness, assembly, and removal. | 30 days before installation of formwork | ACI 301 6.1.2.1. |
|  | Location for Mock-ups | 30 days before installation of formwork | ACI 301 6.1.2.2. a |
|  | Technical data and samples of finish. | 30 days before installation of formwork | ACI 301 6.1.2.2.c and d, |
|  | [Lightweight Concrete] |  |  |
|  | Test results or calculations correlating equilibrium density to the required fresh bulk density. Submit test results and correlation for review and approval by LANL. | 15 days before the placement. | ACI 301 7.1.2.2 |
|  | [Mass Concrete] (36 inch or greater thickness) |  |  |
|  | Documentation and test data on cementitious material, aggregates, admixtures, and water. If the Subcontractor deems it necessary to use a retarding, accelerating, or other admixture in mass concrete, obtain engineer-of-record review and approval of the manufacturer’s data on the admixture and the Subcontractor’s test results on the admixture with the other project materials. | 30 days before the placement. | 8.1.2 |
|  | Thermal Control Plan and/or a request for alternatives to the thermal control plan | 15 days before the placement. | 8.1.3 |
|  | [Prestresssed/Post Concrete] |  |  |
|  | Installation drawings and data on: • Sizes and heights of tendon support bars and chairs; • Tendon locations; • Size, details, location, materials, and stress grade (where applicable) for tendons and accessories; • Jacking procedures, stressing sequence, and tensioning forces; • Wobble and curvature coefficients and anchorage set data; and • Details of reinforcement to prevent busting and spalling. | 30 days before the initial placement. | 9.1.2.1.a |
|  | Required calculations | Submitted with the design package at contractual design review stages (i.e., 30%, 60%, 90%) | 9.1.2.1.b |
|  | Drawings and design criteria | Submitted with the design package at contractual design review stages (i.e., 30%, 60%, 90%) | 9.1.2.1.c |
|  | Certification for grout constituents. | 30 days before the initial placement. | 9.1.2.1.d |
|  | Test data substantiating the expected coefficient and anchorage set. | 30 days before the placement. | 9.1.2.2.a |
|  | Jack clearances. | 48 hours before the placement. | 9.1.2.2.c |
|  | Certified mill tests for a sample taken from the production lot of the prestressing/post-tensioning tendon that will be used in the Work. Documentation must maintain traceability to delivered tendons. | 15 days before the placement. | 9.1.2.3.a |
|  | Stressing jack calibration certificates and stressing records. | 30 days after the placement. | 9.1.2.3.b |
|  | Grouting records | 15 prior to need date | 9.1.2.3.d |
|  | Water tightness test data for encapsulated anchors, when applicable | 15 days before the placement. | 9.2.1 |
|  | Duct test data , when applicable | 15 days before the placement. | 9.2.1.2.c |
|  | Proposed locations of couplers at locations other than as indicated on the Contract Documents. | 15 days before the placement. | 9.2.1.4 |
|  | Documentation of installer certification | 15 days before the placement. | 9.3.1 |
|  | Documentation of Inspector certification | 15 days before the placement. | 9.3.2 |

END OF SECTION

**************************************************************

Do not delete the following reference information:

**************************************************************

FOR LANL USE ONLY

This project specification is based on LANL Master Specification 03 3001 Rev. 6, dated August 30, 2012.