SECTION 05 1000

STRUCTURAL METAL FRAMING

************************************************************************************************************

This specification section is for use with LANL ESM Chapter 5, Sections I and II in particular; therefore it is primarily applicable to ML-4 (routine) projects.  For ML-1, ML-2, and some ML-3, additional requirements and independent reviews may be required; see ESM Ch 1 Section Z10 Specifications and Quality sections.

The ESM Chapter 5, Part II, paragraph 7.0, via reference to the International Building Code (IBC), Chapter 22*, contains provisions governing the quality, design, fabrication and erection of steel used structurally in buildings or structures.  It is the intent of this and other Metals Division sections of the specifications to address those provisions pertaining to quality, fabrication and erection; however, the specifier is ultimately responsible for ensuring ALL para. 7.0/Chapter 22 provisions are complied with on a given project.

This template must be edited for each project.  In doing so, specifier must add job-specific requirements.  Brackets are used in the text to indicate designer choices or locations where text must be supplied by the designer.  Once the choice is made or text supplied, remove the brackets.  The specifications must also be edited to delete specification requirements for processes, items, or designs that are not included in the project -- and specifier’s notes such as these.  To seek a variance from requirements in the specifications that are applicable, contact the Engineering Standards Manual Structural POC. Please contact POC with suggestions for improvement as well.
When assembling a specification package, include applicable specifications from all Divisions, especially Division 1, General requirements.
*IBC Chapter 22 stipulates compliance with a) AISC Specification for Structural Steel Buildings and, since LANL is in Seismic Design Category (SDC) D, b) AISC 341, Part I.

NOTE:  Since composite construction at LANL is seldom used, it is not addressed herein.  If composite construction is to be used on a given project, edit this Section as necessary to ensure compliance with IBC Chapter 22, Section 2205, para. 2205.3.

************************************************************************************************************

************************************************************************************************************

NOTE: The project drawings must meet the requirements of the AISC Code of Standard Practice for Steel Buildings and Bridges, Section 3 and, as applicable, AISC Seismic Provisions for Structural Steel Buildings, Part I, except for deviations specifically identified in the drawings and/or the version of this Section that is tailored for use on the project.

NOTE:  Ensure the project drawings and the version of this Section that is tailored for use on the project do not conflict with each other.

************************************************************************************************************

PART 1 GENERAL

- SECTION INCLUDES

A.	Requirements for structural steel used in building construction, including shop-applied finishes and field-applied touchup.

- REFERENCES

The publications listed below form a part of this specification to the extent referenced. The publications are referred to in the text by the basic designation only.

AMERICAN INSTITUTE OF STEEL CONSTRUCTION (AISC)

AISC 303 	Code of Standard Practice for Steel Buildings and Bridges

AISC 325 					Steel Construction Manual, 13th Ed.

AISC 326 					Detailing for Steel Construction

AISC 341 	Seismic Provisions for Structural Steel Buildings, including Supplement No. 1

AISC 360 	Specification for Structural Steel Buildings

ASME INTERNATIONAL (ASME)

ASME B46.1 	Surface Texture, (Surface Roughness, Waviness, and Lay)

ASTM INTERNATIONAL (ASTM)

ASTM A 6 	General Requirements for Rolled Structural Steel Bars, Plates, Shapes, and Sheet Piling

ASTM A 36 	Carbon Structural Steel

ASTM A 53 	Pipe, Steel, Black and Hot-Dipped, Zinc-Coated Welded and Seamless

ASTM A 123 	Zinc (Hot-Dip Galvanized) Coatings on Iron and Steel Products

ASTM A 108 	Standard Specification for Steel Bar, Carbon and Alloy, Cold-Finished

ASTM A 143 	Safeguarding Against Embrittlement of Hot-Dip Galvanized Structural Steel Products and Procedure for Detecting Embrittlement

ASTM A 153 	Zinc Coating (Hot-Dip) on Iron and Steel Hardware

ASTM A 283	Low and Intermediate Tensile Strength Carbon Steel Plates

ASTM A 307 	Carbon Steel Bolts and Studs, 60,000 psi Tensile Strength

ASTM A 325 	Structural Bolts, Steel, Heat Treated, 120/105 ksi Minimum Tensile Strength

##### ASTM A 354	Quenched and Tempered Alloy Steel Bolts, Studs, and Other Externally Threaded Fasteners

ASTM A 449	Quenched and Tempered Steel Bolts and Studs

ASTM A 490 	Heat-Treated Steel Structural Bolts, 150 ksi Minimum Tensile Strength

ASTM A 500 	Cold-Formed Welded and Seamless Carbon Steel Structural Tubing in Rounds and Shapes

ASTM A 529 	Standard Specification for High-Strength Carbon-Manganese Steel of Structural Quality

ASTM A 563 	Carbon and Alloy Steel Nuts

ASTM A 572 	High-Strength Low-Alloy Columbium-Vanadium of Structural Steel

ASTM A 588 	Standard Specification for High-Strength Low-Alloy Structural Steel with 50 ksi Minimum Yield Point to 4-in. Thick

ASTM A 780 	Repair of Damaged and Uncoated Areas of Hot-Dip Galvanized Coatings

ASTM A 913	High-Strength Low-Alloy Steel Shapes of Structural Quality, Produced by Quenching and Self-Tempering Process (QST)

ASTM A 992 	Structural Steel Shapes

ASTM C 827 	Changes in Height at Early Ages of Cylindrical Specimens from Cementitious Mixtures

ASTM C 1107 	Packaged Dry, Hydraulic-Cement Grout (Nonshrink)

ASTM F 436 	Hardened Steel Washers

ASTM F 959 	Compressible-Washer-Type Direct Tension Indicators for Use with Structural Fasteners

ASTM F 1544	Anchor Bolts, Steel, 36, 55, and 105-ksi Yield Strength

ASTM F 1852	Twist Off Type Tension Control Structural Bolt/Nut/Washer Assemblies, Steel, Heat Treated, 120/105 ksi Minimum Tensile Strength

AMERICAN WELDING SOCIETY (AWS)

AWS A2.4 	Standard Symbols for Welding, Brazing and Nondestructive Examination

AWS D1.1 	Structural Welding Code – Steel

AWS D1.8 	Structural Welding Code - Seismic Supplement

CRANE MANUFACTURERS ASSOCIATION OF AMERICA (CMAA)

CMAA 70 	Specification for Top Running Bridge and Gantry Type Multiple Girder Electric Overhead Traveling Cranes

RESEARCH COUNCIL ON STRUCTURAL CONNECTIONS (RCSC)

*RCSC Spec	Specification for Structural Joints Using ASTM A325 or A490 Bolts

*Some documents refer to this as AISC 348.

- RELATED SECTIONS

03 6000  Grout

- SUBMITTALS

************************************************************************************************************

NOTE: Submittals must be limited to those necessary for adequate quality control. The importance of an item in the project should be one of the primary factors in determining if a submittal for the item should be required.

Indicate submittal classification in the blank space following the name of the item requiring the submittal by using "REQD" when the submittal requires LANL approval.  Submittal items not designated with a "REQD" are considered as being for Subcontractor’s Quality Control System or for information only.

For ML-1 and ML-2 projects, consider moving items under A.1 to A.2.

************************************************************************************************************

LANL approval is required for submittals with a "REQD" designation; submittals not having a "REQD" designation are for Subcontractor’s Quality Control system, information only, or as otherwise designated.

- Submit the following in accordance with project submittal procedures:

      - Certificates of Compliance:

      - Steel								REQ’D

      - Bolts, nuts, and washers					REQ’D

      - Qualifications for shop welding 				REQ’D

      - Non-shrink grout

      - Overhead, top running crane rail beam

      - [Galvanizing]

      - [Direct tension indicators (per ASTM F 959)]			REQ’D

      - Certified Material Test Reports:

- Welding electrodes and rods					REQ’D

- [Tension control bolt/nut/washer assemblies

(per ASTM F 1852)]						REQ’D

      - Shop Drawings, Specifications, and Procedures:

      - Erection Plan, including description of temporary supports	REQ’D

      - Fabrication drawings, including description of connections	REQ’D

      - Welding Procedures and Procedure Qualification Records	REQ’D

      - Product Data:

- Shop primer (include test report on dry- or wet-film thickness, depending on manufacturer’s recommendations)

- Direct Tension Indicators

- Non-shrink grout

- [Tension Control bolts]

- QUALITY ASSURANCE

************************************************************************************************************

NOTE: AISC has a certification program in effect that confirms that a certified structural steel fabricating plant has the personnel, organization, experience, procedures, knowledge, equipment, capability, and commitment to produce fabricated steel of the required quality for a given category of structural steel framing.

NOTE:  AISC 341, Part I, addresses Quality Assurance (QA).  Specifically, a QA Plan that addresses quality control and quality assurance must be followed by the Subcontractor.  Such a plan will be applicable to many LANL buildings and structures via ESM Chapter 16 (i.e., IBC Chapter 17, Sections 1707-1709).  In this regard, ensure that one of the following two options are selected and implemented:

- Preferred:  Include a ‘pointer’ in the Project’s SSI to an attachment that includes the requirements of the AISC 341 QA plan [i.e., use a Project-specific version of the QA plan template with the SSI (see ESM Ch 16 IBC-IP Att B) and reference this attachment in the SSI].

- Alternative: Include the requirements of AISC 341 QA plan that apply to the Project in the Project’s Statement of Special Inspections (SSI).

If using Option 2 above (i.e., NOT using LANL QA plan template with SSI template), then ensure that any / all welding requirements are checked against AWS D1.8, Chapter 7, Inspection.  Where the provisions of ‘D1.8’ differ from those of AISC 341 QA plan, and they apply to the Project, those provisions of ‘D1.8’ will be included in the Project’s SSI / SSI attachment.

NOTE: Include paragraphs B.4, B.5, and C.4 when the project involves a Seismic Lateral Resisting System (SLRS) per AISC 341, Part 1.

************************************************************************************************************

  - Per LANL Engineering Standards Manual, Chapter 16, Section IBC-GEN, off-site fabrication of framing for buildings must be inspected by a LANL-Building-Official-approved Special Inspector, or shop approved through Section IBC-FAB.

  - Drawing Requirements

    - Submit fabrication drawings for approval prior to fabrication. Prepare per AISC 303 and AISC 326.

    - Drawings must not be reproductions of Subcontract drawings.

    - Include complete information for the fabrication and erection of the structure's components, including the location, type, and size of bolts, welds, member sizes and lengths, connection details, blocks, copes, and cuts.

    - [Shop drawings must include items required by AISC 341, Part I, Para. 5.2, as applicable.]

    - [Erection drawings must include items required by AISC 341, Part I, Para. 5.3, as applicable.]

    - Use AWS A2.4 standard welding symbols.

    - [Shoring and temporary bracing must be designed and sealed by a registered professional engineer and submitted for record purposes [, with calculations,] as part of the drawings.]

    - Member substitutions of details shown on the Subcontract drawings must be clearly highlighted on the fabrication drawings.

    - Explain the reasons for any deviations from the Subcontract drawings.

  - Certifications

- Overhead, Top Running Crane Rail Beam

    - Submit written field survey results for overhead, top running crane rail beam verifying tolerance requirements, area out of tolerance and proposed corrective measures.

- Erection Plan

- Submit for record purposes. Indicate the sequence of erection, temporary shoring and bracing, and a detailed sequence of welding, including each welding procedure required.

- Welding Procedures and Qualifications (Field)

- Field welding, will be done using LANL Welding Procedure Specifications (WPS) meeting the requirements of AWS D1.1 and AWS D1.8 (as applicable) for the processes and materials that will be used for welding.

- Field welders will be certified at LANL by LANL with certification stating the type of welding and positions qualified for, the code and procedure qualified under, date qualified, and the individual certifying the qualification tests.

- Welders will be current as shown in the LANL Welder database.

- [Welding Procedures and Qualifications (Shop)

- Prior to shop welding, submit Welding Procedure Specifications (WPS) and supporting Procedure Qualification Records (PQRs) meeting the requirements of AWS D1.1 and AWS D1.8 (as applicable) for the processes and materials that will be used for welding.

- Prior to shop welding, submit certification for each welder stating the type of welding and positions qualified for, the code and procedure qualified under, date qualified, and the firm and individual certifying the qualification tests.

    - If the qualification date of the welding operator is more than one-year old, the welding operator's qualification certificate must be accompanied by a current certificate by the welder attesting to the fact that he has been engaged in welding since the date of certification, with no break in welding service greater than 6 months.]

- DELIVERY, STORAGE, AND HANDLING

- Deliver, store and handle structural steel:

    - With equipment of adequate capacity.

    - Without overstressing or permanently deflecting material.

    - Without damaging finish.

- Deliver manufactured materials in original unopened packages, containers, or bundles with manufacturer's label intact and legible.

- Store materials off ground, under cover, and away from damp surfaces.

- Remove damaged, unlabeled or unsatisfactory materials which do not meet this specification from the job site.

PART 2 PRODUCTS

STEEL

************************************************************************************************************

NOTE: Materials appropriate to the design will be selected and remaining materials will be deleted.  Designer should require materials, products, and innovative construction methods and techniques which are environmentally sensitive, take advantage of recycling and conserve natural resources.  Only the “preferred material specification” from AISC 325, Table 2-3 are included here, with the exception of material specifications required by AISC 341 (refer to subsequent NOTE) ; however, since there are many other material specifications permissible per AISC 360, the specifier is free to require otherwise, provided that he/she first confirms availability.

************************************************************************************************************

************************************************************************************************************

NOTE: AISC 341 Part I imposes special material requirements on the structural steel and connection materials used in SLRSs.  Some of the requirements are contained in this section of the specifications; however, AISC 341 should be consulted for further detail.

************************************************************************************************************

************************************************************************************************************

NOTE: Designs requiring notch strength or installation and operation at low temperatures will require special material selections. Notch strength will be required based on design geometry or for dynamically loaded structures. When notch toughness is required, the supplementary requirements of the ASTM specification for the steel being considered should be reviewed and the appropriate supplementary requirements (ASTM A 6) specified (ref. AISC 341). In designs where the material will be exposed to temperatures below freezing, the material type should be checked against the proposed ambient and working temperatures for resistance to brittle fracture.

************************************************************************************************************

- Structural Steel (Shapes, Plates Bars, and Threaded Rods)

************************************************************************************************************

NOTE: ASTM A 36 is a general purpose structural grade steel, with a minimum yield strength of 36 ksi, and its use is preferred for M, S, C, MC, and L shapes. For notch toughness, a low-alloy steel should be considered. Increased corrosion resistance in non-marine environments can be obtained by specifying a minimum copper percentage of 0.2 percent. Check availability of shapes. Many are no longer American made.

For plates and bars thicker than 8 inches, the minimum yield strength is 32 ksi.

AISC 341, Part I requires ASTM A 283, Grade D for column base plates in SLRSs.

************************************************************************************************************

- ASTM A 36, Fy = 36 ksi, [32 ksi].  [ASTM A 283, Grade D.]; [           ].

- High-Strength Structural Steel

  - Low-Alloy Steel

************************************************************************************************************

NOTE: ASTM A 572, Grade 50 is the preferred steel type for HP shapes (rolled wide flange shapes used for bearing piles); however, it is available in other grades (number representing yield strength in ksi): 42, 55, 60, and 65.

ASTM A 992 is the preferred steel type for W shapes (rolled wide flange shapes) intended for use in building framing.

AISC 341 says ASTM A 529; ASTM A 588; ASTM A 913 Grade 50, 60, or 65; and ASTM A 572 Grades 42, 50 and 55 are material options for various steel shapes in SLRSs.

************************************************************************************************************

- ASTM A 992; [ASTM A 529]; [ASTM A 572, Grade 50 [_____]];  [ASTM A 588]; [ASTM A 913, Grade [_____]]; [                 ].

- Steel Pipe

************************************************************************************************************

NOTE: ASTM A 53 pipe, Grade B has a minimum yield strength of 35 ksi and is available in the following weight classes: STD (Standard), XS (Extra Strong), and XXS (Double-extra Strong).

************************************************************************************************************

- ASTM A53, Grade B, weight class [STD].

- Hollow Structural Steel (HSS) / Structural Steel Tubing

************************************************************************************************************

NOTE: The preferred material specification for HSS is ASTM A 500 Grade B, which has minimum yield strengths of 42 (round) and 46 ksi (rectangular), ASTM A 500 tubing may not be suitable for dynamically loaded structures or applications requiring notch strength.

************************************************************************************************************

- ASTM A500, Grade B  [_____]; [          ].

BOLTS, NUTS, AND WASHERS

************************************************************************************************************

NOTE: Commonly used bolts, nuts, and washers are listed under the applicable type of steel using the same terminology specified in "Steel" paragraph.  Verify material selection with the design and modify if required.

************************************************************************************************************

************************************************************************************************************

NOTE: Designs requiring notch strength or installation and operation at low temperatures will require special material selections. Notch strength will be required based on design geometry or for dynamically loaded structures. When notch toughness is required, the supplementary requirements of the ASTM specification for the steel being considered should be reviewed and the appropriate supplementary requirements (ASTM A 6) specified. In designs where the material will be exposed to temperatures below freezing, the material type should be checked against the proposed ambient and working temperatures for resistance to brittle fracture.

AISC 341 says all bolts in SLRSs must be pre-tensioned high-strength bolts.

************************************************************************************************************

Provide the following unless otherwise indicated

- Structural Steel [, Steel Pipe]

- Common Bolts

- ASTM A 307, Grade A [   ].

- Nuts

- ASTM A 563; [       ].

- Washers

************************************************************************************************************

NOTE: Special washer requirements may apply; ref. AISC 325, Table 2-5.

************************************************************************************************************

- ASTM F 436.

- High-Strength Structural Steel [and HSS]

- Bolts

************************************************************************************************************

NOTE: Do not galvanize ASTM A 490 bolts. When galvanizing ASTM A 325 bolts limit hardness of bolts to Rockwell C-32.

************************************************************************************************************

************************************************************************************************************

NOTE: Do not mix bolt material specifications ASTM A 325 and ASTM A 490 on the same diameter bolts in high strength connections.

Do not place ASTM A 325 and ASTM A 490, which have a hardness equal or in excess of Rockwell C-32, in contact with a galvanized surface.

The ASTM A 325 and ASTM A 490 specified are for a maximum diameter of 1.5 inches. If larger bolts are required, include the following ASTM publications in paragraph 1.2:

ASTM A 354 - Quenched and Tempered Alloy Steel Bolts, Studs, and Other Externally Threaded Fasteners

ASTM A 449 - Quenched and Tempered Steel Bolts and Studs.

************************************************************************************************************

- ASTM A 325; [ASTM A 490].

- Nuts

- ASTM A 563; [           ].

- Washers

************************************************************************************************************

NOTE: Special washer requirements may apply; ref. AISC 325, Table 2-5.

************************************************************************************************************

- ASTM F 436.

- Foundation Anchorage

- Bolts/Rods

- ASTM F 1544, Grade 36 [55] [105] anchor rods.

- Nuts

  - ASTM A 563; [            ].

- Washers

************************************************************************************************************

NOTE: Special washer requirements may apply; ref. AISC 325, Table 2-5.

************************************************************************************************************

- ASTM F 436.

- Direct-Tension-Indicator Washers

- ASTM F 959, type [325] [325-3] [490] [490-3]

- [Twist-Off-Type Tension-Control Bolts

- ASTM F 1852, type [1] [3]

- [Self-Locking Nuts

- Provide nuts with a locking pin set in the nut.

      - The locking pin must slide along the bolt threads, and by reversing the direction of the locking pin, the nut must be removed without damaging the nut or bolt.

      - Provide stainless steel locking pins.]

Structural Steel Accessories

- Welding Electrodes and Rods

    - AWS D1.1 Table 3.1.

    - AWS D1.8, Paragraphs 6.3 and 6.4 (i.e., all subparagraphs, as applicable)

- Non-Shrink Grout

************************************************************************************************************

NOTE: Some non-shrink grouts derive their non-shrink properties from an increase in volume of metal due to oxidation.  Where oxidation is not desired for appearance sake, specify nonmetallic grout.

************************************************************************************************************

- ASTM C 1107, with no ASTM C 827 shrinkage. [Grout must be nonmetallic.]

- Welded Shear Stud Connectors

- AWS D1.1 Chapter 7, Type B shear stud connectors made from ASTM A 108 material.

[Shop Primer

************************************************************************************************************

NOTES:

- Generic preparation, priming and painting (PPP) requirements are contained in Section 09 9100; if these meet the needs of the project then delete this paragraph.

- Should the project require other PPP then keep the paragraph, edit in the requirements as necessary, and edit 09 9100 so there are no conflicts.  Also, edit other related paragraphs of this Section as necessary (i.e., 2.7.B, 3.1.C and 3.7).

- In either case (1 or 2), ensure no conflict exists with the project PPP requirements and any/all requirements of AISC 360, Chapter J; RCSC Spec, Section 3: and AISC 341, Part 1, Section 7.

************************************************************************************************************

- [            ]].

[GALVANIZING

************************************************************************************************************

NOTE: Most structural steel is painted. If galvanized items are required, they must be indicated or specified. The galvanizing specified is by the hot-dip process. This process requires large amounts of energy and unevenly heats steel sections that can be large and/or thick, occasionally warping the steel sections. Using zinc coating by thermal spraying (metallizing) as an alternative to hot-dip galvanizing should be considered for certain steel sections. The following American Welding Society (AWS) publications should be consulted for further information:

TS-85 - Thermal Spraying - Practice, Theories, and Application

C2.2-67 - Recommended Practices for Metallizing with Aluminum and Zinc for Protection of Iron and Steel.

************************************************************************************************************

- ASTM A 123 or ASTM A 153, as applicable, unless specified otherwise galvanize after fabrication where practicable.]

[OVERHEAD, TOP-RUNNING CRANE RAIL

************************************************************************************************************

NOTE: Base crane rail shape and size on the crane capacity and maximum wheel loads. Consult the crane manufacturer for their recommended rail.

************************************************************************************************************

- [AISC 325], [_____] pound crane rail section and [bolted] [welded] joints. Provide rail fasteners and a minimum rail length of 10 feet.]

FABRICATION

- Markings

- Prior to erection, identify members by a painted erection mark.

- Connecting parts assembled in the shop for reaming holes in field connections must be match-marked with scratch and notch marks.

- Do not locate erection markings on areas to be welded [or on surfaces that will be exposed in the completed structure].

- Do not locate match markings in areas that will decrease member strength or cause stress concentrations. [Affix embossed tags to hot-dipped galvanized members.]

- Shop Primer

- Do not prime steel surfaces embedded in concrete, [surfaces to receive sprayed-on fireproofing,] [surfaces to receive epoxy coatings,] or surfaces within 0.5 inch of the toe of the welds prior to welding (except surfaces on which metal decking is to be welded).

- [Cleaning

- [         ]].

- [Primer

- [         ]].

- [Fireproofing] [and] [Epoxy] Coated Surfaces

- Clean and prepare surfaces to receive [sprayed-on fireproofing] [epoxy] coatings per the manufacturer's recommendations.

- [Surface Finishes

************************************************************************************************************

NOTE: AISC 303 states "finished" surfaces, where identified, should have a maximum roughness of 500.  For bearing surfaces, a maximum roughness of 125, in lieu of 500, is recommended.

************************************************************************************************************

- ASME B46.1 maximum surface roughness of 125 for bearing surfaces, unless indicated otherwise.]

- Drainage Holes

- Drill adequate 1/2 inch drainage holes to eliminate water traps but not affect the structural integrity.  Indicate locations on the detail drawings.

PART 3  EXECUTION

- FABRICATION

************************************************************************************************************

NOTE:  Regarding subparagraph A.1 (below), some OSHA provisions (contained in OSHA 29 CFR Part 1926, Subpart R-Steel Erection) pertain to the EOR.  The most-commonly encountered such provision at LANL is that the design of column base plates, and their foundations, must allow for the use of a minimum of four (4) anchor rods.  This issue comes up again in Para. 3.3.A.

NOTE: Regarding para. C, if bearing-type high-strength bolted connections are required, delete the preparation/painting exception for contact surfaces of friction-type high-strength bolted connections.

AISC 341 requires faying surfaces for bolted joints in Seismic Load Resisting Systems to be prepared as required for Class A or better slip-critical joints.

As mentioned previously, LANL inspection and/or approval of the fabrication plant is required for the structural steel to be furnished for the project.

************************************************************************************************************

- Fabrication per the applicable provisions of AISC 360.  Fabricate and assemble in the shop to the greatest extent possible.  The fabricating plant must be [inspected] [and] [approved] per paragraph 1.4.A.

  - Regardless of what is indicated on the Project drawings, column base plates shall be fabricated to accommodate the installation of no fewer than four (4) anchor rods.

- Compression joints depending on contact bearing must have a surface roughness not in excess of 500 micro inches as determined by ASME B46.1.  Ends must be square within the tolerances for milled ends specified in ASTM A6.

- Prepare structural steelwork, except surfaces of steel to be encased in concrete, surfaces to be field welded, surfaces to be fireproofed, and contact surfaces of friction-type high-strength bolted connections for painting per [RCSC Spec] [AISC 341] [_____] and primed with the specified paint.

- INSTALLATION

- [Overhead, Top-Running Cranes

  - Do not splice truss top and bottom chords except as approved by LANL.

      - Chord splices must occur at panel joints at approximately the third point of the span.

  - The center of gravity lines of truss members must intersect at panel points unless otherwise approved by LANL.

- When the center of gravity lines do not intersect at a panel point, make provisions for the stresses due to eccentricity.

  - Camber of trusses must be 1/8 inch in 10 feet unless otherwise indicated.

  - Provide runway rails and beams per AISC 325 and CMAA 70 except that, in case of conflict, the requirements of CMAA 70 govern.

- In addition, provide a maximum vertical difference of 0.03 inch in the elevation between adjacent runway rail tops and adjacent runway beam tops at joints.

- Provide adjustable runway support connections to allow placement of the crane rails and beams to the tolerances specified.

- Stagger runway rail joints a minimum of one foot, except that the stagger must not be the same as the crane wheel spacing.]

- ERECTION

************************************************************************************************************

NOTE:  Regarding paragraph B (below), some AISC 303 provisions (in Sections 1, 3, and 7) pertain to the EOR in certain instances.  Also, if the building or structure includes a steel SLRS, AISC 341 contains provisions regarding erection drawings that the EOR must ensure are complied with.  Finally, if the building or structure exceeds either 60-feet in height or two stories, remove the brackets and retain subparagraph 1.

************************************************************************************************************

- Erect structural steel per OSHA 29 CFR Part 1926, Subpart R-Steel Erection.

  - Regardless of what is indicated on the Project drawings, no column shall  be erected with fewer than four anchor rods.  In the event that fewer than four rods are indicated on the drawings, and the column base plate and/ or the plate bearing surface will not accommodate the installation of four rods, stop work and notify LANL and the EOR.

- Erect  structural steel per the applicable provisions of AISC 360 Chapter M; and AISC 303, Sections 1 and 7 [; and AISC 341, Part I, paragraph 5.3].

- Erection plan must be reviewed, stamped and sealed by a licensed structural engineer.

- Baseplates [Bearing plates] [and] [Leveling Plates]:

      - Clean all metal surfaces to bare metal. Remove all dirt, oil, grease, and other foreign material that would hinder bond between metal and grout.

      - The surface that grout will be placed on will also be cleaned of bond-hindering materials, and then the surface will be roughened prior to setting plates.

      - Align, level and maintain final positioning of components to be grouted.

        - Set plates for structural members and equipment supports on wedges, shims, or leveling nuts as required.

        - Weld plate washers to top of baseplate.

        - Snug-tighten anchor rods after supported members have been positioned and plumbed.  Do not remove wedges or shims but, if they protrude, cut off flush with edge of plate before packing with grout.

      - Where perimeter skirts are used, provide [1/4 to ½ in] vent holes in corners of base plates in order to facilitate venting of entrapped air.  If the base plate design contains two or more compartment areas, venting holes must be provided in the corners of each compartment.

      - In a swift manner, pack grout solidly between plate and bearing surface to the extent that all air pockets are removed.

      - Neatly finish exposed surfaces, protect grout and allow to cure.

      - Comply with the more stringent of either the grout manufacturer’s installation instructions, or the following:

        - Moist cure grout.

        - Remove forms after grout is set.  Trim grout edges to form smooth surface, splayed 45 degrees.

        - Tighten anchor rods after grout has cured for a minimum of 3 days.

- Baseplates for Post-Installed Anchors:

  - Non-grouted baseplates installed with anchors may have a maximum 1/8 inch gap as evidenced under exterior edges around the plate provided that (1) the plate exhibits bearing contact within its interior against the  concrete surface, and (2) the uneven bearing does not prevent application of the prescribed torque.

If an unacceptable bearing contact condition exists, follow one of these two procedures:

    - Rework the concrete surface to obtain a proper fit.

    - For gaps of up to 1 inch, the baseplate may be grouted instead using   the following technique:

- Insert anchors and set the baseplate.

- Install nuts to finger tight condition.

- Install shims positioned no more than ½ inch away from the anchors to reduce gaps between baseplates and shims to 1/8 inch or less at anchor locations.

- Apply tightening torque. The bolt tightening shall not be performed when interior shims under the baseplates have been placed away from anchors, so that downward bending of the baseplate would result upon tightening. Shims shall be moved as close as possible to the anchors before applying the installation torque.

- Fill the gap with non-shrink grout leaving the shims in place. For baseplates on walls, where grouting is not feasible, the gap may be filled with shim plates. The shims may be stacked, but no more than four shims shall be stacked.

************************************************************************************************************

NOTE: Good design practice provides most connections and members with proper drainage. If water ponding cannot be avoided, specify a waterproofing material to suit the specific needs of the project.

************************************************************************************************************

- CONNECTIONS

************************************************************************************************************

NOTE: Use AISC 341 Part I for all of the structural steel members and connections associated with SLRSs.

************************************************************************************************************

  - Except as modified in this section, connections not detailed must be designed per AISC [360] [341].

- Build connections into existing work.

- Do not tighten anchor bolts set in concrete with impact torque wrenches.

- Punch, subpunch and ream, or drill bolt holes perpendicular to the surface of the member.

- Bolts, nuts, and washers must be clean of dirt and rust, and lubricated as specified by the respective manufacturers.

  - Bolts

- ASTM A 307 [A 325] [A490] bolts must be tightened to "snug tight."

- "Snug tight" is achieved with a few impacts of an impact wrench, or the full effort of an ironworker using a spud wrench.

- If firm contact of joint plies cannot be obtained with snug tight, contact LANL for further instructions.

- Bolts that have been previously tensioned must not be reused.

  - [Pre-Tensioned High-Strength Bolts

************************************************************************************************************

NOTE: The four bolt tightening methods currently allowed by AISC will provide acceptable results if bolt assemblies are kept free of dirt and rust, if properly lubricated, and if proper installation procedures are followed.

If Turn-of-Nut pretensioning option is selected, either “with match-marking,” or “without match-marking” must be specified for the purpose of inspection.

************************************************************************************************************

************************************************************************************************************

NOTE: If the bracketed item is included for a job, delete the first sentence of the paragraph.

Slip-critical connections must be identified on the drawings.

************************************************************************************************************

    - ASTM A 325 and ASTM A 490 bolts must be fully tensioned per RCSC Spec, Table 8.1.

[a.	Provide [Tension Control bolts] [or] [Direct Tension Indicator washers] [turn-of-nut pretensioning] [calibrated wrench pretensioning] in all [ASTM A 325] [or] [ASTM A 490] bolted connections.].

b.	Bolts must be installed in connection holes and initially brought to a snug tight fit. After the initial tightening procedure, bolts must then be fully tensioned, progressing from the most rigid part of a connection to the free edges.

    - Installation of Direct Tension Indicator Washer (DTI)

        - ASTM F 959. Where possible, the DTI must be installed under the bolt head and the nut tightened.

        - If the DTI is installed adjacent to the turned element, provide a flat ASTM F 436 washer between the DTI and nut when the nut is turned for tightening, and between the DTI and bolt head when the bolt head is turned for tightening.

        - Orientation of DTI and ASTM F 436 washers must be as indicated in RCSC Spec, Figure C-8.1.]

- Gas Cutting

- Use of gas-cutting torch in the field for correcting fabrication errors will not be permitted on any major member in the structural framing.

- Use of a gas cutting torch will be permitted on minor members not under stress only after approval has been obtained from LANL.

- WELDING

************************************************************************************************************

NOTE: Projects involving AISC 341 must include para. E, and the type and extent of removal must be specified in accordance with the weld design(s).
************************************************************************************************************

- AWS D1.1. Provide AWS D1.1 qualified welders, welding operators, and tackers.

- AWS D1.8. Provide AWS D1.8 qualified welders, welding operators, and tackers as required.

[1.	Grind exposed welds smooth as indicated.]

- The Subcontractor must develop and submit the Welding Procedure Specifications (WPS) with supporting Procedure Qualification Records (PQRs) for all shop welding, including welding done using prequalified procedures.

- Welding Procedure Specifications, both prequalified and qualified, must be submitted for approval.

- Field welding will use LANL WPS’s by welders tested and certified by LANL at LANL.

- [Removal of Temporary Welds, Run-Off Plates, and Backing Strips]

- [SHOP PRIMER REPAIR

- [           ]].

- [GALVANIZING REPAIR

************************************************************************************************************

NOTE: Most structural steel is painted. If galvanized items are required, they must be indicated or specified. The galvanizing specified is by the hot-dip process. This process requires large amounts of energy and unevenly heats steel sections that may be large and/or thick, occasionally warping the steel sections. Using zinc coating by thermal spraying (metallizing) as an alternative to hot-dip galvanizing should be considered for certain steel sections. The following American Welding Society (AWS) publications should be consulted for further information:

TS-85 - Thermal Spraying - Practice, Theories, and Application

C2.2-67 - Recommended Practices for Metallizing with Aluminum and Zinc for Protection of Iron and Steel.

************************************************************************************************************

- Provide as indicated or specified.

    - Galvanize after fabrication where practicable.

    - Repair damage to galvanized coatings using ASTM A 780 zinc rich paint for galvanizing damaged by handling, transporting, cutting, welding, or bolting.

    - Do not heat surfaces to which repair paint has been applied.]

- [FIELD QUALITY CONTROL

  - Perform field tests, and provide labor, equipment, and incidentals required for testing.

- LANL must be notified in writing of defective welds, bolts, nuts, and washers within 7 working days of the date of inspection.

  - Welds

- Visual Inspection

- Furnish the services of AWS-certified welding inspectors for fabrication and erection inspection and testing and verification inspections.

- All welds must be visually inspected to AWS D1.1 Para. 6.9 and Table 6.1 category specified in drawings or specifications

- Welding inspectors must visually inspect and mark welds, including fillet weld end returns.

- Non-Destructive Testing

************************************************************************************************************

NOTE: The designer must indicate the location and extent of test welds and method(s) of testing desired. The following information is presented as guidance. Dye penetrant testing detects small surface defects by enhancing the visibility of the flaw. Magnetic particle testing detects surface cracks and near-surface cracks; this test provides more information than the dye penetrant testing, and for approximately the same cost. Ultrasonic and radiographic testing detect surface and internal cracks, delaminations, lack of fusion, and density and thickness variations; these tests offer basically the same information, but their usage is limited by location and type of weld. Generally, fillet welds can only be dye penetrant or magnetic particle tested. Complete penetration welds at butt joints should be radiographically tested; all other complete penetration welds should be ultrasonically tested.

************************************************************************************************************

- AWS D1.1. Test locations must be [as indicated] [selected by LANL].

- If more than [20] [_____] percent of welds made by a welder contain defects identified by testing, then all welds made by that welder must be tested by radiographic or ultrasonic testing, as approved by LANL.

- When all welds made by an individual welder are required to be tested, magnetic particle testing must be used only in areas inaccessible to either radiographic or ultrasonic testing. Retest defective areas after repair.

Testing frequency: Provide the following types and number of tests:

Test Method 					Number of Tests

Radiographic 					[_____]

Ultrasonic 					[_____]

Magnetic Particle 				[_____]

Dye Penetrant 				[_____]

- AWS D1.8 test locations must be as outlined in the Quality Plan ( see Para. 1.4.D)

- If more than [20] [_____] percent of welds made by a welder contain defects identified by testing, then all welds made by that welder must be tested by radiographic or ultrasonic testing, as approved by LANL.

- When all welds made by an individual welder are required to be tested, magnetic particle testing must be used only in areas inaccessible to either radiographic or ultrasonic testing. Retest defective areas after repair.

Testing frequency: Provide the following types and number of tests:

Test Method 					Number of Tests

Radiographic 					[_____]

Ultrasonic 					[_____]

Magnetic Particle 				[_____]

Dye Penetrant 				[_____]

  - Direct Tension Indicator Washer (DTI)

- DTI Compression

- DTIs must be tested in place to verify that they have been compressed sufficiently to provide the 0.015 inch gap as required by ASTM F 959.

- Gaps

- For DTIs, comply with requirements of ASTM F959.  Verify that gaps are less than gaps specified in Table 2 therein.

  - [Overhead, Top-Running Crane Rails and Beams

************************************************************************************************************

NOTE: Include paragraph for overhead, top-running cranes.  Underhung bridge cranes and monorail systems are normally provided with their own patented track systems and do not normally require the tight tolerances specified for overhead, top-running cranes.

************************************************************************************************************

- Survey runway rails and beams horizontally and vertically after installation to verify compliance with the tolerance requirements of CMAA 70 and the additional tolerance requirements specified in this section.

      - After each survey, submit a written report to LANL with the following information: field survey results, tolerance requirements, areas out of tolerance, and proposed corrective measures.

      - Proposed corrective measures must be approved by LANL.

      - Following completion of corrective measures, areas that were previously out of tolerance must be re-surveyed and another written report must be furnished to LANL.

      - [Field surveys must be performed and sealed by a registered land surveyor.]

  - High-Strength Bolts

************************************************************************************************************

NOTE: For paras. 1 and 2, use RCSC Spec.

************************************************************************************************************

    - Inspection by Subcontractor

- Inspect high-strength bolted connections per [RCSC Spec, Section 9].

- Inspect proper preparation, size, gaging location, and acceptability of welds; identification marking; operation and current characteristics of welding sets in use; [and calibration of torque wrenches for high-strength bolts.]

    - Testing

- LANL has the option to perform nondestructive tests on the installed bolts to verify compliance with pre-load bolt tension requirements.

- The test locations and amount / extent of testing will be selected by LANL.

  - [Pretensioned Joints

- Inspection

- Observe the pre-installation verification job site testing required by RCSC Spec, Section 7 and confirm that the procedure to be used provides the required tension.

- Monitor the work to ensure the testing procedures are routinely followed on joints that are specified to be fully tensioned.]

  - [Slip-Critical Joints

- Inspection

- In addition to the inspections required for pretensioned joints, confirm that the faying surfaces have been properly prepared before the connections are assembled.]

  - [Testing for Embrittlement

- ASTM A 143 for steel products hot-dip galvanized after fabrication.]

END OF SECTION

*******************************************************************************************************

Do not delete the following reference information:

*******************************************************************************************************

FOR LANL USE ONLY

This project specification is based on LANL Master Specification 05 1000 Rev. 4, dated April 23, 2012.