SECTION 05 1000

STRUCTURAL METAL FRAMING

************************************************************************************************************

This Section applies to structural steel for buildings that are designed in accordance with AISC 360 and/or 341*, facilities classified as Natural Phenomena Hazards (NPH) Risk Category (RC) I - IV facilities, and ML-3 and ML-4 projects.  In general, this section does not apply to nuclear facilities.  This section may apply to nuclear facilities that, because of the low amount of material at risk, are classified as RC II or RC IV.

For nuclear facilities, ML-1 / ML-2 projects (and ML-3 potentially), and NPH Design Category (NDC) 3 - 4, this Section must be further amplified and developed.  This would include considering design requirements from DOE STD-1020, AISC N690; “Quality Assurance Requirements” from DOE O 414.1D, and 10 CFR Part 830 Subpart A; and “Safety Basis Requirements” from 10 CFR Part 830 Subpart B.  Also, use additional quality assurance requirements from DOE G 414.1-2B as applicable.  Independent review would also be required.

The ESM Ch. 5 Sect. I ‘crosswalk tables’ between the old NPH Performance Category designations (i.e., PC-1 - PC-3) and the current designations (i.e., RCs and NDCs) should be reviewed by those using this section for work in existing facilities (that are still ‘PC-based’).

*   Refer to ESM Chapter 5, Part II, paragraph 7.0, which references the International Building Code (IBC), Chapter 22.  IBC Section 2205, Structural Steel, contains provisions governing the quality, design, fabrication and erection of steel used structurally in buildings or structures.  It is the intent of this and other Metals Division sections of the specifications to address those provisions pertaining to quality, fabrication and erection; however, the specifier is ultimately responsible for ensuring ALL para. 7.0 and Chapter 22 provisions are complied with on a given project.

Edit this template for each project. In doing so, Specifier must add job-specific requirements.

Brackets are used in the text to indicate where text must be supplied by the Specifier. Once the choice is made or text supplied, remove the brackets. The specifications must also be edited to delete specification requirements for materials, systems, processes, items, or designs that are not included in the Project-- and Specifier's notes such as these. Additional tailoring requirements are contained in ESM Chapter 1 Section Z10 Att. F, Specifications.

To seek a variance from requirements in the specifications that are applicable, contact the Engineering Standards Manual Structural Specs POC.  Please contact POC with suggestions for improvement as well.
When assembling a specification package, include applicable specifications from all Divisions, especially Division 1, General requirements.

NOTES:

- With the exception of composite flexural members (i.e., floor beams), composite construction at LANL is seldom used; hence, it is not addressed herein.  If composite construction is to be used on a given project, edit this Section as necessary to ensure compliance with IBC Chapter 22, Section 2206.

- Architecturally Exposed Structural Steel (AESS) is not included herein.  If AESS is required then a new Section must be created.  Refer to AIA MasterSpec Sect. 051213.

- In addition to the requirements of IBC Sect. 1603, the project drawings must meet the requirements of the AISC 360, Ch. A, Sect. A4*, Section 3 and, as applicable, AISC 341, Ch. A, Sect. A4.  *Despite the reference in A4 to AISC 303 (Sect. 3), 360 does contain several drawing requirements; these are summarized in the commentary to A4.

************************************************************************************************************

PART 1 GENERAL

- RELATED SectionS

  - Division 01 Specification Sections apply to this Section.

- SUMMARY

- Section includes:

  - Structural steel.

  - Field-installed shear connectors.

- Related requirements:

************************************************************************************************************

Retain subparagraphs below to cross-reference requirements Construction Subcontractor might expect to find in this Section but are specified in other Sections.

Regarding 05 3100 and field-installed shear connectors, all that is provided is an ‘installation’ sentence saying shear stud connectors are to be welded through steel deck to structural members below.  Everything else required to specify shear studs is contained herein (i.e., in 05 1000).

************************************************************************************************************

Section 03 6000 Grout.

Section 05 3100 Metal Decking for field installation of shear connectors through deck.

Section 05 5000 Metal Fabrications for [steel lintels and shelf angles not attached to structural-steel frame] [miscellaneous steel fabrications] [and] [other steel items] not defined as structural steel.

[Section 09 9100 Painting] for surface-preparation and priming requirements.

[Section 13 3419 Metal Building Systems for structural steel.]

[Section 41 2213.13 Bridge Cranes for structural steel.]

- REFERENCES

The publications listed below form a part of this specification to the extent referenced. The publications are referred to in the text by the basic designation only.

- American Institute of Steel Construction (AISC)

- AISC 303 	Code of Standard Practice for Steel Buildings and Bridges

- AISC 341 	Seismic Provisions for Structural Steel Buildings

- AISC 360 	Specification for Structural Steel Buildings

- ASTM International (ASTM)

- ASTM A 6 	General Requirements for Rolled Structural Steel Bars,

Plates, Shapes, and Sheet Piling

- ASTM A 36 	Carbon Structural Steel

- ASTM A 53 	Pipe, Steel, Black and Hot-Dipped, Zinc-Coated Welded

and Seamless

- ASTM A 123 	Zinc (Hot-Dip Galvanized) Coatings on Iron and Steel

Products

- ASTM A 108 	Steel Bar, Carbon and Alloy,

Cold-Finished

- ASTM A 153 	Zinc Coating (Hot-Dip) on Iron and Steel Hardware

- ASTM A 307 	Carbon Steel Bolts and Studs, 60,000 psi Tensile Strength

- ASTM A 325 	Structural Bolts, Steel, Heat Treated, 120/105 ksi Minimum

Tensile Strength

- ASTM A 500 	Cold-Formed Welded and Seamless Carbon Steel

Structural Tubing in Rounds and Shapes

- ASTM A 529 	High-Strength Carbon-

Manganese Steel of Structural Quality

- ASTM A 563 	Carbon and Alloy Steel Nuts

- ASTM A 572 	High-Strength Low-Alloy Columbium-Vanadium of

Structural Steel

- ASTM A 700	Practices for Packaging, Marking, and Loading Methods

for Steel Products for Shipment

- ASTM A 780 	Repair of Damaged and Uncoated Areas of Hot-Dip

Galvanized Coatings

- ASTM A 992 	Structural Steel Shapes

- ASTM B 695	Coatings of Zinc Mechanically Deposited on Iron and Steel

- ASTM F 436 	Hardened Steel Washers

- ASTM F 959 	Compressible-Washer-Type Direct Tension Indicators for

Use with Structural Fasteners

- ASTM F 1554	Anchor Bolts, Steel, 36, 55, and 105-ksi Yield Strength

- ASTM F 1852	Twist Off Type Tension Control Structural Bolt/Nut/Washer

Assemblies, Steel, Heat Treated, 120/105 ksi Minimum Tensile Strength

- American Welding Society (AWS)

- AWS D1.1 	Structural Welding Code – Steel

- AWS D1.8 	Structural Welding Code - Seismic Supplement

- Master Painters Institute (MPI)

- MPI #18	Single Component Organic Zinc-Rich Primer

- MPI #19	Inorganic Zinc-Rich Primer

- MPI #79	Alkyd Anti-Corrosive Metal Primer

- Research Council on Structural Connections (RCSC)

- RCSC Spec*	Specification for Structural Joints Using ASTM A325 or

A490 Bolts

* Some documents refer to this as AISC 348.

- The Society for Protective Coatings (SSPC) and National Association of Corrosion Engineers International (NACE)

- SSPC-PA 1			Shop, Field, and Maintenance Painting of

Steel

- SSPC-Paint 20 		Paint Specification No. 20 Zinc-Rich

Primers (Type I, “Inorganic,” and

Type II, “Organic”).

- SSPC-Paint 23 		Paint Specification No. 23 Latex Primer for

Steel Surfaces.

- SSPC-Paint 25		Paint Specification No. 25 Zinc Oxide,

Alkyd, Linseed Oil Primer for Use Over

Hand Cleaned Steel Type I and Type II.

- SSPC-PAINT 25 BCS		Paint Specification No. 25 BCS Zinc Oxide,

Alkyd, Linseed Oil Primer for Use over Blast

Cleaned Steel.

- SSPC-PS Guide 7.00	Painting System Guide 7.00:  Guide for

Selecting One-Coat Shop Painting 	Systems.

- SSPC-SP 1			Solvent Cleaning

- SSPC-SP 2			Hand Tool Cleaning

- SSPC-SP 3			Power Tool Cleaning

- SSPC-SP 7/			Brush-off Blast Cleaning

NACE No. 4

- SSPC-SP 11			Power Tool Cleaning to Bare Metal

- SSPC-SP 14/			Industrial Blast Cleaning

NACE No. 8

- SSPC-SP 6/			Commercial Blast Cleaning

NACE No. 3

- definitions

************************************************************************************************************

After Section has been edited for a Project, retain applicable terms below.

************************************************************************************************************

  - Structural Steel: Elements of the structural frame indicated on Drawings and as described in AISC 303, "Code of Standard Practice for Steel Buildings and Bridges.

  - Seismic Force-Resisting System: Elements of structural-steel frame designated as "SFRS" or along grid lines designated as "SFRS" on Drawings, including columns, beams, and braces and their connections.

  - Protected Zone: Area of structural members or connections designated as "Protected Zone" on Drawings. Limitations apply to fabrication and attachments in such areas.

  - Demand Critical Welds: Those welds, the failure of which would result in significant degradation of the strength and stiffness of the SFRS and which are designated as "Demand Critical" on Drawings.

- COORDINATION

************************************************************************************************************

Retain first paragraph below if primers are fully specified in this Section rather than in painting Section.

************************************************************************************************************

        - Coordinate selection of shop primers with topcoats to be applied over them. Comply with paint and coating manufacturers' written recommendations to ensure that shop primers and topcoats are compatible with one another.

        - Coordinate installation of anchorage items to be embedded in or attached to other construction without delaying the Work. Provide setting diagrams, sheet metal templates, instructions, and directions for installation.

- ACTION SUBMITTALS

- Product Data:  For each type of product.

- Shop Drawings:

  - Include details of cuts, connections, splices, camber, holes, and other pertinent data.

  - Include embedment Drawings.

  - Indicate welds by standard AWS symbols, distinguishing between shop and field welds, and show size, length, and type of each weld. Show backing bars that are to be removed and supplemental fillet welds where backing bars are to remain.

  - Indicate type, size, and length of bolts, distinguishing between shop and field bolts. Identify pretensioned and slip-critical, high-strength bolted connections.

  - Identify members and connections of the SFRS.

  - Indicate locations and dimensions of protected zones.

  - Identify demand critical welds.

- Erection Drawings.

- Welding Procedure Specification (WPS) and Procedure Qualification Record (PQR):

  - Shop:

    - Prior to shop welding, submit WPS and supporting PQR meeting the requirements of AWS D1.1 and, as applicable, AWS D1.8 for the processes and materials that will be used for welding.

  - Field:

    - Prior to field welding, submit LANL WPS meeting the requirements of AWS D1.1 and, as applicable, AWS D1.8 for the processes and materials that will be used for welding.

************************************************************************************************************

Retain "Delegated-Design Submittal" Paragraph below if fabricator is responsible for selecting or completing details of structural-steel connections required to withstand specific design loads. Professional engineer is defined in Section 01 4000 Quality Requirements.

************************************************************************************************************

- Delegated Design Submittal:  For structural-steel connections indicated to comply with design loads, include analysis data signed and sealed by the professional engineer, registered in the State of New Mexico, responsible for their preparation.

- INFORMATIONAL SUBMITTALS

************************************************************************************************************

Informational submittals must be limited to those necessary for adequate quality control. The importance of an item, or complexity, in the context of the project should determine whether or not a submittal is required.

Retain "Qualification Data" Paragraph below with qualification requirements in Section 01 4000 Quality Requirements and as may be supplemented in "Quality Control" Article.
************************************************************************************************************

  - Qualification Data: For [Installer] [fabricator] [shop-painting applicators] [professional engineer] [Quality Control Inspector].

************************************************************************************************************

Retain "Welder Performance Qualification Records” Paragraph below if retaining "Welding Qualifications" Paragraph in "Quality Control" Article.

************************************************************************************************************

  - Welder Performance Qualification Records (WPQR).

************************************************************************************************************

Consider retaining "Paint Compatibility Certificates" Paragraph below if primers are fully specified in this Section rather than in painting Section.

************************************************************************************************************

  - Paint Compatibility Certificates: From manufacturers of topcoats applied over shop primers, certifying that shop primers are compatible with topcoats

************************************************************************************************************

Coordinate first paragraph below with qualification requirements in Section 01 4000 Quality Requirements.

************************************************************************************************************

  - Certified material test reports for structural steel, structural fasteners, and weld filler material, including chemical and physical properties.

  - Product Test Reports: For the following:

************************************************************************************************************

Revise list below to suit Project. Insert alternative design bolts if required.

************************************************************************************************************

- Revise list below to suit Project. Insert alternative design bolts if required.

    - Bolts, nuts, and washers including mechanical properties and chemical analysis.

    - Direct-tension indicators.

    - Tension-control, high-strength, bolt-nut-washer assemblies.

    - Shear stud connectors.

    - Shop primers.

    - <Insert product>.

- Survey of existing conditions

- SUSTAINABLE DESIGN SUBMITTALS

  - Product Data:  For products having recycled content, documentation indicating percentages by weight of postconsumer and pre-consumer recycled content.  Include statement indicating cost for each product having recycled content.

  - Laboratory Test Reports for Credit IEQ 4.2: For primers, documentation indicating that products comply with the testing and product requirements of the California Department of Public Health's (formerly, the California Department of Health Services') "Standard Method for the Testing and Evaluation of Volatile Organic Chemical Emissions from Indoor Sources Using Environmental Chambers."

- QUALITY CONTROL

************************************************************************************************************

AISC 360 Ch. N & AISC 341 Ch. J distinguish between quality control (QC) and quality assurance (QA):

- QC is what is contained herein, & is the responsibility of the Construction Subcontractor (i.e., fabricator & erector).

- QA (which is also required by IBC Ch, 17) is contained in the EOR’s Statement of Special Inspections (SSI), & is the responsibility of LANL (i.e., execution of the SSI).  The SSI template is found in ESM Ch. 16, Sect. IBC-IP, Attach. B.

Although AISC has a certification program for fabricators, and there are some in NM, LANL has evaluated them and found this cert to be insufficient to ensure quality.  Thus, the Fabricator Qualifications para. below doesn’t mention AISC certification.

Also, although AISC has a certification program for installers/erectors, there are none in NM at time of writing; therefore, there is no para. below for Installer Qualifications.  The same goes for AISC Sophisticated Paint Endorsements and SSPC-qualified paint shops.

The list referred to in first para. below is found in LANL ESM Chapter 16, Section IBC-GEN, “Listing of Approved IBC Testing Agencies and Fabricators.”

************************************************************************************************************

  - Fabricator Qualifications:  The fabricator shall be approved by LANL.  LANL maintains a list of pre-approved fabricators.  If use of a non-pre-approved fabricator is desired, several months shall be allowed for in the Project schedule in order to obtain LANL approval; and the cost associated with such shall be at the Subcontractor’s expense.

  - Quality Control Inspector (QCI) Qualifications:  The qualifications of the QCI(s) engaged by the fabricator and/ or the erector shall comply with the applicable provisions in Section 01 4000, Quality Requirements, and AISC 360 Chapter N, paragraph N4.1.

************************************************************************************************************

Retain subparagraph below if Project includes a SFRS.

AISC 360 & 341 define NDT as being a QA responsibility; however, the “Scope para.” in the respective “QA – QC chapters (i.e., N1 & J1)” allows for the LBO to have it performed by an LBO-approved fabricator.  This “allowance” is not exercised herein for the following reasons:

  - The NDT-related qualifications in ‘360’ would have to be added herein (as a new para.),

  - The NDT-related qualifications in ‘341’ would have to be added to subpara. below,

  - The subsequent Source QC para. (in PART 2) would have to include project-specific NDT requirements (e.g., the applicable NDT method(s), the extent of testing, distinguishing between “seismic & non-seismic” for the methods & extent, etc.), &

  - Welds completed by the erector aren’t included in the allowance (so they must be “QA-ed”, which would “blur the lines” between QA & QC in this Section).

************************************************************************************************************

    - SFRS QCI Qualifications:  In addition to QCI Qualifications (stated above), the qualifications of the QCI(s) engaged by the fabricator and/ or the erector of the SFRS shall comply with the following:

      - Visual welding inspection shall be conducted by personnel qualified in accordance with AWS D1.8 clause 7.2.

************************************************************************************************************

Retain appropriate subparagraph(s) under paragraph below if shop and /or field welding is required. If retaining, also retain "Welding certificates" Paragraph in "Informational Submittals" Article.

************************************************************************************************************

  - Welding Qualifications:

    - Shop.

- Prior to shop welding, submit WPQR certification for each welder stating the type of welding and positions qualified for, the code and procedure qualified under, date qualified, and the firm and individual certifying the qualification tests.

- If the qualification date of the welding operator is more than 180 days old, the welding operator's qualification certificate must be accompanied by a current certificate by the welder attesting to the fact that he has been engaged in welding since the date of certification, with no break in welding service greater than 6 months.

    - Field.

- Refer to Section 01 4455 Onsite Welding and Joining Requirements.

***********************************************************************************************************

Retain subparagraph below if Project includes welding of /in an SFRS(s).

***********************************************************************************************************

3.         Welders and welding operators performing work on bottom-flange, demand-critical welds shall pass the supplemental welder qualification testing, as required by AWS D1.8.  FCAW-S and FCAW-G shall be considered separate processes for welding personnel qualification.

  - Comply with applicable provisions of the following specifications and documents:

************************************************************************************************************

Retain references in subparagraphs below if applicable. Insert others to suit Project.

************************************************************************************************************

- AISC 303.

- AISC 360.

- RCSC SPEC.

- AISC 341.

- DELIVERY, STORAGE, AND HANDLING

- Comply with any /applicable portions of AISC 303 Chapter 6, Shop Fabrication and Delivery.

- Package, mark, and load steel products in accordance with ASTM A700.

- Deliver, store and handle materials:

    - With equipment of adequate capacity.

    - Without overstressing or permanently deflecting material or any supporting structures.

    - Without damaging finish.

- Deliver manufactured materials in original unopened packages, containers, or bundles with manufacturer's label intact and legible.

  - Fasteners may be repackaged provided LANL's testing and inspecting agency observes repackaging and seals containers.

  - Clean and relubricate bolts and nuts that become dry or rusty before use.

  - Comply with manufacturers' written recommendations for cleaning and lubricating ASTM F 1852 fasteners and for retesting fasteners after lubrication.

- Inspect fasters and structural steel upon receipt at site including the following:

  - Item identification and marking

  - Shipping damage has not occurred

  - Required documentation has been provided and is acceptable.

  - Suspect/counterfeit items have not been provided.

- Store materials in designated areas that are well drained (preferably gravel covered or paved), off ground, under cover, and away from damp surfaces.

- Store materials in areas reasonably removed from the actual construction area and traffic so that the possibility of damage from construction equipment is minimized.

- Store primer materials in accordance with manufacturer’s recommendations.

- Remove damaged, unlabeled or unsatisfactory materials which do not meet this specification from the job site.

PART 2 PRODUCTS

- PERFORMANCE REQUIREMENTS

************************************************************************************************************

Retain "Connections" Paragraph below if fabricator is responsible for selecting or completing details of structural-steel connections required to withstand specific design loads. AISC 303 requires that connection details be submitted for approval if fabricator selects or completes them.

************************************************************************************************************

  - Connections: Provide details of [simple shear] connections required by the Contract Documents to be selected or completed by structural-steel fabricator, including comprehensive engineering analysis by a qualified professional engineer, to withstand loads indicated and comply with other information and restrictions indicated.

************************************************************************************************************

Revise subparagraphs below if design of complex connections is delegated to fabricator's qualified professional engineer.

************************************************************************************************************

    - Select and complete connections using [schematic details indicated] [and] [AISC 360] [Insert source].

    - Use [Load and Resistance Factor Design; data are given at factored-load level] [Allowable Stress Design; data are given at service-load level].

  - Moment Connections:  [Type PR, partially] [Type FR, fully] restrained.

  - Construction:  [Moment frame] [Braced frame] [Shear wall system] [Combined system of moment frame and braced frame] [Combined system of moment frame and shear walls] [Combined system of braced frame and shear walls] [Combined system of moment frame, braced frame, and shear walls].

- STRUCTURAL STEEL

- Recycled Content of Steel Products:

          - Postconsumer recycled content:

            - Basic Oxygen Furnace:  16%

            - Electric Arc Furnace:  67%

Recovered Materials:

Basic Oxygen Furnace:  25 - 30%

Electric Arc Furnace:  100%

************************************************************************************************************

Only the “preferred material specification” from AISC Manual, Part 2 are included here; however, since there are many other material specifications permissible per AISC 360, the specifier is free to require otherwise, provided that he/she first confirms availability.

************************************************************************************************************

************************************************************************************************************

AISC 341 Part I imposes special material requirements on the structural steel and connection materials used in SFRSs.  Some of these requirements are included herein; however, AISC 341 should be consulted for assurance /further detail.

************************************************************************************************************

- Non-W-Shapes, Plates, and Bars

************************************************************************************************************

ASTM A 36 is a general purpose structural grade steel, with a minimum yield strength (Fy) of 36 ksi, and its use is preferred for M, S, C, MC, and L shapes. Increased corrosion resistance in non-marine environments can be obtained by specifying a minimum copper percentage of 0.2 percent.

************************************************************************************************************

- ASTM A 36 [ASTM A 529, Grade 50.] [ASTM A 572, Grade 50] [ASTM A 529, Grade 50] [              ].

- W-Shapes

************************************************************************************************************

ASTM A 992 is the preferred steel type for W-shapes (rolled wide flange shapes) intended for use in building framing.

************************************************************************************************************

  - ASTM A 992 [ASTM A 529, Grade 50] [ASTM A 572, Grade 50 ] [ASTM A 529, Grade 50]; [                 ].

- Steel Pipe

************************************************************************************************************

ASTM A 53 pipe, Grade B has Fy = 35 ksi and is available in the following weight classes: Std (Standard), x-Strong (Extra Strong), and xx-Strong (Double-extra Strong).

************************************************************************************************************

- ASTM A 53, Grade B, weight class [Std] [x-Strong] [xx-Strong].

- Hollow Structural Steel (HSS) / Structural Steel Tubing

************************************************************************************************************

The preferred material specification for HSS / structural tubing is ASTM A 500 Grade B, which has Fy = 42 (for round HSS) and 46 ksi (for rectangular HSS).  ASTM A 500 may not be suitable for dynamically loaded structures or applications requiring notch strength.

************************************************************************************************************

- ASTM A 500, Grade B, Minimum Yield Strength = [_____]ksi [          ].

************************************************************************************************************

Retain second subparagraph below for SFRS welds (per AISC 341 Ch. A).

************************************************************************************************************

- Welding Filler Metals/ Electrodes and Rods

    - AWS D1.1 Table 3.1.

    - [Sesimic Force Resisting System Welds:  AWS D1.8, clause 6.3 (i.e., all subclauses that apply).]

- BOLTS,  connectors, And Anchors

************************************************************************************************************

AISC 360 Ch. J says, “Snug-tightened joints or joints with ASTM A307 bolts shall be permitted except where otherwise specified.”  And the commentary to Ch. M says, “It is suggested that snug-tight bearing-type connections with ASTM A325…bolts be used in applications where ASTM A307 bolts are permitted.”  Finally, the AIA MasterSpec-Evaluations says, “…ASTM A 307…may be used for temporary bracing and connection of minor elements, but their use has generally ceased for bolted connections.”  Given all of the above, ASTM A307 bolts are not included herein.

************************************************************************************************************

************************************************************************************************************

Do not mix bolt material specifications ASTM A 325 and ASTM A 490 (not included herein, add if necessary) on the same diameter bolts in high-strength connections.

Do not place ASTM A 325 (or ASTM A 490), which have a hardness equal or in excess of Rockwell C-32, in contact with a galvanized surface.

If using A325 bolts for some connections and A490 bolts for others, indicate location of each on Drawings.

************************************************************************************************************

************************************************************************************************************

AISC 341 requires all bolts in SFRSs to be pre-tensioned high-strength bolts.

************************************************************************************************************

************************************************************************************************************

Washer requirements in Paragraphs A and B do not comply with RCSC Spec Table 6.2.1 in all situations involving oversized and slotted holes in the outer ply.  If such holes apply to Project, refer to Table 6.2.1 and edit washer requirements accordingly.

************************************************************************************************************

A.	High-Strength Bolts, Nuts, and Washers: ASTM A 325, Type 1, heavy-hex steel structural bolts; ASTM A 563, Grade C, heavy-hex carbon-steel nuts; and ASTM F 436, Type 1, hardened carbon-steel washers; all with plain finish.

************************************************************************************************************

Retain subparagraph below if applicable.

************************************************************************************************************

- Direct-Tension Indicators: ASTM F 959, Type 325, compressible-washer type with plain finish.

B.	Zinc-Coated High-Strength Bolts, Nuts, and Washers: ASTM A 325, Type 1, heavy-hex steel structural bolts; ASTM A 563, Grade DH heavy-hex carbon-steel nuts; and ASTM F 436, Type 1, hardened carbon-steel washers.

- Finish: [Hot-dip zinc coating] [Mechanically deposited zinc coating] [Hot-dip or mechanically deposited zinc coating].

- Direct-Tension Indicators: ASTM F 959, Type 325, compressible-washer type with [mechanically deposited zinc coating] [mechanically deposited zinc coating, baked epoxy-coated] finish.

************************************************************************************************************

Tension-control (twist-off) bolt assemblies in Paragraph below correspond to strength of ASTM A 325 bolts.

************************************************************************************************************

- Tension-Control, High-Strength Bolt-Nut-Washer Assemblies: ASTM F 1852, Type 1, [heavy-hex] [round] head assemblies consisting of steel structural bolts with splined ends, heavy-hex carbon-steel nuts, and hardened carbon-steel washers.

  - Finish: [Plain] [Mechanically deposited zinc coating].

************************************************************************************************************

Retain "Shear Connectors" Paragraph below if shop or field welding of shear studs to steel framing is required. Similar applies to Paragraph of the same title in Erection article.

************************************************************************************************************

- Shear Connectors: ASTM A 108, Grades 1015 through 1020, headed-stud type, cold-finished carbon steel; AWS D1.1, Type B.

************************************************************************************************************

Retain appropriate materials in the two (2) Anchor-Rods paragraphs below or revise if other materials are required. AISC uses the generic term "anchor rods" to include hooked, headed, and threaded and nutted rods.

Use of hooked anchors for resisting tensile loads is discouraged by AISC; they prefer use of headed, or threaded & nutted, rods in such situations.

Use of anchor rods for resisting large shear loads is discouraged by AISC; they prefer use of something else (e.g., shear lugs, etc.) in such situations.

Per AISC Manual, Part 14, ASTM A 36 plate washers are typically used in base-plate applications (due to their typical holes being larger than oversized ones).  See Part 14, Table 14-2 for more detail, and edit the following washer requirements accordingly.

************************************************************************************************************

        - Unheaded Anchor Rods: ASTM F 1554, Grade 36 [ASTM F 1554, Grade 55, weldable] [             ].

Configuration: [Straight] [Hooked].

Nuts: ASTM A 563 heavy-hex carbon steel.

Plate Washers: ASTM A 36 carbon steel.

Washers: ASTM F 436, Type 1, hardened carbon steel.

Finish: [Plain] [Hot-dip zinc coating, ASTM A 153, Class C] [Mechanically deposited zinc coating, ASTM B 695, Class 50].

Headed Anchor Rods: ASTM F 1554, Grade 36 [ASTM F 1554, Grade 55, weldable] [            ], straight with heavy-hex head.

Nuts: ASTM A 563 heavy-hex carbon steel.

Plate Washers: ASTM A 36 carbon steel.

Washers: ASTM F 436, Type 1, hardened carbon steel.

Finish: [Plain] [Hot-dip zinc coating, ASTM A 153, Class C] [Mechanically deposited zinc coating, ASTM B 695, Class 50].

Threaded Rods: [ASTM A 36] [ASTM A 193, Grade B7] [ASTM A 354, Grade BD] [ASTM A 449] [ASTM A 572/A 572M, Grade 50].

Nuts: ASTM A 563 [heavy-]hex carbon steel.

Washers: [ASTM F 436, Type 1, hardened] [ASTM A 36] carbon steel.

Finish: [Plain] [Hot-dip zinc coating, ASTM A 153, Class C] [Mechanically deposited zinc coating, ASTM B 695, Class 50].

[Clevises] [and] [Turnbuckles]: Made from cold-finished carbon steel bars, ASTM A 108, Grade 1035.

Eye Bolts and Nuts: Made from cold-finished carbon steel bars, ASTM A 108, Grade 1030.

Sleeve Nuts: Made from cold-finished carbon steel bars, ASTM A 108, Grade 1018.

************************************************************************************************************

Retain Paragraph below if applicable.  If applicable, but bearing is required to allow movement along more than one axis, revise Paragraph.

************************************************************************************************************

- Structural Slide Bearings: Low-friction assemblies, of configuration indicated, that provide vertical transfer of loads and allow horizontal movement perpendicular to plane of expansion joint while resisting movement within plane of expansion joint.

************************************************************************************************************

Retain subparagraph below and list of manufacturers below it to require products from manufacturers listed or a comparable product from other manufacturers.

************************************************************************************************************

- Manufacturers: Subject to compliance with requirements, [provide products by the following] [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

************************************************************************************************************

Retain subparagraph below and list of manufacturers below it to identify a specific product or a comparable product from manufacturers listed. Retain option and delete insert note if manufacturer's name and model number are indicated on Drawings.

************************************************************************************************************

- Basis-of-Design Product: Subject to compliance with requirements, provide [product indicated on Drawings] [Insert manufacturer's name; product name or designation] or comparable product by one of the following:

Amscot Structural Products Corp.

Fluorocarbon Company Limited.

R.J. Watson Bridge & Structural Engineered Systems.

Seismic Energy Products, L.P.

[                                          ].

- Mating Surfaces: [PTFE and PTFE] [PTFE and mirror-finished stainless steel].

- Coefficient of Friction: Not more than [0.03] [0.04] [0.05] [0.06] [0.10] [0.12] [            ].

- Design Load: Not less than [2,000 psi] [5,000 psi] [6,000 psi] [             ].

************************************************************************************************************

Total movement capability includes movement in both directions (i.e., left and right of expansion joint) and is generally twice the dimension of the expansion joint.

************************************************************************************************************

- Total Movement Capability: [2 inches] [                   ].

- PRIMER

************************************************************************************************************

For assistance with proper specification of the content that follows, refer to AIA MasterSpec – Evaluations, Structural Steel Framing, 051200 (pp. E8 – E11).

Insert proprietary primers if required as part of special coating or painting system.  Coordinate primer selection with surface preparation and topcoats, requirements for slip-critical joints, and limitations of sprayed fire-resistive materials.  Insert color if required.

************************************************************************************************************

- Primer: Comply with Section 09 9100 Painting.

************************************************************************************************************

Primer in Paragraph below requires SSPC-SP 2 surface preparation or better and 24-hours of drying before recoating. Type II has lower VOC content than Type I.

************************************************************************************************************

- Primer: SSPC-Paint 25, [Type I] [Type II], zinc oxide, alkyd, linseed oil primer.

************************************************************************************************************

Primer in Paragraph below requires SSPC-SP 6/NACE No. 3 commercial blast-cleaning surface preparation or better and 24 hours' drying before recoating. Type II has lower VOC content than Type I.

************************************************************************************************************

- Primer: SSPC-Paint 25 BCS, [Type I] [Type II], zinc oxide, alkyd, linseed oil primer.

************************************************************************************************************

Primer in first "Primer" Paragraph below requires SSPC-SP 6/NACE No. 3 commercial blast-cleaning surface preparation or better and 24 hours' drying before recoating. SSPC recommends two primer coats before exposing steel to exterior, and one or two topcoats.

************************************************************************************************************

- Primer: SSPC-Paint 23, latex primer.

************************************************************************************************************

Verify that fabricator offers primers that meet limitations and characteristics in Paragraph below. Fabricator's standard primer requires SSPC-SP 2 surface preparation or better and usually provides minimal protection.

************************************************************************************************************

- Primer: Fabricator's standard lead- and chromate-free, nonasphaltic, rust-inhibiting primer complying with MPI#79 and compatible with topcoat.

- Galvanizing Repair Paint: [MPI#18, MPI#19, or SSPC-Paint 20] [ASTM A 780].

- fabrication

        - Structural Steel: Fabricate and assemble in shop to greatest extent possible. Fabricate according to AISC 303, and to AISC 360.

- Camber structural-steel members where indicated.

- Fabricate beams with rolling camber up.

- Identify high-strength structural steel according to ASTM A 6 and maintain markings until structural steel has been erected.

- Mark and match-mark materials for field assembly.

************************************************************************************************************

Retain subparagraph below if shop priming is required.

************************************************************************************************************

- Complete structural-steel assemblies, including welding of units, before starting shop-priming operations.

        - Thermal Cutting: Perform thermal cutting by machine to greatest extent possible.

- Plane thermally cut edges to be welded to comply with requirements in AWS D1.1.

************************************************************************************************************

Retain option in Paragraph below if permitted. RCSC SPEC has restrictions on thermally cut bolt holes.  The option below is permitted in statically loaded joints. Revise standard bolt holes to oversized, short-slotted, or long-slotted bolt holes if permitted, and indicate locations of each type on Drawings.

************************************************************************************************************

- Bolt Holes: Cut, drill, [mechanically thermal cut,] or punch standard bolt holes perpendicular to metal surfaces.

- Finishing: Accurately finish ends of columns and other members transmitting bearing loads.

************************************************************************************************************

Retain Paragraph below for unpainted structural steel. Delete if shop coating is required and retain applicable requirements in "Shop Priming" Article. Default cleaning in AISC 303 requires use of solvent cleaner (i.e., SSPC-SP 1) as well as a hand-tool (i.e., SSPC-SP 2) “…or other suitable means.”

************************************************************************************************************

- Cleaning: Clean and prepare steel surfaces that are to remain unpainted according to [SSPC-SP 1.] [SSPC-SP 2.] [SSPC-SP 3.]

************************************************************************************************************

Retain "SFRS Bolted Joints" Paragraph below if Project includes a SFRS that contains bolted-joint connections.

AISC 341 requires all bolts to be installed as pretensioned high-strength bolts.  Faying surfaces must be prepared as required for slip-critical connections per AISC 360 Sect. J3.8, achieving at least a Class A slip coefficient*.  Any/ all options in paragraph below will result in satisfactory faying surfaces.

*There are two exceptions – end plate moment connections and bolted joints that don’t transfer load via shear – see AISC 341 para. D2.2(4) for more detail.

For faying surfaces of bolted joints not associated with a SFRS, only the RCSC SPEC requirements need be met:

- RCSC does not impose any restrictions on the use of uncoated, coated, or galvanized faying surfaces in sung-tightened and pretensioned joints; however, this is not the case for slip-critical (S-C) joints.

- If S-C joints are included in Project, the applicable RCSC (para. 3.2.2) restrictions must be met.  Any/ all options in paragraph below will result in satisfactory faying surfaces.

- Retain both options in para. if Project includes S-C joints in addition to SFRS bolted joints

- If Project doesn’t includes S-C joints, but not SFRS bolted joints, retain first option only & delete the term“SFRS.”

Based on final content of para. below, coordinate content of ALL subsequent portions of this Section that affect/ deal with surface preparation and coating type.

While these requirements pertain to shop connection & field connections, it’s not likely that the Subcontractor responsible for the latter will have any control over faying surfaces.

************************************************************************************************************

- [Slip-Critical] [and] SFRS Bolted Joints:  The faying surfaces of bolted joints in the SFRS shall be [unpainted clean mill scale steel surfaces] [, or surfaces with Class A coatings (per RCSC SPEC Appendix A) on blast-cleaned steel] [, or hot-dipped galvanized and roughened surfaces (per RCSC SPEC paragraph 3.2.2(c)].

************************************************************************************************************

Retain "Shear Connectors" Paragraph below if shear connectors are shop installed to structural steel. ************************************************************************************************************

- Shear Connectors: Prepare steel surfaces as recommended by manufacturer of shear connectors. Use automatic end welding of headed-stud shear connectors according to AWS D1.1 and manufacturer's written instructions.

************************************************************************************************************

Retain "Steel Wall-Opening Framing" Paragraph below if steel wall-opening framing is required and included in this Section. ************************************************************************************************************

- Steel Wall-Opening Framing: Select true and straight members for fabricating steel wall-opening framing to be attached to structural-steel frame. Straighten as required to provide uniform, square, and true members in completed wall framing. Build up welded framing, weld exposed joints continuously, and grind smooth.

************************************************************************************************************

Retain "Welded Door Frames" Paragraph below if structural-steel-welded door frames attached to structural-steel frame are required. Welded door frames are usually used in industrial buildings, but they may be used in other types of buildings for large door openings. Coordinate requirements with Drawings. ************************************************************************************************************

- Welded Door Frames: Build up welded door frames attached to structural-steel frame. Weld exposed joints continuously and grind smooth. Plug-weld fixed steel bar stops to frames. Secure removable stops to frames with countersunk machine screws, uniformly spaced not more than 10 inches o.c. unless otherwise indicated.

- Holes: Provide holes required for securing other work to structural steel and for other work to pass through steel members.

************************************************************************************************************

Delete option in first subparagraph below if allowing thermally cut holes. ************************************************************************************************************

- Delete option in first subparagraph below if allowing thermally cut holes.

- Cut, drill, or punch holes perpendicular to steel surfaces. [Do not thermally cut bolt holes or enlarge holes by burning.]

- Baseplate Holes: Cut, drill, mechanically thermal cut, or punch holes perpendicular to steel surfaces.

- Weld threaded nuts to framing and other specialty items indicated to receive other work.

- shop connections

************************************************************************************************************

Good design practice ensures connections and members have proper drainage. If water ponding cannot be avoided, specify a waterproofing material to suit the specific needs of the project.  This also applies to subsequent “Field-Connections” Article.    ************************************************************************************************************

  - High-Strength Bolts: Shop install high-strength bolts according to RCSC SPEC for type of bolt and type of joint specified.

************************************************************************************************************

JOINT TYPE:  RCSC requires that joint types be specified in the Contract Documents for most loading conditions. The joint types in "Joint Type" Subparagraph below are the three types RCSC recognizes. Insert particular bolt pretensioning method (i.e., Turn-of-Nut; Calibrated Wrench; Twist-Off-Type, Tension-Control Bolt; or Direct-Tension Indicator) for pretensioned or slip-critical joints.

AISC 341 does not allow the use of snug-tightened joints in the SFRS.

PRETENSIONING METHOD:  For pretensioned or slip-critical joints, select one of the four bolt-tightening methods allowed by RCSC SPEC, each of which provides satisfactory results if bolt assemblies are kept free of dirt and rust, if properly lubricated, and if proper installation procedures are followed.

For turn-of-nut pretensioning, LANL requires selection of “with match-marking,” or “without match-marking” for inspection purposes.  Per RCSC SPEC Commentary, “Match-marking…is certainly an aid to inspection…”

These notes are also applicable to subsequent “Field-Connections” Article.

************************************************************************************************************

    - Joint Type: [Snug tightened] [Pretensioned] [Slip critical].

      - The pretensioning method used for the bolts in [pretensioned] [and] [slip-critical] joints shall be [turn-of-nut [with match-marking] [without match-marking]] [calibrated wrench] [twist-off-type, tension-control-bolt] [direct-tension indicator].

************************************************************************************************************

Retain option in subparagraph below if Project includes SFRS and welding therein. ************************************************************************************************************

  - Weld Connections: Comply with AWS D1.1 [and AWS D1.8] for tolerances, appearances, welding procedure specifications, weld quality, and methods used in correcting welding work.

************************************************************************************************************

Retain subparagraph below if built-up sections are required. ************************************************************************************************************

    - Assemble and weld built-up sections by methods that maintain true alignment of axes without exceeding tolerances in AISC 303 for mill material

- Shop Priming

************************************************************************************************************

Retain this Article if shop priming is required.  If it is required, edit first Paragraph as necessary to suit Project.

************************************************************************************************************

- Shop prime steel surfaces except the following:

  - Surfaces embedded in concrete or mortar. Extend priming of partially embedded members to a depth of 2 inches.

  - Surfaces to be field welded.

  - Surfaces of high-strength bolted, slip-critical and/ or SFRS connections.

  - Surfaces to receive sprayed fire-resistive materials (applied fireproofing).

  - Galvanized surfaces.

  - Surfaces enclosed in interior construction.

- Surface Preparation: Clean surfaces to be painted. Remove loose rust and mill scale and spatter, slag, or flux deposits. Prepare surfaces according to the following specifications and standards.

Retain surface-preparation standards in nine subparagraphs below or revise to suit Project. Subparagraphs are listed from least to most comprehensive surface preparation and from lowest to highest cost. Coordinate minimum surface-preparation requirements with selection of primers, paint, and coating systems. See EvaluationsRetain surface-preparation standards in nine subparagraphs below or revise to suit Project. Subparagraphs are listed from least to most comprehensive surface preparation and from lowest to highest cost. Coordinate minimum surface-preparation requirements with selection of primers, paint, and coating systems. See Evaluations.

************************************************************************************************************

Retain surface-preparation standards in six subparagraphs below or revise to suit Project. Subparagraphs are listed from least to most comprehensive surface preparation and from lowest to highest cost. Coordinate minimum surface-preparation requirements with selection of primers, paint, and coating systems.

For assistance with proper specification of the following content, refer to AISC Manual, Part 2, Table 2-8; and AIA MasterSpec – Evaluations, Structural Steel Framing, 051200, pp. E8 – E11.

Surface-prep standards that exceed the highest one herein -- SSPC SP 6/ NACE No. 3 -- exist.  If such higher standard(s) is required, and the Project can afford the associated cost, then edit the standard(s) into subparagraphs below.

Cleaning in first and second subparagraphs below removes loose rust, mill scale, and paint. Cleaning in first subparagraph is minimum surface preparation accepted by AISC for painted steel. ************************************************************************************************************

  - SSPC-SP 2.

  - SSPC-SP 3.

************************************************************************************************************

Cleaning in subparagraph below permits tight residues of rust, mill scale, and coatings to remain. ************************************************************************************************************

  - SSPC-SP 7/NACE No. 4.

************************************************************************************************************

Cleaning in subparagraph below requires complete removal of rust, mill scale, and paint by power tools. SSPC-SP 11 uses nonabrasive methods and bridges the gap between the marginal cleaning required in SSPC-SP 2, SSPC-SP 3, and SSPC-SP 7/NACE No. 4 and the more thorough cleaning required in SSPC-SP 6/NACE No. 3, SSPC-SP 10/NACE No. 2, and SSPC-SP 5/NACE No. 1. ************************************************************************************************************

  - SSPC-SP 11.

************************************************************************************************************

Cleaning in subparagraph below exceeds SSPC-SP 7/NACE No. 4 but is less than cleaning specified in SSPC-SP 6/NACE No. 3. ************************************************************************************************************

  - SSPC-SP 14/NACE No. 8.

************************************************************************************************************

Cleaning in subparagraph below requires that 2/3 of surface area be free of visible residue. ************************************************************************************************************

  - SSPC-SP 6/NACE No. 3.

- Priming: Immediately after surface preparation, apply primer according to manufacturer's written instructions and at rate recommended by SSPC to provide a minimum dry film thickness of 1.5 mils.  Use priming methods that result in full coverage of joints, corners, edges, and exposed surfaces.

************************************************************************************************************

Retain first subparagraph below if "Priming" Paragraph above does not suffice. Stripe painting adds cost but helps ensure that hard-to-reach areas, such as crevices, inside corners, and welds, are thoroughly coated and that sharp edges receive adequate coverage. ************************************************************************************************************

  - Stripe paint corners, crevices, bolts, welds, and sharp edges.

  - Apply two coats of shop paint to surfaces that are inaccessible after assembly or erection. Change color of second coat to distinguish it from first.

************************************************************************************************************

Delete "Surface Preparation" and "Priming" paragraphs above if retaining "Painting" Paragraph below. SSPC-PS Guide 7.00 includes either SSPC-SP 2 or SSPC-SP 3 surface preparation plus a limited choice of nonlead primers. SSPC sets a minimum dry film thickness of 1.5 mils. These one-coat shop-painting systems are not expected to protect weather-exposed steel beyond a few months.  Revise below to AISC 303 default thickness of 1 mil if permitted. ************************************************************************************************************

- Painting: Prepare steel and apply a one-coat, nonasphaltic primer complying with SSPC-PS GUIDE 7.00 to provide a dry film thickness of not less than 1.5 mils.

- GALVANIZING

************************************************************************************************************

Most structural steel is painted. If galvanized items are required, they must be indicated or specified (i.e., retain this Article).  Once painting and/or galvanizing is finalized in this Section, ensure there are no coordination issues with other Sections (e.g., Sect. 05 5000, etc.).

The galvanizing specified is by the hot-dip process, which requires large amounts of energy and unevenly heats steel sections that can be large and/or thick, occasionally warping the steel sections.

Using zinc coating by thermal spraying (metallizing) as an alternative to hot-dip galvanizing should be considered for certain steel sections. The following American Welding Society (AWS) publications should be consulted for further information:

TS-85 - Thermal Spraying - Practice, Theories, and Application

C2.2-67 - Recommended Practices for Metallizing with Aluminum and Zinc for Protection of Iron and Steel.

************************************************************************************************************

- Hot-Dip Galvanized Finish: Apply zinc coating by the hot-dip process to structural steel according to ASTM A 123.

  - Fill vent and drain holes that are exposed in the finished Work unless they function as weep holes, by plugging with zinc solder and filing off smooth.

************************************************************************************************************

Revise locations below where galvanizing is required to suit Project. Subparagraph is an example only; delete and indicate items to be galvanized on Drawings if preferred. ************************************************************************************************************

  - Galvanize [lintels] [shelf angles] [and] [welded door frames] attached to structural-steel frame and located in exterior walls.

- SOURCE/ FABRICATOR QUALITY CONTROL

- Fabricator’s QCI: Perform the monitoring, and shop tests and inspections required by the fabricator’s quality control procedures.

  - Provide QCI with access to places where structural-steel work is being fabricated or produced to perform tests and inspections.

- The QCI shall monitor material identification procedures in order to ensure compliance with AISC 303 Section 6.1.

- The QCI shall inspect the following as a minimum, as applicable:

  - Shop welding, high-strength bolting, and details in accordance with AISC 360 Section N5, except paragraph N5.5.

  - Shop cut and finished surfaces in accordance with AISC 360 Section M2.

  - Shop heating for straightening, cambering and curving in accordance with AISC 360 Section M2.1.

  - Tolerances for shop fabrication in accordance with AISC 303 Section 6.

************************************************************************************************************

Retain Article below if Project includes a SFRS and involves shop fabrication of it/ some of it.
************************************************************************************************************

2.10    SFRS SOURCE/ FABRICATOR QC

- Inspection tasks and documentation for QC for the SFRS shall be as provided in

the tables in AISC 341 Sections J6 – J9.  The nondestructive testing (NDT) of

welded joints (paragraph J6.2) is excluded.

PART 3  EXECUTION

- examination

- Verify, with steel erector present, elevations of concrete- and masonry-bearing surfaces and locations of anchor rods, bearing plates, and other embedments for compliance with requirements.

  - Prepare a certified survey of existing conditions. Include bearing surfaces, anchor rods, bearing plates, and other embedments showing dimensions, locations, angles, and elevations.

- Proceed with installation only after unsatisfactory conditions have been corrected.

- preparaTION

- Provide temporary shores, guys, braces, and other supports during erection to keep structural steel secure, plumb, and in alignment against temporary construction loads and loads equal in intensity to design loads. Remove temporary supports when permanent structural steel, connections, and bracing are in place unless otherwise indicated.

************************************************************************************************************

Retain subparagraph below if design of composite or diaphragm construction is based on shoring. Revise to suit Project. ************************************************************************************************************

  - Do not remove temporary shoring supporting composite deck construction until cast-in-place concrete has attained its design compressive strength.

- ERECTION

************************************************************************************************************

Regarding 1st paragraph below, there are several OSHA provisions that pertain to/ affect the EOR (ref. OSHA 29 CFR Part 1926, Subpart R-Steel Erection); however, only the most-commonly-encountered one (at LANL) is included herein: Design of column base plates and their foundations must accommodate the use of a minimum of four (4) anchor rods.  All of the OSHA provisions should be reviewed for applicability to the Project, and the paragraph edited as necessary.

************************************************************************************************************

- Erect structural steel per OSHA 29 CFR Part 1926, Subpart R-Steel Erection.

  - Regardless of what is indicated on the Project drawings, no column shall be erected with fewer than four anchor rods.  In the event that fewer than four rods are indicated on the drawings, and the column base plate and/ or the plate bearing surface will not accommodate the installation of four rods, stop work and notify LANL and the Engineer of Record (EOR).

- Set structural steel accurately and to elevations indicated and according to AISC 360 and AISC 303.

- Unless otherwise indicated, nuts on cast-in-place anchor rods shall be snug-tightened without using an impact wrench.  In addition, the nuts shall have full thread engagement.

- Baseplates [Bearing plates] [and] [Leveling Plates]:

************************************************************************************************************

Revise requirements in subparagraphs below, which are primary intended for baseplates,  to suit Project.  For example, if bearing plates with integral anchorages are required for Steel Joist Framing, then welding of plate washers is not applicable, etc.

************************************************************************************************************

      - Clean bottom surface of plates of all dirt, oil, grease, and other foreign material that would hinder bond between metal and concrete or grout.

      - The bearing surfaces of concrete and masonry shall be cleaned of bond-reducing materials, and roughened prior to setting plates.

      - Align, level and maintain final positioning of components to be grouted or embedded.

        - Set plates for structural members and equipment supports on wedges, shims, or leveling nuts as required.

        - Weld plate washers to top of baseplate.

        - Snug-tighten anchor rods after supported members have been positioned and plumbed.  Do not remove wedges or shims but, if they protrude, cut off flush with edge of plate before packing with grout.

      - Where perimeter skirts are used, provide [1/4 to ½ in] vent holes in corners of base plates in order to facilitate venting of entrapped air.  If the base plate design contains two or more compartment areas, venting holes must be provided in the corners of each compartment.

      - In a swift manner, pack grout solidly between plate and bearing surface to the extent that all air pockets are removed.

      - Neatly finish exposed surfaces, protect grout and allow to cure.

      - Comply with the more stringent of either the grout manufacturer’s installation instructions, or the following:

        - Moist cure grout.

        - Remove forms after grout is set.  Trim grout edges to form smooth surface, splayed 45 degrees.

        - Tighten anchor rods after grout has cured for a minimum of 3 days.

- Baseplates for Post-Installed Anchors:

  - Non-grouted baseplates installed with anchors may have a maximum 1/8 inch gap as evidenced under exterior edges around the plate provided that (1) the plate exhibits bearing contact within its interior against the  concrete surface, and (2) the uneven bearing does not prevent application of the prescribed torque.

  - If an unacceptable bearing contact condition exists, follow one of these two procedures:

    - Rework the concrete surface to obtain a proper fit.

    - For gaps of up to 1 inch, the baseplate may be grouted instead using the following technique:

HOLD POINT:  EOR must be notified before proceeding so that post-installed anchor design can be checked, and if necessary, modified.

    - Insert anchors and set the baseplate.

    - Install nuts to finger tight condition.

    - Install shims positioned < ½ inch away from the anchors to reduce gaps between baseplates and shims to < 1/8 inch at anchor locations.

    - Apply tightening torque. The bolt tightening shall not be performed when interior shims under the baseplates have been placed away from anchors, so that downward bending of the baseplate would result upon tightening. Shims shall be moved as close as possible to the anchors before applying the installation torque.

    - Fill the gap with non-shrink grout leaving the shims in place. For baseplates on walls, where grouting is not feasible, the gap may be filled with shim plates. The shims may be stacked, but no more than four shims shall be stacked.

- Maintain erection tolerances of structural steel within AISC 303.

- Align and adjust various members that form part of complete frame or structure before permanently fastening. Before assembly, clean bearing surfaces and other surfaces that are in permanent contact with members. Perform necessary adjustments to compensate for discrepancies in elevations and alignment.

  - Level and plumb individual members of structure.

************************************************************************************************************

Review subparagraph below and revise to suit Project.  Retain temperature allowances if required.

************************************************************************************************************

  - Make allowances for difference between temperature at time of erection and mean temperature when structure is completed and in service.

- Splice members only where indicated.

************************************************************************************************************

Retain option in first paragraph below if thermal cutting is permitted.

************************************************************************************************************

- Do not use thermal cutting during erection [unless approved by EOR. Finish thermally cut sections within smoothness limits in AWS D1.1].

- Do not enlarge unfair holes in members by burning or using drift pins. Ream holes that must be enlarged to admit bolts.

- Shear Connectors: Prepare steel surfaces as recommended by manufacturer of shear connectors. Use automatic end welding of headed-stud shear connectors according to AWS D1.1 and manufacturer's written instructions.

- FIELD CONNECTIONS

************************************************************************************************************

Several author notes in Part 2 are applicable to field connections too.  Before editing this (Field Connections) Article, see author notes associated with the Bolted-Joints paragraph in the Fabrication Article, and with the Shop Connections Article.

************************************************************************************************************

  - High-Strength Bolts: Install high-strength bolts according to RCSC SPEC for type of bolt and type of joint specified.

- Joint Type: [Snug tightened] [Pretensioned] [Slip critical].

  - The pretensioning method used for the bolts in [pretensioned] [and] [slip-critical] joints shall be [turn-of-nut [with match-marking] [without match-marking]] [calibrated wrench] [twist-off-type, tension-control-bolt] [direct-tension indicator].

************************************************************************************************************

Retain option in "Weld Connections" Paragraph below for Projects involving AISC 341.

************************************************************************************************************

  - Weld Connections: Comply with AWS D1.1 [and AWS D1.8] for tolerances, appearances, welding procedure specifications, weld quality, and methods used in correcting welding work.

- Comply with AISC 303 and AISC 360 for bearing, alignment, adequacy of temporary connections, and removal of paint on surfaces adjacent to field welds.

************************************************************************************************************

Retain first subparagraph below if required.  Indicate locations if limited to certain areas. AISC 303 permits backing bars and runoff tabs to remain in place.

For Projects with a SFRS, AISC 341 para. A4.2 has requirements pertaining to indication of weld backing removal, weld backing not removed, and weld tab removal.   Edit 1st subpara. below &/ or drawings, as necessary, in accordance with these requirements.
************************************************************************************************************

- Remove backing bars or runoff tabs [where indicated], back gouge, and grind steel smooth.

- Assemble and weld built-up sections by methods that maintain true alignment of axes without exceeding tolerances in AISC 303 for mill material.

- FIELD/ ERECTOR QUALITY CONTROL

  - Erector’s QCI: Perform the field tests and inspections required by the erector’s quality control procedures.

      - Provide QCI with access to places where structural-steel work is being erected to perform tests and inspections.

- The QCI shall inspect the following as a minimum, as applicable:

  - Field welding, high-strength bolting, and details in accordance with AISC 360 Section N5, except paragraph N5.5.

  - Steel deck and headed steel stud anchor placement and attachment in accordance with AISC 360 Section N6.

  - Field cut surfaces in accordance with AISC 360 Section M2.2.

  - Field heating for straightening in accordance with AISC 360 Section M2.1.

  - Tolerances for field erection in accordance with AISC 303 paragraph 7.13.

************************************************************************************************************

Retain Article below if Project includes a SFRS and involves field erection of it/ some of it.
************************************************************************************************************

- SFRS FIELD/ ERECTOR QC

- Inspection tasks and documentation for QC for the SFRS shall be as provided in the tables in AISC 341 Sections J6 – J9.  NDT of welded joints (paragraph J6.2) is excluded.

- REPAIRS AND PROTECTION

    - Galvanized Surfaces: Clean areas where galvanizing is damaged or missing and repair galvanizing to comply with ASTM A 780.

******************************************************************************************************

Retain first "Touchup Painting" Paragraph below if on-site paint repair is included in this Section. Touchup painting may be unnecessary if building is immediately enclosed and in-service conditions require no permanent paint protection.

******************************************************************************************************

    - Touchup Painting: Immediately after erection, clean exposed areas where primer is damaged or missing and paint with the same material as used for shop painting to comply with SSPC-PA 1 for touching up shop-painted surfaces.

      - Clean and prepare surfaces by SSPC-SP 2 or SSPC-SP 3.

**********************************************************************************************************

Retain "Touchup Painting" Paragraph below if touchup painting is required for Project but is not part of the Work of this Section.

************************************************************************************************************

    - Touchup Painting: Cleaning and touchup painting are specified in Section 09 9000 Painting.

END OF SECTION

*******************************************************************************************************

Do not delete the following reference information:

*******************************************************************************************************

THE FOLLOWING REFERENCE IS FOR LANL USE ONLY

This project specification section is based on LANL Master Specification Section 05 1000 Rev. 9, dated September 29, 2015.