SECTION 05 3000

METAL DECKING

*************************************************************************************************************

Edit this template for each Project. In doing so, Specifier must add job-specific requirements.  Brackets are used in the text to indicate where text must be supplied by the Specifier. Once the choice is made or text supplied, remove the brackets. The specifications must also be edited to delete specification requirements for materials, systems, processes, items, or designs that are not included in the Project-- and Specifier's notes such as these.  Additional tailoring requirements are contained in ESM Chapter 1 Section Z10 Att. F, Specifications.

To seek a variance from requirements in the specifications that are applicable, contact the Engineering Standards Manual Structural Specs POC. Please contact POC with suggestions for improvement as well.

When assembling a specification package, include applicable specifications from all Divisions, especially Division 1, General requirements.
This specification section covers the requirements for metal floor and roof* decks, including accessories.

*    If this section is used for roof deck then coordination between structural and architectural EORs is required to ensure that their respective design intent for the roof is adequately conveyed to Construction Subcontractor, to include de-conflicting this section and any architectural roof covering/deck section used (e.g., this section and 07 4113, Metal Roof Panels, can be used for architectural and structural.). The diaphragm-related note at bottom of this page will likely be of assistance in this coordination.

This specification section is for use with LANL ESM Chapter 5, Section II; therefore, it is applicable to ML-4 Projects. For ML-1, 2, and 3 applications, additional requirements and independent reviews should be added if increased confidence in procurement or execution is desired; see ESM Chapter 1 Section Z10 Specifications and Quality sections.

ESM Chapter 5, Sect. II, para. 7.0, references the International Building Code (IBC), Chapter 22, Steel, for guidance on design requirements for steel building structures, and components therein, most of which are contained in this and other METALS sections of the specifications. 
*************************************************************************************************************

*************************************************************************************************************

NOTE: All decks that are expected to function as diaphragms (in the structure’s lateral-force-resisting system), as well as all composite decks and connections*, must be designed by the structural EOR in accordance with the IBC.  All connections must be shown.  Drawings must show wind uplift loads for roof joist design in addition to the items listed below.

For non-diaphragm acting, non-composite decks, the Construction Subcontractor may provide the deck design and connections.  In this case, in addition to the items listed below, the drawings must show roof live loads, including snow loads, and wind loads, including internal and external pressures and high intensity zones. Consider showing a roof uplift and snow load plan on the drawings.

*   Composite decks are not to be confused with composite beams:  The former are included herein, regulated by SDI, and their behavior is achieved via ‘features’ on/of the metal deck; while the latter are not included, are regulated by AISC, and their behavior is achieved via shear connectors welded to steel beams either with or without the presence of metal deck.

As applicable, and as a minimum, show/ indicate the following items on the Project drawings:

- Deck and Deck Attachment

  - Depth, type (profile), and dimensional design (vs. gage) thickness.

  - Deck material (including yield strength) and deck finish.

  - Deck attachment type, spacing, and details.

2. 	Framing plan(s) showing the size, location, and type of all deck supports.

3.	For composite floor deck, the information on Loads and Concrete and Reinforcing required by SDI C, Section 1.3.

- Design deck to carry the concrete and deck dead loads, and the live loads during construction before the concrete sets. Additional concrete dead load due to deflection of the deck shall be considered when necessary to prevent excessive stresses or deflections in the deck.

4.	Locations of roof expansion joints, roof sumps and drains, HVAC openings, and other deck openings.

5.	Locations of floor expansion joints, floor drains, HVAC openings, and other deck openings.

6.	Details and fastening requirements of supplemental steel framing at openings; typically of openings exceeding 12 inches.

7. 	Locations and details of flexible closure strips between tops of partitions and walls and underside of steel deck.

8. 	Layout and extent of cellular floor-deck systems for use as raceways. Coordinate with electrical Drawings for locations and layouts of preset inserts, activation kits, afterset inserts, service fittings, header ducts, trench header ducts, and riser locations.

- 	Note that both cellular decking to be used as electrical raceway and Electrified Cellular Floor Decking, if required by Project, will have to be edited in to this Section (i.e., neither of these are included herein).

9. 	Locations of fire-resistance-rated construction and details of assembly required. Include details of fire-resistive closures between the top of partitions and the fluted profile of the underside of steel deck.

Finally, structural steel design must be such that the requirements of OSHA Steel Erection Standard, 29 CFR Part 1926, Subpart R-Steel Erection, can be met.

*************************************************************************************************************

PART 1 GENERAL

  - RELATED SECTIONS

- Division 1 Specification Sections apply to this Section.

  - SUMMARY

- Section Includes:

  - Roof deck.

  - Acoustical roof deck.

  - Cellular roof deck.

  - Acoustical cellular roof deck.

  - Composite floor deck.

  - Noncomposite form deck.

- Related Requirements

************************************************************************************************************

Retain subparagraphs below to cross-reference requirements Construction Subcontractor/ Installer might expect to find in this Section but are specified in other Sections.

NOTES:  03 3001 template will require editing if it is used by Project for lightweight concrete.

Finally, Articles 2.6 & 3.2 of 05 5000 will require editing if that Section is used by Project for framed deck openings with miscellaneous steel shapes.

*************************************************************************************************************

- Section 03 3001 Reinforced Concrete for normal-weight [and lightweight] structural concrete fill over metal deck.

- Section 05 1000 Structural Metal Framing for shop- and field-welded shear connectors.

- [Section 05 5000 Metal Fabrications for framing deck openings with miscellaneous steel shapes.]

- Section 09 9100 Painting for repair painting of primed deck and finish painting of deck.

  - REFERENCES

The publications listed below form a part of this specification to the extent referenced. The publications are referred to in the text by the basic designation only.

- ASTM INTERNATIONAL (ASTM)

- ASTM A 653 	Steel Sheet, Zinc-Coated (Galvanized) or Zinc-Iron Alloy-Coated (Galvannealed) by the Hot-Dip Process

- ASTM A 780 	Repair of Damaged and Uncoated Areas of Hot-Dipped Galvanized Coatings

- ASTM A 1008 	Steel Sheet, Cold-Rolled, Carbon, Structural, High-Strength Low-Alloy and High-Strength Low-Alloy with Improved Formability

- ASTM C 423 	Sound Absorption and Sound Absorption Coefficients by the Reverberation Room Method

- ASTM E 108	Test Methods for Fire Tests of Roof Coverings

- ASTM E 119	Test Methods for Fire Tests of Building Construction and Materials

- AMERICAN WELDING SOCIETY (AWS)

- AWS D1.3 		Structural Welding Code – Sheet Steel

- STEEL DECK INSTITUTE (SDI)

- SDI-NC1.0 		Standard for Noncomposite Steel Floor Deck

- SDI-RD1.0		Standard for Steel Roof Deck

- SDI-C			Standard for Composite Steel Floor Deck Slabs

- SDI-QA/QC		Quality Control and Quality Assurance for

Installation of Steel Deck

- THE SOCIETY FOR PROTECTIVE COATINGS (SSPC)

- SSPC Paint 20 	Zinc-Rich Coating (Type I - "Inorganic" and Type II- "Organic")

- UNDERWRITERS LABORATORIES (UL)

- UL 790  		Test Methods for Fire Tests of Roof Coverings

  - ACTION SUBMITTALS

- Product Data:  For each type of deck, accessory, and product indicated.

- Installation Drawings:

        - "Laboratory Test Reports for Credit EQ 4" Subparagraph below applies to LEED for Schools.

- Show deck layout and all accessories, including installation details.

- Per the requirements of 01 4444 Offsite Welding and Joining Requirements and/or 01 4455 Onsite Welding and Joining Requirements, submit

****************************************************************************************************

When offsite only, delete submittals below regarding onsite welding. For high risk applications such as ML-1 or ML-2, add submittals for “Weld Filler Material Control Procedures” and “Filler Material Certified Material Test Reports (CMTRs)” when required.  Add “Post-Weld Heat Treatment Procedures” when required.

****************************************************************************************************

  - Welding Procedure Specification (WPS) and supporting Procedure Qualification Record (PQR).  [Note:  For Onsite welding use of LANL WPS/PQR is the default; coordinate usage with the LANL CWI; no submittal required]

  - Welder Performance Qualification Records (WPQR) including continuity [Note: For Onsite, welders are tested by LANL who will produce WPQR and track continuity; this includes brazing, bonding and fusing; no submittal required]

  - Inspector qualification records

  - Inspection procedures

  - Shop drawings with weld details/symbols

  - INFORMATIONAL SUBMITTALS

*************************************************************************************************************

Informational submittals must be limited to those necessary for adequate quality control. The importance of an item, or complexity, in the context of the Project should determine whether or not a submittal for it is required.

Retain "Qualification Data" Paragraph below with qualification requirements in Section 01 4000 Quality Requirements and as may be supplemented in "Quality Control" Article.

*************************************************************************************************************

- Qualification Data: For [Installer] [Quality Control Inspector].

************************************************************************************************************

Coordinate first paragraph below with qualification requirements in Section 01 4000 Quality Requirements.

************************************************************************************************************

- Certified material test reports for each type of metal deck, mechanical fastener, and including chemical and physical properties.

- Product Test Reports: Based on evaluation of comprehensive tests performed by a qualified testing agency, indicating that each of the following complies with requirements.

#### Power-actuated mechanical fasteners.

#### Acoustical roof deck.

- Independent Evaluation Reports (e.g., ICC-ES ESR, etc.) on deck(s), including profile, thickness, physical properties and finish.

**********************************************************************************************************

Retain paragraph below if Subcontractor is responsible for field quality-control testing and inspecting.  Retain paragraph below if Subcontractor is responsible for field quality-control testing and inspecting.Retain paragraph below if Construction Subcontractor is responsible for field quality-control testing and inspecting.

***************************************************************************************************************************************************************************************************************

- Field quality-control reports.

  - SUSTAINABLE DESIGN SUBMITTALS

    - Product Data: For products having recycled content, documentation indicating percentages by weight of postconsumer and pre-consumer recycled content. Include statement indicating cost for each product having recycled content.

    - Laboratory Test Reports for Credit IEQ 4.2:  For primers, documentation indicating that products comply with the testing and product requirements of the California Department of Public Health's (formerly, the California Department of Health Services) “Standard Method for the Testing and Evaluation of Volatile Organic Emissions from Indoor Sources Using Environmental Chambers.”

  - QUALITY CONTROL

*************************************************************************************************************

SDI-QA/QC, which is referenced by IBC, distinguishes between quality control (QC) and quality assurance (QA):

- QC is what is contained herein, & is the responsibility of the Construction Subcontractor (i.e., installer).

- QA (which is also required by IBC Ch, 17) is contained in the EOR’s Statement of Special Inspections (SSI), & is the responsibility of LANL (i.e., execution of the SSI).  The SSI template is found in ESM Ch. 16, Sect. IBC-IP, Attach. B.

Testing agency is normally engaged by LANL.

### *************************************************************************************************************

- The installer shall produce and maintain quality control procedures and perform inspection to confirm that their work is performed in accordance with SDI-QA/QC, construction documents, installation drawings, shop drawings, design documents and applicable referenced standards.  All material control and installation procedures shall be monitored by the installer’s Quality Control Inspector (QCI).

- QCI Qualifications:  The qualifications of the QCI(s) engaged by the installer shall comply with the applicable provisions in Section 01 4000, Quality Requirements, and SDI-QA/QC Paragraph 3.1.

*************************************************************************************************************

### Retain appropriate subpara(s) under paragraph below if shop and/or field welding is required.  If retaining, also retain ”WPQR” paragraph in "Action Submittals" Article.

### *************************************************************************************************************

- Welding Qualifications:

- Refer to 01 4444 Offsite Welding and Joining Requirements and/or Section 01 4455 Onsite Welding and Joining Requirements.

************************************************************************************************************

A metal roof deck can serve as both a roof covering and a roof deck, or just the latter.  In either case, it is part of the IBC definition of “Roof Assembly;” therefore, compliance with IBC Section 1505, Fire Classification is required.  Retain and edit paragraph below if Project includes a metal roof deck.

************************************************************************************************************

- Fire-Resistance Listing and Identification: Provide metal roof deck tested, listed and identified as follows.

  - Identification: Class [A] [B] [C].

  - List published by [    ].

  - Testing shall be in accordance with [ASTM E 108] [UL 790].

  - DELIVERY, STORAGE, AND HANDLING

    - Protect steel deck from corrosion, deformation, and other damage during delivery, storage, and handling.

    - Stack steel deck on platforms or pallets and slope to provide drainage. Protect with a waterproof covering and ventilate to avoid condensation.

*****************************************************************************************************

Retain paragraph below if Subcontractor is responsible for field quality-control testing and inspecting.  Retain paragraph below if Subcontractor is responsible for field quality-control testing and inspecting.Retain subparagraph below if acoustical cellular roof deck with insulation is required.

*********************************************************************************************************************************************************************************************************

      - Protect and ventilate acoustical cellular roof deck with factory-installed insulation to maintain insulation free of moisture.

PART 2 PRODUCTS

*************************************************************************************************************

For Projects involving work on existing buildings, include, or refer to, Section 01 6000, Product Requirements, paragraph 1.2.Bif applicable.

*************************************************************************************************************

  - PERFORMANCE REQUIREMENTS

- SDI Standards: Comply with calculated structural characteristics of steel deck according to [SDI-NC1.0] [,] [and] [SDI-C] [,] [and] [SDI-RD1.0] [as applicable].

*************************************************************************************************************

Retain paragraph below only if products specified are part of a fire-resistance-rated assembly. Indicate rating, testing agency, and testing agency's design designation on Drawings.

On a related note, all of the deck types herein used in/ for roofs and/ or floors can be part of a fire-resistance-rated assembly.  If such applies to Project then selection of the finish of the deck(s) on a given Project (in Articles 2.2 – 2.5 herein) warrants special/ extra consideration.

Per SDI-RD1.0, and –NC1.0 (and SDI-C says similar), “…Specification of painted deck in areas that require spray-on fire proofing should be avoided unless specifically permitted by the applicable fire rated assembly. This must be clearly called out in the contract documents. In general, there are three types of fire resistive assemblies; those achieving the fire resistance by membrane protection, direct applied protection, or with an unprotected assembly. Of these three, only the systems that utilize direct applied protection are concerned with the finish of the steel deck. In these systems, the finish of the steel deck can be the factor that governs the fire resistance rating that is achieved. In assemblies with direct applied fire protection the finish (paint) is critical…”

*************************************************************************************************************

- Fire-Resistance Ratings: Comply with ASTM E 119; testing by a qualified testing agency. Identify products with appropriate markings of applicable testing agency.

- Indicate design designations from UL's "Fire Resistance Directory" or from the listings of another qualified testing agency.

*************************************************************************************************************

EPA-CPG requires ‘recycled content’ regardless of whether or not LEED credit is being pursued.

*************************************************************************************************************

- Recycled Content of Steel Products:

- Postconsumer recycled content:

- Basic Oxygen Furnace:  16%

- Electric Arc Furnace:  67%

- Recovered Materials

- Basic Oxygen Furnace:  25-30%

- Electric Arc Furnace:  100%

  - ROOF DECK

*********************************************************************************************************

Retain this Article if roof deck is required.

Retain "Manufacturers" paragraph and list of manufacturers below to require products from manufacturers listed or a comparable product from other manufacturers.

*********************************************************************************************************

- Manufacturers: Subject to compliance with requirements, [provide products by the following] [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

- ASC Profiles, Inc.

- Canam Steel Corporation; Canam Group Inc.

- CMC Joist & Deck.

- Consolidated Systems, Inc.

- Cordeck.

- DACS, Inc.

- Epic Metals Corporation.

- Marlyn Steel Decks, Inc.

- New Millennium Building Systems, LLC.

- Nucor Corporation.

- Roof Deck, Inc.

- Valley Joist.

- Verco Decking, Inc., a Nucor Company.

- [Insert manufacturer's name].

*************************************************************************************************************

In the “Roof Deck” Para. below, the reason for prohibiting top-flange stiffening grooves is to ensure roof insulation is secured as well as possible.  If non-flat top-flange surfaces won’t adversely affect Project (e.g., roof deck not insulated, insulation will be adequately secured to deck despite its stiffening grooves, etc.).

Same goes for Acoustical Roof Deck in subsequent Article.

*************************************************************************************************************

- Roof Deck:  Fabricate panels, without top-flange stiffening grooves, to comply with SDI-RD, and with the following:

*************************************************************************************************************

Retain one or more of the steel-sheet Subparagraphs below to suit Project.

Retain steel grade from options in "Prime-Painted Steel Sheet" subparagraph below.  When making this selection, due consideration shall be given to the finish on the deck.

Per SDI-RD, “The finish on the steel deck shall be compatible for the environment to which the deck is exposed within the finished structure, and shall be specified by the [EOR].  A primer coat of paint is intended to protect the steel for only a short period of exposure in ordinary atmospheric conditions and should be considered an impermanent and provisional coating. Field painting of prime painted deck is recommended especially where the deck is exposed.  In corrosive or high moisture atmospheres, a galvanized finish is desirable…”

*************************************************************************************************************

- Prime-Painted Steel Sheet: ASTM A 1008, Structural Steel (SS), [Grade 33] [Grade 40] [Grade 80] minimum, shop primed with manufacturer's standard baked-on, rust-inhibitive primer.

- Color: [Manufacturer's standard] [Gray] [White] [Gray top surface with white underside].

*************************************************************************************************************

Retain steel grade and zinc-coating weight from options in subparagraph below.

*************************************************************************************************************

- Retain steel grade and zinc-coating weight from options in "Galvanized-Steel Sheet" Subparagraph below.

- Galvanized-Steel Sheet: ASTM A 653, Structural Steel (SS), [Grade 33] [Grade 40] [Grade 80], [G60] [G90] zinc coating.

*************************************************************************************************************

Retain steel grade from options in subparagraph below.

*************************************************************************************************************

#### Retain steel grade from options in "Galvanized and Shop-Primed Steel Sheet" Subparagraph below.

- Galvanized and Shop-Primed Steel Sheet: ASTM A 653, Structural Steel (SS), [Grade 33] [Grade 40] [Grade 80], G60 zinc coating; cleaned, pretreated, and primed with manufacturer's standard baked-on, rust-inhibitive primer.

            - Color: [Manufacturer's standard] [Gray] [White] [Gray top surface with white underside].

*************************************************************************************************************
Retain roof-deck category and profile type from "Deck Profile" and "Cellular Deck Profile" subparagraphs below. Categories and profiles are based on SDI nomenclature; manufacturers may identify same categories and profiles with other designations. Insert different proprietary profiles, if required, to suit Project.

*************************************************************************************************************

- Retain roof-deck category and profile type from "Deck Profile" and "Cellular Deck Profile" subparagraphs below. Categories and profiles are based on SDI nomenclature; manufacturers may identify same categories and profiles with other designations. Insert different proprietary profiles, if required, to suit Project.

- Deck Profile: [As indicated] [Type NR, narrow rib] [Type IR, intermediate rib] [Type WR, wide rib] [Type 3DR, deep rib] [Long span].

- Cellular Deck Profile: [As indicated] [Type WR, wide rib] [Type 3DR, deep rib] [Long span], with bottom plate.

*************************************************************************************************************
Retain one option in "Profile Depth" subparagraph below or revise to suit Project. Indicate locations on Drawings if various depths are required. 
*************************************************************************************************************

- Retain one profile depth from "Profile Depth" Subparagraph below or revise to suit Project. Indicate locations on Drawings if various depths are required. FM Global approval, if required, is limited to roof deck 1-1/2 inches (38 mm) deep.

- Profile Depth: [As indicated] [1-1/2 inches] [2 inches] [3 inches] [4-1/2 inches] [6 inches] [7-1/2 inches].

************************************************************************************************************Retain one steel thickness from subparagraph below or revise to suit Project

***********************************************************************************************************

- Retain one steel thickness from "Design Uncoated-Steel Thickness" Subparagraph below or revise to suit Project.

- Design Uncoated-Steel Thickness: [As indicated] [0.0295 inch] [0.0358 inch] [0.0474 inch] [0.0598 inch] [0.0747 inch].

************************************************************************************************************Retain one steel thickness from subparagraph below if cellular roof deck, combining a roof-deck profile with a bottom plate, is required. Thickness combinations are based on deck unit (first) and bottom plate (second).
***********************************************************************************************************

- Retain one steel thickness from "Design Uncoated-Steel Thicknesses; Deck Unit/Bottom Plate" Subparagraph below if cellular roof deck, combining a roof-deck profile with a bottom plate, is required. Thickness combinations are based on deck unit (first) and bottom plate (second).

- Design Uncoated-Steel Thicknesses; Deck Unit/Bottom Plate: [As indicated] [0.0358/0.0358 inch] [0.0358/0.0474 inch] [0.0474/0.0474 inch] [0.0474/0.0598 inch] [0.0598/0.0474 inch] [0.0598/0.0598 inch].

*************************************************************************************************************Retain span used in design from subparagraph below.
************************************************************************************************************

- Retain span used in design from "Span Condition" Subparagraph below.

- Span Condition: [As indicated] [Simple span] [Double span] [Triple span or more].

*************************************************************************************************************
Retain side-lap configuration from subparagraph below. Interlocking seams may be fastened by welding or button punching
************************************************************************************************************

- Side Laps: [Overlapped] [Interlocking seam] [Overlapped or interlocking seam at Installer's option].

Retain side-lap configuration from "Side Laps" Subparagraph below. Interlocking seams may be fastened by welding or button punching.

  - ACOUSTICAL ROOF DECK

*************************************************************************************************************
Retain this Article if acoustical roof deck is required.

Retain "Manufacturers" Paragraph and list of manufacturers below to require products from manufacturers listed or a comparable product from other manufacturers.

*************************************************************************************************************

- Manufacturers: Subject to compliance with requirements, [provide products by the following] [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

- ASC Profiles, Inc.

- Canam Steel Corporation; Canam Group Inc.

- CMC Joist & Deck.

- Consolidated Systems, Inc.

- Cordeck.

- CSi Metal Deck Group

- DACS, Inc.

- Epic Metals Corporation.

- Marlyn Steel Decks, Inc.

- New Millennium Building Systems, LLC.

- Nucor Corporation.

- Roof Deck, Inc.

- [Insert manufacturer's name].

- Acoustical Roof Deck: Fabricate panels, without top-flange stiffening grooves, to comply with SDI-RD1.0, and with the following:

*************************************************************************************************************
Prior to selecting one or more of the steel-sheet subparagraphs below, read the author note in the same location of the previous Article (i.e., Roof Deck, Prime-Painted Steel Sheet).

Retain steel grade from options in "Prime-Painted Steel Sheet" subparagraph below,

*************************************************************************************************************

- Prime-Painted Steel Sheet: ASTM A 1008, Structural Steel (SS), [Grade 33] [Grade 40] [Grade 80] minimum, shop primed with manufacturer's standard baked-on, rust-inhibitive primer.

            - Color: [Manufacturer's standard] [Gray] [White] [Gray top surface with white underside].

*************************************************************************************************************
Retain steel grade and zinc-coating weight from options in subparagraph below.

*********************************************************************************************************

- Retain steel grade and zinc-coating weight from options in "Galvanized-Steel Sheet" Subparagraph below.

- Galvanized-Steel Sheet: ASTM A 653, Structural Steel (SS), [Grade 33] [Grade 40] [Grade 80], [G60] [G90] zinc coating.

*************************************************************************************************************
Retain steel grade from options in subparagraph below.

*************************************************************************************************************

#### Retain steel grade from options in "Galvanized and Shop-Primed Steel Sheet" Subparagraph below.

- Galvanized and Shop-Primed Steel Sheet: ASTM A 653, Structural Steel (SS), [Grade 33] [Grade 40] [Grade 80], G60 zinc coating; cleaned, pretreated, and primed with manufacturer's standard baked-on, rust-inhibitive primer.

- Color: [Manufacturer's standard] [Gray] [White] [Gray top surface with white underside].

*************************************************************************************************************
Retain roof-deck category and profile type from "Deck Profile" and "Cellular Deck Profile" subparagraphs below. Categories and profiles are based on SDI nomenclature; manufacturers may identify same categories and profiles with other designations. Insert different proprietary profiles, if required, to suit Project.

*************************************************************************************************************

#### Retain roof-deck category and profile type from "Deck Profile" and "Cellular Deck Profile" subparagraphs below. Categories and profiles are based on SDI nomenclature; manufacturers may identify same categories and profiles with other designations. Insert different proprietary profiles, if required, to suit Project.

- Deck Profile: [As indicated] [Type WR, wide rib] [Type 3DR, deep rib] [Long span].

- Cellular Deck Profile: [As indicated] [Type WR, wide rib] [Type 3DR, deep rib] [Long span], with bottom plate.

*************************************************************************************************************
Retain one option in "Profile Depth" subparagraph below or revise to suit Project. Indicate locations on Drawings if various depths are required. 
*************************************************************************************************************

- Profile Depth: [As indicated] [1-1/2 inches] [2 inches] [3 inches] [4-1/2 inches] [6 inches] [7-1/2 inches].

*************************************************************************************************************
Retain one steel thickness from subparagraph below if noncellular acoustical roof deck is required or revise to suit Project.
*************************************************************************************************************

- Design Uncoated-Steel Thickness: [As indicated] [0.0295 inch] [0.0358 inch] [0.0474 inch] [0.0598 inch].

Retain one steel thickness from "Design Uncoated-Steel Thickness" Subparagraph below or revise to suit Project.

*************************************************************************************************************
Retain one steel thickness from subparagraph below if cellular acoustical roof deck, combining a roof-deck profile with a bottom plate, is required. Thickness combinations are based on deck unit (first) and bottom plate (second).

*************************************************************************************************************

- Design Uncoated-Steel Thicknesses; Deck Unit/Bottom Plate: [As indicated] [0.0358/0.0358 inch] [0.0358/0.0474 inch] [0.0474/0.0358 inch] [0.0474/0.0474 inch] [0.0474/0.0598 inch] [0.0598/0.0474 inch] [0.0598/0.0598 inch].

*************************************************************************************************************
Retain span used in design from subparagraph below.

*************************************************************************************************************

- Retain span used in design from "Span Condition" Subparagraph below.

- Span Condition: [As indicated] [Simple span] [Double span] [Triple span or more].

*************************************************************************************************************
Retain side-lap configuration from subparagraph below. Interlocking seams may be fastened by welding or button punching

************************************************************************************************************

- Side Laps: [Overlapped] [Interlocking seam] [Overlapped or interlocking seam at Construction Subcontractor's option].

- Acoustical Perforations: [Deck units with manufacturer's standard perforated vertical webs] [Cellular deck units with manufacturer's standard perforated flat-bottom plate welded to ribbed deck].

Retain side-lap configuration from "Side Laps" Subparagraph below. Interlocking seams may be fastened by welding or button punching.

*************************************************************************************************************
Retain subparagraph below if sound-absorbing insulation is required *************************************************************************************************************

- Sound-Absorbing Insulation: Manufacturer's standard premolded roll or strip of glass or mineral fiber. [Insert actual physical properties and thicknesses of insulation].

*************************************************************************************************************
Retain first subparagraph below if cellular acoustical roof deck requires factory-installed sound-absorbing insulation 
*************************************************************************************************************

- Factory install sound-absorbing insulation into cells of cellular deck.

*************************************************************************************************************
Retain first subparagraph below if sound-absorbing insulation is to be field installed in topside deck ribs at same time roofing system is installed *************************************************************************************************************

            - Installation of sound-absorbing insulation is specified in Section [Insert Section number] "[Insert title of applicable roofing Section]”.

*************************************************************************************************************
Retain one noise reduction coefficient (NRC) requirement from options in subparagraph below or revise to suit Project. Consult deck manufacturer to verify tested NRC values for proposed roof-deck assembly. Published NRC values usually rely on a specific roof insulation above the deck

*************************************************************************************************************

- Acoustical Performance: NRC [0.65] [0.75] [0.80] [0.85] [0.90], tested according to ASTM C 423

  - COMPOSITE FLOOR DECK

*************************************************************************************************************
Retain this Article if composite floor deck is required.

Retain "Manufacturers" Para. and list of manufacturers below to require products from manufacturers listed or a comparable product from other manufacturers.

*************************************************************************************************************

- Manufacturers: Subject to compliance with requirements, [provide products by the following] [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

- ASC Profiles, Inc.

- Canam Steel Corporation; Canam Group Inc.

- CMC Joist & Deck.

- Consolidated Systems, Inc.

- Cordeck.

- DACS, Inc.

- Epic Metals Corporation.

- Marlyn Steel Decks, Inc.

- New Millennium Building Systems, LLC.

- Nucor Corporation.

- Roof Deck, Inc.

- Verco Decking, Inc., a Nucor Company.

- [Insert manufacturer’s name].

- Composite Floor Deck: Fabricate panels, with integrally embossed or raised pattern ribs and interlocking side laps, to comply with SDI-C, with the minimum section properties indicated, and with the following:

************************************************************************************************************
Retain one or more of the steel-sheet subparagraphs below to suit Project.  When making this selection, due consideration shall be given to the finish on the deck.

Per SDI-C, “The finish on the [deck] must be…suitable for the environment to which the deck is exposed within the finished structure.  Because the [deck] is the positive bending reinforcement for slab, its service life should at least be equal to the design service life of the structure...  When [deck] with an unpainted to and painted bottom is used, the primer coat is intended to protect the steel for only a short period of exposure in ordinary atmospheric conditions and shall be considered an impermanent and provisional coating. In highly corrosive or chemical atmospheres or where reactive materials could be in contact with the steel deck, special care in specifying the finish should be used, which could include specialized coatings or materials…”

Retain steel grade and color, if applicable, from options in "Prime-Painted Steel Sheet" subparagraph below.

SDI-C para. 2.1 limits the design yield stress based on the ductility of the steel.

********************************************************************************************************

- Prime-Painted Steel Sheet: ASTM A 1008, Structural Steel (SS), [Grade 33] [Grade 40] [Grade 80] minimum, with top surface phosphatized and unpainted and underside surface shop primed with manufacturer's standard [gray] [or] [white] baked-on, rust-inhibitive primer.

*************************************************************************************************************
Retain either "Galvanized-Steel Sheet" or "Galvanized and Shop-Primed Steel Sheet" subparagraph below for galvanized-steel sheet.

Retain zinc-coating weight from options in subparagraph below.

*************************************************************************************************************

- Retain steel grade and zinc-coating weight from options in "Galvanized-Steel Sheet" Subparagraph below.

- Galvanized-Steel Sheet: ASTM A 653, Structural Steel (SS), Grade 33, [G30] [G60] [G90] zinc coating.

**********************************************************************************************************
Retain zinc-coating weight and color, if applicable, from options in subparagraph below.

***********************************************************************************************************

- Galvanized and Shop-Primed Steel Sheet: ASTM A 653, Structural Steel (SS), Grade 33, [G30] [G60] zinc coating; with unpainted top surface and cleaned and pretreated bottom surface primed with manufacturer's standard [gray] [white] baked-on, rust-inhibitive primer.

**********************************************************************************************************
Retain one profile depth from "Profile Depth" subparagraph below or revise to suit Project. Indicate locations on Drawings if various depths are required. 
**********************************************************************************************************

- Profile Depth: [1-1/2 inches] [2 inches] [3 inches] [As indicated].

*************************************************************************************************************
Retain one steel thickness from subparagraph below or revise to suit Project

*************************************************************************************************************

- Design Uncoated-Steel Thickness: [0.0295 inch] [0.0358 inch] [0.0474 inch] [0.0598 inch].

*************************************************************************************************************
Retain span used in design from subparagraph below.

*************************************************************************************************************

- Span Condition: [As indicated] [Simple span] [Double span] [Triple span or more].

  - NONCOMPOSITE FORM DECK

************************************************************************************************************
Retain this Article if noncomposite form deck is required. Form deck may be used in roof and floor applications, in which the deck is used as a form for reinforced concrete slabs.. Insert minimum section properties here or indicate on Drawings

Retain "Manufacturers" Para. and list of manufacturers below to require products from manufacturers listed or a comparable product from other manufacturers.

************************************************************************************************************

- Manufacturers: Subject to compliance with requirements, [provide products by the following] [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

- ASC Profiles, Inc.

- Canam Steel Corporation; Canam Group Inc.

- CMC Joist & Deck.

- Cordeck.

- CSi Metal Dek Group.

- DACS, Inc.

- Marlyn Steel Decks, Inc.

- New Millennium Building Systems, LLC.

- Nucor Corporation.

- Roof Deck, Inc.

- Valley Joist .

- Verco Decking, Inc., a Nucor Company.

- [Insert manufacturer's name].

- Noncomposite Form Deck: Fabricate ribbed-steel sheet noncomposite form-deck panels to comply with SDI-NC1.0, with the minimum section properties indicated, and with the following:

************************************************************************************************************
Retain one or more of the steel-sheet subparagraphs below to suit Project.  When making this selection, due consideration shall be given to the finish on the deck.

Per SDI-NC, “The finish on the steel deck shall be compatible for the environment to which the deck is exposed within the finished structure, and shall be specified by the [EOR]… When non-composite deck with a painted bottom is used, the primer coat is intended to protect the steel for only a short period of exposure in ordinary atmospheric conditions and shall be considered an impermanent and provisional coating.  In highly corrosive or chemical atmospheres or where reactive materials could be in contact with the steel deck, special care in specifying the finish should be used, which could include specialized coatings or materials. In highly corrosive environments, consideration should be given to designing the slab to resist all service loads…”

Retain steel grade from options in "Uncoated Steel Sheet" subparagraph below

************************************************************************************************************

- Steel Sheet: ASTM A 1008, Structural Steel (SS), [Grade 33] [Grade 40] [Grade 80] minimum

*************************************************************************************************************
Retain steel grade from options in subparagraph below

*************************************************************************************************************

- Prime-Painted Steel Sheet: ASTM A 1008, Structural Steel (SS), [Grade 33] [Grade 40] [Grade 80] minimum, with [top and] underside surface shop primed with manufacturer's standard baked-on, rust-inhibitive primer.

  - Color: [Manufacturer's standard] [Gray] [White] [Gray top surface with white underside].

*************************************************************************************************************
Retain either "Galvanized-Steel Sheet" or "Galvanized and Shop-Primed Steel Sheet" subparagraph below for galvanized-steel sheet.

Per SDI-NC, “…When galvanized material is used to support a reinforced concrete slab, the slab dead load is considered to be permanently carried by the deck.  For any permanent load carrying function, a minimum galvanized coating conforming to ASTM A924 (which includes, & is referenced by, “A 653”), G30 is recommended….”

Retain steel grade and zinc-coating weight from options in subparagraph below.

*************************************************************************************************************

- Galvanized-Steel Sheet: ASTM A 653, Structural Steel (SS), [Grade 33] [Grade 40] [Grade 80], [G30] [G60] [G90] zinc coating.

************************************************************************************************************
Retain steel grade from options in subparagraph below.

# ************************************************************************************************************

- Galvanized and Shop-Primed Steel Sheet: ASTM A 653, Structural Steel (SS), [Grade 33] [Grade 80], G60 zinc coating; cleaned, pretreated, and primed with manufacturer's standard baked-on, rust-inhibitive primer.

- Retain steel grade and zinc-coating weight from options in "Galvanized-Steel Sheet" Subparagraph below.

Retain steel grade from options in "Galvanized and Shop-Primed Steel Sheet" Subparagraph below.

- Color: [Manufacturer's standard] [Gray] [White] [Gray top surface with white underside].

# *************************************************************************************************************
Retain one profile depth from "Profile Depth" subparagraph below or revise to suit Project. Indicate locations on Drawings if various depths are required. *************************************************************************************************************

- Profile Depth: [9/16 inch] [15/16 inch] [1-5/16 inches] [1-1/2 inches].

*************************************************************************************************************
Retain one steel thickness from subparagraph below or revise to suit Project

************************************************************************************************************

- Design Uncoated-Steel Thickness: [0.0149] [0.0179] [0.0239] [0.0295 inch] [0.0358 inch] [0.0474 inch] [0.0598 inch].

Retain one steel thickness from "Design Uncoated-Steel Thickness" Subparagraph below or revise to suit Project.

*************************************************************************************************************
Retain span used in design from subparagraph below.

*************************************************************************************************************

    - Retain span used in design from "Span Condition" Subparagraph below.

- Span Condition: [As indicated] [Simple span] [Double span] [Triple span or more].

*************************************************************************************************************
Retain side-lap configuration from subparagraph below. Interlocking seams may be fastened by welding or button punching.

*************************************************************************************************************

- Side Laps: [Overlapped] [Interlocking seam] [Overlapped or interlocking seam at Installer's option].

  - ACCESSORIES

- General: Provide manufacturer's standard accessory materials for deck that comply with requirements indicated.

- Mechanical Fasteners: Corrosion-resistant, low-velocity, power-actuated or pneumatically driven carbon-steel fasteners; or self-drilling, self-threading screws.

- Side-Lap Fasteners: Corrosion-resistant, hexagonal washer head; self-drilling, carbon-steel screws, No. 10 minimum diameter.

- Flexible Closure Strips: Vulcanized, closed-cell, synthetic rubber.

- Miscellaneous Sheet Metal Deck Accessories: Steel sheet, minimum yield strength of 33,000 psi, not less than 0.0359-inch design uncoated thickness, of same material and finish as deck; of profile indicated or required for application

********************************************************************************************************
Revise "Pour Stops and Girder Fillers" Para. below to suit Project. Pour-stop thickness and profile guidelines are presented in SDI-C, and -NC.

********************************************************************************************************

- Pour Stops and Girder Fillers: Steel sheet, minimum yield strength of 33,000 psi, of same material and finish as deck, and of thickness and profile [indicated] [recommended by SDI-C and/ or SDI-NC1.0 for overhang and slab depth].

- Column Closures, End Closures, Z-Closures, and Cover Plates: Steel sheet, of same material, finish, and thickness as deck unless otherwise indicated.

************************************************************************************************************
Piercing hanger tabs in Para. below are designed for embedment in concrete slabs; delete if not required. Before retaining this type of tab, verify whether it can support the loads to which it will be subjected without overloading the deck slab or becoming overstressed.

Rolled-in hanger tabs for composite floor deck may be available from some manufacturers, but improper use could result in overstressing the tabs or overloading the composite deck.  Suspended-ceiling failures and excessive deck deflection have been attributed to overloaded tabs. If selected for use, insert rolled-in hanger tabs here; verify load limits, availability, limitations, and recommendations with deck manufacturers

Refer to SDI-C for more information on hangers.

************************************************************************************************************

- Piercing Hanger Tabs: Piercing steel sheet hanger attachment devices for use with floor deck.

************************************************************************************************************
Retain weld washers in Para. below if weld-fastening deck to the supporting structure with arc spot (“puddle”) welds on deck units with an uncoated minimum steel thickness of less than 0.028 inch. Retain weld washer thickness. ************************************************************************************************************

- Weld Washers: Uncoated steel sheet, shaped to fit deck rib, [0.0598 inch] [0.0747 inch] thick, with factory-punched hole of 3/8-inch minimum diameter.

### ************************************************************************************************************
Retain either "Flat Sump Plates" or "Recessed Sump Pans" Para. below if required. Recessed sump pans are seldom used.  Coordinate with choice of roof drain if recessed sump pans are required.

************************************************************************************************************

- Flat Sump Plates: Single-piece steel sheet, 0.0747 inch thick, of same material and finish as deck. For drains, cut holes in the field.

- Recessed Sump Pans: Single-piece steel sheet, 0.0747 inch thick, of same material and finish as deck, with 3-inch-wide flanges and [level] [sloped] recessed pans of 1-1/2-inch minimum depth. For drains, cut holes in the field.

- Galvanizing Repair Paint: [ASTM A 780] [SSPC-Paint 20, with dry film containing a minimum of 94 percent zinc dust by weight].

- Repair Paint: Manufacturer's standard rust-inhibitive primer of same color as primer.

PART 3  EXECUTION

  - EXAMINATION

### Examine supporting frame and field conditions for compliance with requirements for installation tolerances and other conditions affecting performance.

### Proceed with installation only after unsatisfactory conditions have been corrected.

  - INSTALLATION, GENERAL

  - Install deck panels and accessories according to applicable execution/ installation requirements and commentary in [SDI-NC1.0] [,] [and] [SDI-C] [,] [and] [SDI-RD1.0], manufacturer's written instructions, and provisions in this Section.

  - Install temporary shoring before placing deck panels if required to meet deflection limitations.

### Locate deck bundles to prevent overloading of supporting members.

### Place deck panels on supporting frame and adjust to final position with ends accurately aligned and bearing on supporting frame before being permanently fastened. Do not stretch or contract side-lap interlocks.

### *************************************************************************************************************
Retain subparagraph below if long-span cellular roof deck is required.

*************************************************************************************************************

- Align cellular deck panels over full length of cell runs and align cells at ends of abutting panels.

  - Place deck panels flat and square and fasten to supporting frame without warp or deflection.

  - Cut and neatly fit deck panels and accessories around openings and other work projecting through or adjacent to deck.

### *************************************************************************************************************Coordinate reinforcing requirements of openings in first Para. below with Section 05 5000.

*************************************************************************************************************

  - Provide additional reinforcement and closure pieces at openings as required for strength, continuity of deck, and support of other work.

  - Comply with AWS requirements and procedures for manual shielded metal arc welding, appearance and quality of welds, and methods used for correcting welding work.

### *************************************************************************************************************In deciding whether or not to retain Para. below, see para. 3.3 of the applicable SDI document(s) (i.e., “RD,” “NC,” &/or “C”).

*************************************************************************************************************

  - Mechanical fasteners may be used in lieu of welding to fasten deck. Locate mechanical fasteners and install according to deck manufacturer's written instructions.

  - ROOF-DECK INSTALLATION

### *************************************************************************************************************
This Article includes installation requirements for classes of roof deck and form deck used in roof applications. Revise first Para. below and insert requirements if mechanical fastening to supports is permitted.

*************************************************************************************************************

- Fasten roof-deck panels to steel supporting members by arc spot (puddle) welds of the surface diameter indicated or arc seam welds with an equal perimeter that is not less than 1-1/2 inches long, and as follows:

### *************************************************************************************************************
Retain one weld diameter from "Weld Diameter" subparagraph below or revise to suit Project.

*************************************************************************************************************

- Weld Diameter: [5/8 inch] [3/4 inch], nominal.

### *************************************************************************************************************

### Retain one of the two subparagraphs below. First subparagraph is based on SDI-RD. Revise if diaphragm-design requirements require closer weld spacings.

### Retain second subparagraph if showing requirements on Drawings.

*************************************************************************************************************

- Retain one weld spacing from options in "Weld Spacing" Subparagraph below. First option is based on SDI specifications for roof deck; second, on FMG Loss Prevention Data Sheet 1-29 recommendations for roof deck securement. Retain third if showing requirements on Drawings. Revise if diaphragm requirements or FM Global approval requires closer weld spacings.

- Weld Spacing: Weld edge ribs of panels at each support. Space additional welds an average of 12 inches apart, but not more than 18 inches apart.

- Weld Spacing: Space and locate welds as indicated.

### *************************************************************************************************************
Retain "Weld Washers" subparagraph below if deck thickness is less than 0.028 inch.

*************************************************************************************************************

- Weld Washers: Install weld washers at each weld location.

- Weld washers shall not be used between supports along the sidelaps.

### *************************************************************************************************************
SDI-RD requires side-lap and perimeter edge fastening if deck spans exceed 60 inches. Revise fastener spacing in Para. below if required.  Diaphragm-design requirements may necessitate fastening for spans < 60 inches, and/ or revision of fastener spacing below.

*************************************************************************************************************

- Side-Lap and Perimeter Edge Fastening: Fasten side laps and perimeter edges of panels between supports, at intervals not exceeding 36 inches, and as follows:

- SDI requires side-lap and perimeter edge fastening if deck spans exceed 60 inches (1524 mm). Revise fastener spacing in "Side-Lap and Perimeter Edge Fastening" Paragraph below if required.

- Side-Lap and Perimeter Edge Fastening: Fasten side laps and perimeter edges of panels between supports, at intervals not exceeding the lesser of 1/2 of the span or [18 inches] [36 inches], and as follows:

*************************************************************************************************************
Select acceptable fastening method(s) from subparagraphs below. Service loads or diaphragm design may require larger side lap welds.

For other options, see SDI-RD.

*************************************************************************************************************

- Select acceptable fastening method(s) from three subparagraphs below. Coordinate with choice of side lap.

          - Mechanically fasten with self-drilling, No. 10 diameter (0.19 inches) or larger, carbon-steel screws.

          - Fasten with arc spot welds with a minimum 5/8 inch minimum visible diameter, or minimum 1-1/2 inch long fillet weld.

*************************************************************************************************************
1-1/2” is the minimum end bearing stipulated in SDI-RD; however, it goes to say if < 1-1/2” of bearing is available, or if high support reactions are expected, the EOR should check the deck web crippling capacity..
*************************************************************************************************************

- End Bearing: Install deck ends over supporting frame with a minimum end bearing of 1-1/2 inches [Insert Dimension], with end joints as follows:

### *************************************************************************************************************
Retain one of three options in "End Joints" subparagraph below. SDI-RD allows lapped or butted ends for roof deck.

*************************************************************************************************************

- Retain one of three options in "End Joints" Subparagraph below. SDI allows lapped or butted ends for roof deck. FM Global recommends that ends lap a minimum of 2 inches (51 mm).

- End Joints: [Lapped] [Butted] [Lapped or butted at Installer's option].

- Roof Sump Pans and Sump Plates: Install over openings provided in roof deck and [weld] [mechanically fasten] flanges to top of deck. Space [welds] [mechanical fasteners] not more than 12 inches apart with at least one [weld] [fastener] at each corner.

- Install reinforcing channels or zees in ribs to span between supports and [weld] [or] [mechanically fasten].

- Miscellaneous Roof-Deck Accessories: Install ridge and valley plates, finish strips, end closures, and reinforcing channels according to deck manufacturer's written instructions. [Weld] [or] [mechanically fasten] to substrate to provide a complete deck installation.

- Weld cover plates at changes in direction of roof-deck panels unless otherwise indicated.

### *************************************************************************************************************
Retain Para. below if flexible closures are required or permitted. Usually delete if fire-resistance-rated partitions are required.
*************************************************************************************************************

- Flexible Closure Strips: Install flexible closure strips over partitions, walls, and where indicated. Install with adhesive according to manufacturer's written instructions to ensure complete closure.

### *************************************************************************************************************
Retain Para. below if installation of sound-absorbing insulation is specified in applicable low-slope roofing Section. Coordinate with roofing installation to prevent exposure to weather.

*************************************************************************************************************

- Sound-Absorbing Insulation: Installation into topside ribs of deck as specified in Section [Insert Section number] "[Insert title of applicable roofing Section]."

  - FLOOR-DECK INSTALLATION

### *************************************************************************************************************
This Article includes installation requirements for classes of floor deck and form deck used in floor applications. Revise first Para. below and insert requirements if mechanical fastening to supports is permitted.

*************************************************************************************************************

- Fasten floor-deck panels to steel supporting members by arc spot (puddle) welds of the surface diameter indicated and as follows:

### *************************************************************************************************************
Retain one weld diameter from "Weld Diameter" subparagraph below or revise to suit Project.

*************************************************************************************************************

- Weld Diameter: [5/8 inch] [3/4 inch], nominal.

### *************************************************************************************************************
Retain one of two "Weld Spacing" subparagraphs below. First subparagraph is based on SDI-NC and -C.  Revise if diaphragm-design requirements require closer weld spacings.

### Retain second subparagraph if showing requirements on Drawings.

*************************************************************************************************************

- Weld Spacing: Weld edge ribs of panels at each support. Space additional welds an average of 12 inches apart, but not more than 18 inches apart.

- Weld Spacing: Space and locate welds as indicated.

### *************************************************************************************************************
Retain "Weld Washers" subparagraph below if deck thickness is less than 0.028 inch.

*************************************************************************************************************

- Weld Washers: Install weld washers at each weld location.

- Weld washers shall not be used between supports along the sidelaps.

### *************************************************************************************************************
SDI-NC and -C require side-lap and perimeter edge fastening if deck spans exceed 60 inches.  Revise fastener spacing in Para. below if required.  Diaphragm-design requirements may necessitate fastening for spans < 60 inches, and/ or revision of fastener spacing below.

*************************************************************************************************************

- Side-Lap and Perimeter Edge Fastening: Fasten side laps and perimeter edges of panels between supports, at intervals not exceeding [36 inches, and as follows:

*************************************************************************************************************
Select acceptable fastening method(s) from subparagraphs below. Service loads or diaphragm design may require larger side lap welds.

For other options, see SDI-NC, and/or -C.

*************************************************************************************************************

- Select acceptable fastening method(s) from three subparagraphs below. Coordinate with choice of side lap.

- Mechanically fasten with self-drilling, No. 10 diameter (0.19 inches) or larger, carbon-steel screws.

- Fasten with arc spot welds with a minimum 5/8 inch minimum visible diameter, or a minimum of 1-1/2-inch-long fillet weld.

*************************************************************************************************************
1-1/2” is the minimum end bearing stipulated in SDI-NC; however, it goes to say if < 1-1/2” of bearing is available, or if high support reactions are expected, the EOR should check the deck web crippling capacity.

With regard to composite decks, SDI-C doesn’t stipulate a minimum, rather it requires EOR to determine min. bearing lengths AND fastener edge distances in accordance with AISI S100.
*************************************************************************************************************

- End Bearing: Install deck ends over supporting frame with a minimum end bearing of [1-1/2 inches] [Insert dimension], with end joints as follows:

### *************************************************************************************************************
Retain one of three options in subparagraph below or indicate locations of each choice on Drawings.  SDI-NC allows lapped or butted ends for noncomposite floor deck.

### Although SDI-C doesn’t explicitly state whether lapped, butted, or both type ends are allowed (or not), comparison of the language therein under “Tolerances,” compared with that of SDI-NC, indicates that lapped ends are not allowed.

*************************************************************************************************************

- End Joints: [Lapped] [Butted] [Lapped or butted at Installer's option].

- Pour Stops and Girder Fillers: Weld steel sheet pour stops and girder fillers to supporting structure according to recommendations of SDI-C and SDI-NC1.0, as applicable, unless otherwise indicated.

### *************************************************************************************************************
Revise "Floor-Deck Closures" Para. below to suit Project.  Sealing cellular deck openings, butt joints, and junctions with trench headers with tape is not included in this Section.

*************************************************************************************************************

- Floor-Deck Closures: Weld steel sheet column closures, cell closures, and Z-closures to deck, as indicated or required, to provide tight-fitting closures at open ends of ribs and sides of deck.

### *************************************************************************************************************
Revise spacing of hanger tabs in Para. below to suit Project.

*************************************************************************************************************

- Install piercing hanger tabs at [14 inches] [Insert spacing] apart in both directions, within 9 inches of walls at ends, and not more than 12 inches from walls at sides unless otherwise indicated.

- FIELD/ INSTALLER QUALITY CONTROL

        - Quality control tasks shall be performed by the installer’s QCI.

        - For quality control inspection, the construction documents, installation drawings, shop drawings, design documents and the applicable referenced standards shall be utilized.

        - In the event that the requirements of the construction documents conflict with the installation drawings or shop drawings, the requirements of the construction documents shall govern.

        - The QCI shall inspect the following as a minimum, as applicable:

          - Field welding of the deck in accordance with AWS D1.3, SDI-C, SDI-NC1.0, SDI-RD1.0.

          - Installation of mechanical fasteners in accordance with SDI-C, SDI-NC1.0, SDI-RD1.0, and manufacturer’s instructions.

          - Steel deck installation in accordance with construction documents, installation drawings, shop drawings, design documents and applicable referenced standards.

          - Scope of inspections shall comply with SDI-QA/QC Appendix 1.

- PROTECTION

### *************************************************************************************************************
Retain one or more of the three repairs paragraphs below if repairs to galvanized or painted surfaces are required. If limiting repairs to roof deck, revise below accordingly.

*************************************************************************************************************

- Galvanizing Repairs: Prepare and repair damaged galvanized coatings on both surfaces of deck with galvanized repair paint according to ASTM A 780 and manufacturer's written instructions.

### *************************************************************************************************************
Retain one of two "Repair Painting" paragraphs below if prime-painted deck is required. Usually retain first "Repair Painting" Paragraph for prime-painted deck and retain surface(s) requiring repair painting. Because shop primer protects for a limited time, repair painting is best applied during or immediately after deck installation.

*************************************************************************************************************

- Repair Painting: Wire brush and clean rust spots, welds, and abraded areas on [both surfaces] [top surface] of prime-painted deck immediately after installation, and apply repair paint.

### *************************************************************************************************************
Retain one of two subparagraphs below if appearance is important. Retain first subparagraph if retaining first option in "Repair Painting" Paragraph above. Retain second subparagraph if preparation and repair painting of bottom surface are specified in Section 09 9100 Painting.

*************************************************************************************************************

- Apply repair paint, of same color as adjacent shop-primed deck, to bottom surfaces of deck exposed to view.

- Wire brushing, cleaning, and repair painting are included in section 09 9100 Painting.

*************************************************************************************************************
Retain "Repair Painting" Paragraph below if repair-painting requirements are included in Section 09 9100 Painting. Coordinate field-painting requirements with Section 09 9100 Painting.

*************************************************************************************************************

- Repair Painting: Wire brushing, cleaning, and repair painting of rust spots, welds, and abraded areas of both deck surfaces are included in Section 09 9100 Painting.

END OF SECTION

********************************************************

### Do not delete the following reference information:

********************************************************

THE FOLLOWING STATEMENT IS FOR LANL USE ONLY

This project specification section is based on LANL Master Specification Section 05 3000 Rev. 4, dated September 3, 2020.

# Footnotes

Formally known as ANSI/SDI-NC1.0.  Similar applies to SDI-RD1.0 (i.e., ANSI/SDI…).