SECTION 08 1100

METAL DOORS AND FRAMES

*************************************************************************************************************

LANL MASTER SPECIFICATION

This template must be edited for each project.  In doing so, specifier must add job-specific requirements.  Brackets are used in the text to indicate designer choices or locations where text must be supplied by the designer.  Once the choice is made or text supplied, remove the brackets.  The specifications must also be edited to delete specification requirements for processes, items, or designs that are not included in the project, add specification requirements not included herein as well as delete specifier’s notes such as these.  Additional tailoring requirements are contained in ESM Chapter 1 Section Z10 Att. F, Specifications.

To seek a variance from requirements in the specifications that are applicable, contact the Engineering Standards Manual Architectural POC. Also, please contact the POC with suggestions for improvement as well.

When assembling a specification package, include applicable specifications from all Divisions, especially Division 1, General requirements.

Specification developed for ML-4 projects.  For ML-1, 2, and 3 applications, additional requirements and independent reviews should be added if increased confidence in procurement or execution is desired; see ESM Chapter 1 Section Z10 Specifications and Quality sections.
*************************************************************************************************************

PART 1  GENERAL

  - SUMMARY

Section includes:

[Interior standard steel doors and frames.]

[Exterior standard steel doors and frames.]

[Interior custom hollow-metal doors and frames.]

[Exterior custom hollow-metal doors and frames.]

Related Requirements:

Retain subparagraphs below to cross-reference requirements Subcontractor might expect to find in this Section but are specified in other Sections.

[Section 08 3473.13, Metal Sound Control Door Assemblies for packaged, acoustically rated hollow-metal door and frame assemblies.]

[Section 08 7100, Door Hardware for door hardware for hollow-metal doors.]

[Section 08 8000, Glazing for glass installed in hollow metal doors and frames.]

[Section 13 4900, Radiation Protection for lead-lined, hollow-metal doors and frames.]

[Section 28 1321, Administrative Access Control System Rough-In for access control and security systems.]

DEFINITIONS

Retain terms that remain after this Section has been edited for a project.

Retain "Minimum Thickness" Paragraph below to indicate that metal thicknesses specified are base-metal measurements and do not include metallic coatings or finishes. Thicknesses indicated in this Section are according to SDI A250.8 and NAAMM-HMMA 803, both of which use the same values.

Minimum Thickness: Minimum thickness of base metal without coatings according to SDI A250.8.

COORDINATION

Coordinate anchorage installation for hollow-metal frames. Furnish setting drawings, templates, and directions for installing anchorages, including sleeves, concrete inserts, anchor bolts, and items with integral anchors. Deliver such items to Project site in time for installation.

Coordinate requirements with the Subcontract Technical Representative (STR) for installation of door hardware, electrified door hardware, and access control and security systems.

  - REFERENCES

*********************************************************************************************************

Edit the references to include only those that apply to the edited specification section.

*********************************************************************************************************

- ASTM International

- ASTM A 153 – Standard Specification for Zinc Coating (Hot-Dip) on Iron and Steel Hardware

- ASTM A 653 – Standard Specification for Steel Sheet, Zinc-Coated (Galvanized) or Zinc-Iron Alloy-Coated (Galvannealed) by the Hot-Dip Process.

- ASTM A 879 - Standard Specification for Steel Sheet, Zinc Coated by the Electrolytic Process for Applications Requiring Designation of the Coating Mass on Each Surface

- ASTM A 1008 – Standard Specification for Steel, Sheet, Cold-Rolled, Carbon, Structural, High-Strength Low-Alloy, High-Strength Low-Alloy with Improved Formability, Solution Hardened, and Bake Hardenable

- ASTM A 1011 - Standard Specification for Steel, Sheet and Strip, Hot-Rolled, Carbon, Structural, High-Strength Low-Alloy, High-Strength Low-Alloy with Improved Formability, and Ultra-High Strength

- ASTM C 518 – Standard Test Method for Steady-State Thermal Transmission Properties by Means of the Heat Flow Meter Apparatus

- ASTM C 665 - Standard Specification for Mineral-Fiber Blanket Thermal Insulation for Light Frame Construction and Manufactured Housing

- ASTM E 136 - Standard Test Method for Behavior of Materials in a Vertical Tube Furnace at 750°C

- Builders Hardware Manufacturers Association (BHMA) A156.115 - Hardware Preparation in Steel Doors or Steel Frames

- National Fire Protection Association (NFPA)

- NFPA 80 – Standard for Fire Doors and Other Opening Protectives.

- NFPA 105 - Standard for Smoke Door Assemblies and Other Opening Protectives.

- NFPA 252 – Standard Methods of Fire Tests of Door Assemblies.

- NFPA 257 - Standard on Fire Test for Window and Glass Block Assemblies.

- Steel Door Institute (SDI)

- SDI 100 – Specifications for Standard Steel Doors and Frames.

- SDI A 250.3 - Test Procedure and Acceptance Criteria for Factory Applied Finish Coatings for Steel Doors and Frames.

- SDI A 250.4 - Test Procedure and Acceptance Criteria for Physical Endurance for Steel Doors, Frames and Frame Anchors.

- SDI A 250.6 –Recommended Practice for Hardware Reinforcing
on Standard Steel Doors and Frames.

- SDI A 250.8 – Specifications for Standard Steel Doors and Frames.

- SDI A 250.10 –Test Procedure and Acceptance Criteria for Prime Painted Steel Surfaces for Steel Doors and Frames.

- SDI A 250.11 – Recommended Erection Instructions for Steel Frames.

- SDI 111 – Recommended Details for Standard Steel Doors, Frames,
Accessories and Related Components.

- SDI 122 – Installation and Troubleshooting Guide for Standard Steel Doors and Frames.

- Underwriters Laboratories (UL)

- UL 9 – Standard for Fire Tests of Window Assemblies.

- UL 10C – Standard for Positive Pressure Fire Tests of Door Assemblies.

- UL 1784 - Standard for Air Leakage Tests of Door Assemblies.

************************************************************************************************************

Edit submittals to include only those absolutely necessary to assure requirements and features that are important for the specific project will be met.

************************************************************************************************************

  - ACTION SUBMITTALS

        - [Product Data: For each type of product.

Include construction details, material descriptions, core descriptions, fire-resistance ratings, and finishes.]

Retain "Shop Drawings" Paragraph below if applicable. SDI A250.8 indicates that manufacturer's published details can replace Shop Drawings for hollow-metal doors and frames unless otherwise indicated.

[Shop Drawings: Include the following:

Elevations of each door type.

Details of doors, including vertical- and horizontal-edge details and metal thicknesses.

Frame details for each frame type, including dimensioned profiles and metal thicknesses.

Locations of reinforcement and preparations for hardware.

Details of each different wall opening condition.

Details of electrical raceway and preparation for electrified hardware, access control systems, and security systems.

Details of anchorages, joints, field splices, and connections.

Details of accessories.

Details of moldings, removable stops, and glazing.]

Retain "Samples for Initial Selection" Paragraph and "Finishes" Subparagraph below for two-stage Samples of factory-applied finishes.

[Samples for Initial Selection: For hollow-metal doors and frames with factory-applied color finishes.]

[Samples for Verification:

Retain "Finishes" Subparagraph below if required for two-stage Samples of factory-applied finishes.

Finishes: For each type of exposed finish required, prepared on Samples of not less than 3 by 5 inches.

Retain "Fabrication" Subparagraph below if fabrication Sample is required.

Fabrication: Prepare Samples approximately 8 by 10 inches to demonstrate compliance with requirements for quality of materials and construction:

Doors: Show vertical-edge, top, and bottom construction; core construction; and hinge and other applied hardware reinforcement. Include separate section showing glazing if applicable.

Frames: Show profile, corner joint, floor and wall anchors, and silencers. Include separate section showing fixed hollow-metal panels and glazing if applicable.]

[Product Schedule: For hollow-metal doors and frames, prepared by or under the supervision of supplier, using same reference numbers for details and openings as those on Drawings. Coordinate with final door hardware schedule.]

  - INFORMATIONAL SUBMITTALS

Retain "Product Test Reports" Paragraph below for fire-rated assemblies.

- [Product Test Reports: For each type of hollow-metal door and frame assembly, for tests performed by a qualified testing agency.]

- [Oversize Construction Certification: For assemblies required to be fire-rated and exceeding limitations of labeled assemblies.]

  - QUALITY ASSURANCE

- Provide doors and frames complying with SDI 100 and as herein specified.

- Fire-Rated Door Assemblies:  Where fire-rated door assemblies are indicated or required, provide fire-rated door and frame assemblies that comply with NFPA 80, and have been tested, listed, and labeled in accordance with ASTM E 152 by a nationally recognized independent testing and inspection agency acceptable to LANL.

  - DELIVERY, STORAGE AND HANDLING

    - Deliver hollow metal work cartoned or crated to provide protection from damage during transit and job storage.  In addition, provide sealed doors in plastic wrapping. Provide additional protection to prevent damage to factory-finished units.

    - Inspect hollow metal work upon delivery for damage.  Minor damages may be repaired provided finish items are equal in all respects to new work and acceptable to the LANL Subcontract Technical Representative (STR); otherwise, remove and replace.

    - Store doors and frames at building site under cover.  Store vertically, place units on minimum 4in. high wood blocking.  Do not use non-vented plastic or canvas shelters which could create a humidity chamber.  If cardboard wrapper on door becomes wet, remove carton immediately.  Provide 1/4 inch space between stacked doors to promote air circulation.

PART 2 PRODUCTS

  - PERFORMANCE REQUIREMENTS

Revise "Fire-Rated Assemblies" Paragraph below to allow neutral pressure testing if required and as acceptable to authorities having jurisdiction. Retain option if temperature-rise-rated assemblies are required.

        - Fire-Rated Assemblies: Complying with NFPA 80 and listed and labeled by a qualified testing agency acceptable to LANL for fire-protection ratings and temperature-rise limits indicated, based on testing at positive pressure according to NFPA 252 or UL 10C.

Smoke- and Draft-Control Assemblies: Provide assemblies with gaskets listed and labeled for smoke and draft control by a qualified testing agency acceptable to LANL, based on testing according to UL 1784 and installed in compliance with NFPA 105.

Retain "Oversize Fire-Rated Door Assemblies" Subparagraph below if required by authorities having jurisdiction.

Oversize Fire-Rated Door Assemblies: For units exceeding sizes of tested assemblies, provide certification by a qualified testing agency that doors comply with standard construction requirements for tested and labeled fire-rated door assemblies except for size.

Retain "Temperature-Rise Limit" Subparagraph below if required and coordinate with option in "Fire-Rated Assemblies" Paragraph above. The IBC allows an exception for buildings equipped throughout with fire-suppression sprinklers.

Temperature-Rise Limit: Where indicated, provide doors that have a maximum transmitted temperature end point of not more than 450 deg F above ambient after 30 minutes of standard fire-test exposure.

Fire-Rated, Borrowed-Lite Assemblies: Complying with NFPA 80 and listed and labeled by a qualified testing agency acceptable to LANL, for fire-protection ratings indicated, based on testing according to NFPA 257 or UL 9.

Thermally Rated Door Assemblies: Provide door assemblies with U-factor of not more than 0.40 deg Btu/F x h x sq. ft. when tested according to ASTM C 518.

  - INTERIOR STANDARD STEEL DOORS AND FRAMES

        - Heavy-Duty Doors and Frames: SDI A 250.8, Level 2; SDI A 250.4, Level B.

Doors:

Type: As indicated in the Door and Frame Schedule.

Thickness: 1-3/4 inches.

Revise "Face" Subparagraph below if embossed or textured faces are required.

Face: Steel sheet, minimum thickness of 0.042 inch.

Edge Construction: Model 2, Seamless.

SDI A250.8 allows the edge bevel to be determined by manufacturer unless otherwise indicated.

Edge Bevel: Bevel lock edge 1/8 inch in 2 inches.

Unless otherwise indicated, SDI A250.8 permits manufacturers to choose core types, including kraft-paper honeycomb, polystyrene, polyurethane, polyisocyanurate, mineral board, or vertical steel stiffener. Retain first option in "Core" Subparagraph below to allow manufacturer to select core, or retain one of the other options to require a particular core.

Core: Manufacturer's standard.

Fire-Rated Core: Manufacturer's standard core for fire-rated and temperature-rise-rated doors.

Frames:

Materials: Steel sheet, minimum thickness of 0.053 inch.

[[Sidelite] [and] [Transom] Frames: Fabricated from same thickness material as adjacent door frame.]

Construction: Full profile welded.

In "Exposed Finish" Subparagraph below, verify with manufacturers availability of factory-finish option for welded frames.

Exposed Finish: [Prime] [Factory].

  - EXTERIOR STANDARD STEEL DOORS AND FRAMES

        - Extra-Heavy-Duty Doors and Frames: SDI A 250.8, Level 3; SDI A 250.4, Level A.

Doors:

Type: As indicated in the Door and Frame Schedule.

Thickness: 1-3/4 inches.

Revise "Face" Subparagraph below if embossed or textured faces are required.

Face: Metallic-coated steel sheet, minimum thickness of 0.053 inch coating.

Edge Construction: Model 2, Seamless.

SDI A250.8 allows the edge bevel to be determined by manufacturer unless otherwise indicated.

Edge Bevel: Bevel lock edge 1/8 inch in 2 inches.

Top Edge Closures: Close top edges of doors with flush closures of same material as face sheets. Seal joints against water penetration.

Bottom Edges: Close bottom edges of doors where required for attachment of weather stripping with end closures or channels of same material as face sheets. Provide weep-hole openings in bottoms of exterior doors to permit moisture to escape.

Unless otherwise indicated, SDI A250.8 permits manufacturers to choose core types, including kraft-paper honeycomb, polystyrene, polyurethane, polyisocyanurate, mineral board, or vertical steel stiffener. Retain first option in "Core" Subparagraph below to allow manufacturer to select core, or retain one of the other options to require a particular core. Coordinate core type with thermal requirements in "Thermally Rated Door Assemblies" Paragraph in "Performance Requirements" Article.

Core: Manufacturer's standard.

Fire-Rated Core: Manufacturer's standard core for fire-rated doors.

Frames:

Materials: Steel sheet, minimum thickness of 0.053 inch.

Some manufacturers have thermally broken frames available; revise "Construction" Subparagraph below if required.

Construction: Full profile welded.

In "Exposed Finish" Subparagraph below, verify with manufacturers availability of factory-finish option for welded frames.

Exposed Finish: [Prime] [Factory].

  - BORROWED LITES

        - Fabricate of steel sheet, minimum thickness of 0.053 inch.

Construction: Full profile welded.

Fabricate in one piece except where handling and shipping limitations require multiple sections. Where frames are fabricated in sections due to shipping or handling limitations, provide alignment plates or angles at each joint, fabricated of metal of same or greater thickness as metal as frames.

Provide countersunk, flat- or oval-head exposed screws and bolts for exposed fasteners unless otherwise indicated.

  - HOLLOW-METAL PANELS

        - Provide hollow-metal panels of same materials, construction, and finish as adjacent door assemblies.

  - FRAME ANCHORS

        - Jamb Anchors:

Type: Anchors of minimum size and type required by applicable door and frame standard, and suitable for performance level indicated.

Quantity: Minimum of three anchors per jamb, with one additional anchor for frames with no floor anchor. Provide one additional anchor for each 24 inches, or portion thereof, of frame height above 7 feet.

Post-installed Expansion Anchor: Minimum 3/8-inch diameter bolts with expansion shields or inserts, with manufacturer's standard pipe spacer.

Floor Anchors: Provide floor anchors for each jamb and mullion that extends to floor. Floor anchors may be set with power-actuated fasteners instead of post-installed expansion anchors if so indicated and approved on Shop Drawings.

Retain "Floor Anchors for Concrete Slabs with Underlayment" Paragraph below when using flowable underlayment over slabs or floor structure.

[Floor Anchors for Concrete Slabs with Underlayment: Adjustable-type anchors with extension clips, allowing not less than 2-inch height adjustment. Terminate bottom of frames at top of underlayment.]

Material: ASTM A 879, Commercial Steel (CS), 04Z coating designation; mill phosphatized.

For anchors built into exterior walls, steel sheet complying with ASTM A 1008 or ASTM A 1011; hot-dip galvanized according to ASTM A 153, Class B.

  - MATERIALS

        - Cold-Rolled Steel Sheet: ASTM A 1008, Commercial Steel (CS), Type B; suitable for exposed applications.

        - Hot-Rolled Steel Sheet: ASTM A 1011, Commercial Steel (CS), Type B; free of scale, pitting, or surface defects; pickled and oiled.

        - Metallic-Coated Steel Sheet: ASTM A 653, Commercial Steel (CS), Type B.

        - Inserts, Bolts, and Fasteners: Hot-dip galvanized according to ASTM A 153.

        - Power-Actuated Fasteners in Concrete: Fastener system of type suitable for application indicated, fabricated from corrosion-resistant materials, with clips or other accessory devices for attaching hollow-metal frames of type indicated.

        - Mineral-Fiber Insulation: ASTM C 665, Type I (blankets without membrane facing); consisting of fibers manufactured from slag or rock wool; with maximum flame-spread and smoke-developed indexes of 25 and 50, respectively; passing ASTM E 136 for combustion characteristics.

        - Glazing: Comply with requirements in Section 08 8000, Glazing.

  - FABRICATION

        - Construct hollow-metal doors and frames to comply with standards indicated for materials, fabrication, hardware locations, hardware reinforcement, tolerances, and clearances, and as specified.

        - Door Astragals: Provide overlapping astragal on one leaf of pairs of doors where required by NFPA 80 for fire-performance rating or where indicated. Extend minimum 3/4 inch beyond edge of door on which astragal is mounted or as required to comply with published listing of qualified testing agency.

        - Hollow-Metal Frames: Fabricate in one piece except where handling and shipping limitations require multiple sections. Where frames are fabricated in sections, provide alignment plates or angles at each joint, fabricated of metal of same or greater thickness as frames.

          - [Sidelite] [and] [Transom Bar] Frames: Provide closed tubular members with no visible face seams or joints, fabricated from same material as door frame. Fasten members at crossings and to jambs by welding [, or by rigid mechanical anchors].

          - Provide countersunk, flat- or oval-head exposed screws and bolts for exposed fasteners unless otherwise indicated.

          - Door Silencers: Except on weather-stripped frames, drill stops to receive door silencers as follows. Keep holes clear during construction.

            - Single-Door Frames: Drill stop in strike jamb to receive three door silencers.

            - Double-Door Frames: Drill stop in head jamb to receive two door silencers.

        - Hardware Preparation: Factory prepare hollow-metal doors and frames to receive templated mortised hardware, and electrical wiring; include cutouts, reinforcement, mortising, drilling, and tapping according to SDI A 250.6, the Door Hardware Schedule, and templates.

          - Reinforce doors and frames to receive non-templated, mortised, and surface-mounted door hardware.

          - Comply with BHMA A156.115 for preparing hollow-metal doors and frames for hardware.

        - Glazed Lites: Provide stops and moldings around glazed lites where indicated. Form corners of stops and moldings with mitered hairline joints.

          - Provide stops and moldings flush with face of door, and with square stops unless otherwise indicated.

          - Multiple Glazed Lites: Provide fixed and removable stops and moldings so that each glazed lite is capable of being removed independently.

          - Provide fixed frame moldings on outside of exterior and on secure side of interior doors and frames. Provide loose stops and moldings on inside of hollow-metal doors and frames.

          - Coordinate rabbet width between fixed and removable stops with glazing and installation types indicated.

          - Provide stops for installation with countersunk flat- or oval-head machine screws spaced uniformly not more than 9 inches o.c. and not more than 2 inches o.c. from each corner.

  - CLEARANCES

- Unless noted otherwise, clearances are subject to tolerance of plus or minus 1/32 inch.

- Clearance between Door and Frame Head and Jambs: 1/8 inch.

- Clearance between Meeting Edges of Pairs of Fire-Rated Doors: 1/8 inch plus or minus 1/16 inch.

- Clearance between Meeting Edges of Non-Rated Pairs of Doors: 1/8 inch to 1/4 inch.

- Clearance at Bottom: 5/8 inch.

- Clearance between Door Face and Door Stop: 1/16 inch to 1/8 inch.

  - STEEL FINISHES

        - Prime Finish: Clean, pretreat, and apply manufacturer's standard primer.

          - Shop Primer: Manufacturer's standard, fast-curing, lead- and chromate-free primer complying with SDI A 250.10; recommended by primer manufacturer for substrate; compatible with substrate and field-applied coatings despite prolonged exposure.

Verify, with manufacturer, availability of finishes in "Factory Finish" Paragraph below; not all manufacturers provide factory finishes.

        - Factory Finish: Clean, pretreat, and apply manufacturer's standard two-coat, baked-on finish consisting of prime coat and thermosetting topcoat, complying with SDI A 250.3.

Retain "Color and Gloss" Subparagraph below for factory finish.

          - Color and Gloss: As selected by Architect from manufacturer's full range.

  - LOUVERS

        - Provide louvers for interior doors, where indicated, which comply with SDI 111, with blades or baffles formed of 0.020-inch thick, cold-rolled steel sheet set into 0.032-inch thick steel frame.

        - Sightproof Louver: Stationary louvers constructed with inverted-V or inverted-Y blades.

        - Lightproof Louver: Stationary louvers constructed with baffles to prevent light from passing from one side to the other.

        - Fire-Rated Automatic Louvers: Louvers constructed with movable blades closed by actuating fusible link, and listed and labeled for use in fire-rated door assemblies of type and fire-resistance rating indicated by same qualified testing and inspecting agency that established fire-resistance rating of door assembly.

Form corners of moldings with hairline joints. Provide fixed frame moldings on outside of exterior and on secure side of interior doors and frames

PART 3  EXECUTION

  - PREPARATION

        - Remove welded-in shipping spreaders installed at factory. Restore exposed finish by grinding, filling, and dressing, as required to make repaired area smooth, flush, and invisible on exposed faces. Touch up factory-applied finishes where spreaders are removed.

Drill and tap doors and frames to receive non-templated, mortised, and surface-mounted door hardware.

  - INSTALLATION

        - General: Install hollow-metal doors and frames plumb, rigid, properly aligned, and securely fastened in place. Comply with approved Shop Drawings and with manufacturer's written instructions.

In "Hollow-Metal Frames" Paragraph below, retain option for SDI or NAAMM-HMMA installation standard to match standards organization cited for fabrication.

        - Hollow-Metal Frames: Comply with SDI A 250.11.

          - Set frames accurately in position; plumbed, aligned, and braced securely until permanent anchors are set. After wall construction is complete, remove temporary braces without damage to completed Work.

            - Where frames are fabricated in sections, field splice at approved locations by welding face joint continuously; grind, fill, dress, and make splice smooth, flush, and invisible on exposed faces. Touch-up finishes.

            - Install frames with removable stops located on secure side of opening.

          - [Fire-Rated Openings: Install frames according to NFPA 80.]

          - Floor Anchors: Secure with post-installed expansion anchors.

Retain first subparagraph below if permitted.

            - Floor anchors may be set with power-actuated fasteners instead of post-installed expansion anchors if so indicated and approved on Shop Drawings.

Retain first subparagraph below if required. Insulation may help reduce sound transmission.

          - Solidly pack mineral-fiber insulation inside frames.

          - [Masonry Walls: Coordinate installation of frames to allow for solidly filling space between frames and masonry with grout or mortar.]

Retain option in "In-Place Concrete or Masonry Construction" Subparagraph below if required.

          - [In-Place Concrete or Masonry Construction: Secure frames in place with post-installed expansion anchors. [Countersink anchors, and fill and make smooth, flush, and invisible on exposed faces.]]

          - Installation Tolerances: Adjust hollow-metal frames to the following tolerances:

            - Squareness: Plus or minus 1/16 inch, measured at door rabbet on a line 90 degrees from jamb perpendicular to frame head.

            - Alignment: Plus or minus 1/16 inch, measured at jambs on a horizontal line parallel to plane of wall.

            - Twist: Plus or minus 1/16 inch, measured at opposite face corners of jambs on parallel lines, and perpendicular to plane of wall.

            - Plumbness: Plus or minus 1/16 inch, measured at jambs at floor.

Add text if grouting frames is required. Industry recommendations discourage grouting. See the Evaluations.

        - Hollow-Metal Doors: Fit and adjust hollow-metal doors accurately in frames, within clearances specified below.

In "Non-Fire-Rated Steel Doors" Subparagraph below, retain first option if using SDI standards in Part 2; retain second option if using NAAMM-HMMA standards in Part 2.

          - Non-Fire-Rated Steel Doors: Comply with SDI A 250.8.

Retain "Fire-Rated Doors" and "Smoke-Control Doors" subparagraphs below if required.

          - Fire-Rated Doors: Install doors with clearances according to NFPA 80.

          - Smoke-Control Doors: Install doors according to NFPA 105.

        - Glazing: Comply with installation requirements in Section 08 8000 "Glazing" and with hollow-metal manufacturer's written instructions.

  - CLEANING AND TOUCHUP

Retain "Prime-Coat Touchup," "Metallic-Coated Surface Touchup," or "Factory-Finish Touchup" Paragraph below for field touchup of painted surfaces; or delete all and retain "Touchup Painting" Paragraph below if touchup is included in painting Sections.

        - Prime-Coat Touchup: Immediately after erection, sand smooth rusted or damaged areas of prime coat and apply touchup of compatible air-drying, rust-inhibitive primer.

        - Metallic-Coated Surface Touchup: Clean abraded areas and repair with galvanizing repair paint according to manufacturer's written instructions.

        - Factory-Finish Touchup: Clean abraded areas and repair with same material used for factory finish according to manufacturer's written instructions.

        - Touchup Painting: Cleaning and touchup painting of abraded areas of paint are specified in painting Sections.

END OF SECTION

***********************************************************

Do not delete the following reference information:

***********************************************************

THE FOLLOWING STATEMENT IS FOR LANL USE ONLY

This project specification is based on LANL Master Specification Section 08 1100 Rev. 2, dated June 8, 2017.