SECTION 09 5100

ACOUSTICAL CEILINGS

*************************************************************************************************************

LANL MASTER SPECIFICATION

New in this revision: Updated for compliance with earthquake loads in ESM Ch. 5 Sect. II R11 (i.e., new accelerations for SDC D and new SDC C and its accelerations)

This template must be edited for each project.  In doing so, specifier must add job-specific requirements.  Brackets are used in the text to indicate designer choices or locations where text must be supplied by the designer.  Once the choice is made or text supplied, remove the brackets.  The document must also be edited to delete specification requirements for processes, items, or designs that are not included in the project, add requirements not contained herein as well as deleting specifier’s notes such as these.  Additional tailoring requirements are contained in ESM Chapter 1 Section Z10 Att. F, Specifications.

To seek relief from requirements in the specifications that are applicable, contact the Engineering Standards Manual Architectural POC. Please contact POC with suggestions for improvement as well.

When assembling a specification package, include applicable specifications from all Divisions, especially Division 1, General requirements.

Section developed for ML-4 projects.  For ML-1, 2, and 3 applications, additional requirements and independent reviews should be added if increased confidence in procurement or execution is desired; see ESM Chapter 1 Section Z10 Specifications and Quality sections.

Seismic

Specification includes requirements associated with seismic design in accordance with ASCE 7, para. 13.5.6, Suspended Ceilings.  Note that there are two exceptions to 13.5.6 that exempt a suspended ceiling from seismic design.  If Project ceiling is exempt, then the portions of this specification that pertain to seismic design must be deleted.

For “non-seismically-exempt suspended ceilings,” ASCE 7 Sect. 13.2 includes two methods for achieving compliance:

1)  Project-specific design and documentation (PSDD), or

2)  Manufacturer’s certification (MC).

If Project selects 1), it has two (2) options:  The EOR can prepare the PSDD, or responsibility for the PSDD can be delegated to the construction subcontractor if allowed by EOR subcontract.  This template must be edited for use for one of these options.

If Project selects 2), this template must be edited to reference (in RELATED REQUIREMENTS) Section 01 8734, Seismic Qualification of Nonstructural Components (IBC), and that Section must be edited for Project specificity.

Finally, the Statement of Special Inspections (SSI) for Projects that include “non-seismically-exempt suspended ceilings” shall include all inspections required by the applicable ICC-ES Report (or similar) for the suspended-ceiling system specified for use.  And, for Projects using MC, the SSI shall also include the Certificate of Compliance.  Refer to ESM Ch. 16 Sect. IBC-IP, Attachment B, Tables 1705.1.1 (special cases), 1704.5 (steel), and 1705.13 (seismic resistance) -- as applicable.  
*************************************************************************************************************

GENERAL

SECTION INCLUDES

Suspended metal grid ceiling system and perimeter trim.

Acoustic [tile] [panels] [metal pans]

Supplementary acoustic insulation over system units.

related requirements

01 4000 Quality Requirements

[Section 01 8734 Seismic Qualification of Nonstructural Components (IBC)]

[Section 05 0520 Post-Installed Concrete and Grouted-Masonry Anchors – Normal Confidence]

[Section 05 0521 Post-Installed Concrete Anchors – High Confidence]

07 2100 Insulation

07 9200 Joint Sealants

08 3100 Access Doors and Panels

09 2116 Gypsum Board Systems

21 1313 Wet Pipe Sprinkler System: Sprinkler Heads in Ceiling Systems

23 3700 Air Outlets and Inlets: Air Diffusion Devices in Ceiling Systems

26 5100 Interior Lighting: Light Fixtures in Ceiling System

27 3000 Voice Communications: Speakers in Ceiling System

28 4600 Fire Detection and Alarm: Fire Alarm Components in Ceiling System

rEFERENCE STANDARDS

ASTM International:

ASTM A 580 - Specification for Stainless Steel Wire

ASTM A 641 – Specification for Zinc-Coated (Galvanized) Carbon Steel Wire

ASTM A 653 - Specification for Steel Sheet, Zinc-Coated (Galvanized) or Zinc-Iron Alloy-Coated (Galvannealed) by the Hot-Dip Process

ASTM B 164 - Specification for Nickel-Copper Alloy Rod, Bar, and Wire

ASTM C 635 - Specification for the Manufacture, Performance, and Testing of Metal Suspension Systems for Acoustical Tile and Lay-in Panel Ceilings

ASTM C 636 - Practice for Installation of Metal Ceiling Suspension Systems for Acoustical Tile and Lay-In Panels

ASTM E 84 –Test Method for Surface Burning Characteristics of Building Materials

ASTM E 119 –Test Methods for Fire Tests of Building Construction and Materials

ASTM E 580 - Practice for Installation of Ceiling Suspension Systems for Acoustical Tile and Lay-in Panels in Areas Subject to Earthquake Ground Motions

ASTM E 1264 - Classification for Acoustical Ceiling Products

American Society of Civil Engineers

ASCE 7 - Minimum Design Loads for Buildings and Other Structures

International Code Council

IBC - International Building Code

UL – Underwriters Laboratory Directory of Construction Materials.

****************************************************************************************************
Include the following paragraph as required to coordinate acoustical ceiling installation with other trades.
****************************************************************************************************

[ADMINISTRATIVE REQUIREMENTS]

[Pre-installation Conference: Conduct conference at Project site to:

Review interfaces with mechanical and electrical systems.

Review and finalize construction schedule and verify availability of materials, Installer’s personnel, equipment, and facilities needed to meet the schedule and avoid delays.]

*************************************************************************************************************

Edit submittals to include only those absolutely necessary to assure the requirements and features that are important for the specific project will be met.

*************************************************************************************************************

ACTION SUBMITTALS

    - [Product Data: Unless providing exactly as specified, submit data for grid system, panels/tiles, and accessories; electrical resistance characteristics and ground connection requirements.]

    - Shop Drawings: Indicate ceiling layout, interruptions to grid, [special-sized panels/tiles,] panels or tiles requiring drilling or cut-out for services, appurtenances or interruptions, edge details, [elevation differences,] [location of mechanical and electrical interfaces,] [and] [________].

*************************************************************************************************************

Include the following paragraph if ceilings are not exempt from seismic design, and PSDD will be provided.  Don’t include paragraph if MC is applicable.  Refer to author note on page 1 for details.

*************************************************************************************************************

      - Indicate installation details required for seismic restraint.

*************************************************************************************************************

Include the following paragraph for submission of physical samples for selection of finish, color, texture, and other properties unless selected during design and specified in 2.1.A below.

*************************************************************************************************************

    - [Samples: Submit two [____x____] inch in size of ceiling grid and panel, illustrating finishes and color.]

    - Manufacturer's Installation Instructions: Submit special procedures, perimeter conditions requiring special attention, and [________].

*************************************************************************************************************

Include the following paragraph if ceilings are (1) not exempt from seismic design and (2) PSDD will be the responsibility of the Subcontractor.  Don’t include paragraph if PSDD will be provided by EOR, or if MC applies to Project.  Refer to author note on page 1 for details.

Professional engineer is defined in Section 01 4000 Quality Requirements.

*************************************************************************************************************

    - Delegated-Design Submittal: For seismic restraints for ceiling systems.

      - Include design calculations for seismic restraints including analysis data signed and sealed by the professional engineer, registered in the State of New Mexico, responsible for their preparation.

*************************************************************************************************************

Delete the following paragraph only if ceilings are exempt from seismic design. *************************************************************************************************************

    - Independent Evaluation Reports: For each acoustical panel ceiling suspension system [and fastener type], from ICC-ES or similar.

    - Field quality-control reports.

  - SUSTAINABLE DESIGN SUBMITTALS

Manufacturer's Certificate: Certify products meet or exceed specified sustainable design requirements.

*************************************************************************************************************

Edit material certifications list to suit products specified in this section and Project sustainable design requirements.

*************************************************************************************************************

      - Materials Resources Certificates:

  - Certify source and origin for [salvaged] [and] [reused] products.

  - Certify recycled material content for recycled content products.

  - Certify source for local and regional materials and distance from Project site.

      - Indoor Air Quality Certificates: Certify volatile organic compound content for each interior sealant and related primer.

  - CLOSEOUT SUBMITTALS

- Operation and Maintenance Data

- Warranty Documentation

- Project Records Documentation

  - EXTRA STOCK MATERIALS Submittals

    - Furnish [________] sq. ft. of extra [tiles] [panels] [metal pans] to the LANL Subcontract Technical Representative (STR).

****** [OR] ******

    - Furnish [________] percent of total acoustic unit area of extra [tiles] [panels] [metal pans] to the LANL Subcontract Technical Representative (STR).

  - QUALITY ASSURANCE

    - Qualifications

      - Manufacturer: Company specializing in manufacturing Products specified in this section with minimum three years [documented] experience.

      - Installer: Company specializing in performing Work of this section [with minimum [________] years [documented] experience [approved by manufacturer].

    - Source Limitations:  Obtain ceiling system through one source from a single manufacturer.

************************************************************************************************************ Fire-rated ceiling system includes all elements above ceiling including floor or roof construction and can include specially constructed gypsum box or acoustic panel surrounding light fixtures and mechanical work. 
***********************************************************************************************************

    - Fire Rated [Floor] [Roof] Construction: [Rating as indicated on Drawings] [[_________] hour rating].

      - Tested Rating: Determined in accordance with ASTM E 119.

************************************************************************************************************* Refer to IBC for tables of fire resistance ratings for various material and assemblies. Tables use item numbers to identify each assembly.
*************************************************************************************************************

      - Prescriptive Rating: [Item Number [________];] determined in accordance with [applicable] [_________] code.

      - Installed System: Conform to [UL] [WH] Design [________] for [ceiling and floor] [ceiling and roof] [_________] assembly.

************************************************************************************************************* IBC requires surface burning to be tested in accordance with ASTM E 84 for individual materials or NFPA 286 for wall and ceiling assemblies.
*************************************************************************************************************

    - Surface Burning Characteristics: Maximum [25/450] [75/450] [200/450] flame spread/smoke developed index when tested in accordance with ASTM E 84.

    - Surface Burning Characteristics: Comply with the following when tested in accordance with NFPA 286.

      - During 40 kW Exposure: No flame spread to ceiling.

      - During 160 kW Exposure: No flame spread to perimeter of tested sample and no flashover.

      - Total Smoke Release: Maximum 1,000 cu m.

*************************************************************************************************************

Include following paragraph if a mock-up is required for approval of final acoustical ceiling design.
*************************************************************************************************************

    - [Mockups:  Build mockups to verify selections made under sample submittals and to demonstrate aesthetic effects and set quality standards for materials and execution.

      - Construct mock-up, 12 feet x 12 feet, including typical field and edge conditions.

      - Locate where indicated on Drawings.

      - Approved mockups may become part of the completed Work if undisturbed up to time of Substantial Completion.]

  - delivery, storage, and handling

    - Deliver acoustical panels/tiles, suspension-system components, and accessories to Project site in original, unopened packages and store them in a fully enclosed, conditioned space where they will be protected against damage from moisture, humidity, temperature extremes, direct sunlight, surface contamination, and other causes.

    - Before installing acoustical panels or tiles, permit them to reach room temperature and stabilized moisture content.

    - Handle acoustical panels and tiles carefully to avoid chipping edges or damaging units in any way.

  - SITE CONDITIONS

    - Install ceiling panels/tiles only after building is enclosed, sufficient heat is provided, dust generating activities have been finished, overhead work is completed, tested and approved, and interior wet work is dry.

    - Maintain uniform temperature of minimum 60 degrees F and a maximum humidity of 40 percent prior to, during, and after ceiling installation.

  - WARRANTY:  Provide manufacturer’s standard, all inclusive warranty.

- PRODUCTS

  - MANUFACTURERS:

      - [Armstrong World Industries, Inc.], Model [________].

      - [CertainTeed Corporation], Model [_________].

      - [United States Gypsum Company], Model [________].

      - Chicago Metallic Corporation, Model [________].

      - [____________________] Model [________].

  - PERFORMANCE REQUIREMENTS

*************************************************************************************************************

Retain the following paragraph if the ceiling(s) isn’t exempt from seismic.  If retaining, edit the Para. in accordance with related edits made in PART 1, and the following:

- Retain only subparagraph 1 if the ceiling must be designed with a Component Importance Factor, Ip, = 1.5 (i.e., it’s a Designated Seismic System, or DSS).

  - Retain the text in the 1st set of brackets if PSDD applies and will be provided by EOR.

  - Retain the text in the 2nd set of brackets if PSDD applies and will be the responsibility of the Subcontractor.

  - Retain the text in the 3rd set of brackets if MC applies to Project.

- Retain only supara. 2 if the ceiling isn’t a DSS, and edit brackets as described for subpara. 1 (above).

  - Retain subparas. 2.a.i and ii if the ceiling(s) includes a sprinkler head(s).

In short, the goals of these performance requirements are as follows:

- DSS:  The extent of damage to the ceiling caused by the design-basis earthquake shall not result in the loss of functionality/operability of the facility, or “ceiling-ed room.”  What this means is that no part of the ceiling falls and, as applicable, “services” that are part of the ceiling (e.g., lights, HVAC, sprinkler heads, etc.) will be operable/functional.

- Non-DSS w/o a sprinkler head:  The extent of damage to the ceiling caused by the design-basis earthquake can be severe up to, but not including, falling of its parts and pieces.

- Non-DSS w/ a sprinkler head:  Same as “w/o;” however, any/all sprinkler heads must be operable following the design-basis earthquake.

*************************************************************************************************************

    - Seismic Performance

The ceiling is a Designated Seismic System and, as such, it shall withstand the effects of earthquake motions as represented by the [seismic hazard indicated on the drawings] [the forces derived from the specified criteria] [design basis earthquake in Section 01 8734].

        - The term “withstand” means “the ceiling will not sustain damage that would result in the loss of functionality/operability of the space/area beneath it when subjected to the seismic [hazard indicated on the drawings] [forces derived from the specified criteria].”

The ceiling shall withstand the effects of earthquake motions as represented by the [seismic hazard indicated on the drawings] [the forces derived from the specified criteria] [design basis earthquake in Section 01 8734].

##### The term “withstand” means “no part of the ceiling will fall when subjected to the [seismic hazard indicated on the drawings] [derived from the specified criteria].”

### The preceding definition of “withstand” is not applicable to the fire- protection sprinklers (FPS) heads.

### The term “withstand” for FPS heads means “no head shall sustain damage caused by the motion of, or damage sustained by, the ceiling it’s contained in to the extent that it’s inoperable following the earthquake motions in question.

    - Surface-Burning Characteristics: Comply with ASTM E 84; testing by a qualified testing agency. Identify products with appropriate markings of applicable testing agency.

    - Fire-Resistance Ratings: Comply with ASTM E 119; testing by a qualified testing agency. Identify products with appropriate markings of applicable testing agency.

- Indicate design designations from UL’s “Fire Resistance Directory” or from the listings of another qualified testing agency.

*************************************************************************************************************

Retain the following Article if ceiling(s) aren’t exempt from seismic design, and PSDD will be the responsibility of the Subcontractor.  Don’t retain it if PSDD will be provided by EOR, or if MC applies to Project.  
*************************************************************************************************************

  - SEISMIC DESIGN CRITERIA

    - Delegated Design: Engage a qualified professional engineer, as defined in Section 01 4000 Quality Requirements, to design seismic restraints for ceiling systems.

*************************************************************************************************************

Ref. ESM Ch. 5 Sect. II, Earthquake Loads for the source of the criteria/data listed below, and for editing of them.
*************************************************************************************************************

    - Acoustical ceiling shall be designed in accordance with the aforementioned “Seismic Performance” requirements, the loads derived from the following parameters/data.

      - Seismic-Restraint Loading:

        - IBC Risk Category:  [I] [II] [III] [IV].

        - IBC Site Class:  D.

*************************************************************************************************************

Edit the next two (2) subparas. based on the applicable SDC (i.e., D or C).  In each instance in which options exist, the 1st two (2) are the default values for SDC D and SDC C, respectively.

A good reference for the differences between the code requirements for industry-standard construction for ceilings in SDC D vs. SDC C is ASCE 7 Para. C13.5.6.2 & its Table C13.5.6.1.

*************************************************************************************************************

        - IBC Design Spectral Response Acceleration Parameters:  SDS = [0.55] [0.49] [____]g, SD1 = [0.44] [0.23] [____]g, T0 = [0.12] [0.10] [___ ] sec.

        - IBC Seismic Design Category:  [D] [C].

        - ASCE 7 Component Importance Factor, Ip:  [1.0] [1.5].

        - ASCE 7 Component Response Modification Factor: 2.5.

        - ASCE 7 Component Amplification Factor: 1.0.

  - acoustical TILES AND panels, general

    - Low-Emitting Materials: Acoustical tile and panel ceilings shall comply with the testing and product requirements of the California Department of Health Services’ “Standard Practice for the Testing of Volatile Organic Emissions from Various Sources Using Small-Scale Environmental Chambers.”

    - Recycled Content:

- Minimum 20% recycled content.

    - Glass-Fiber-Based Tiles and Panels: Made with binder containing no urea formaldehyde.

************************************************************************************************************

Biobased acoustical tiles and panels are Designated Green Products for Federal Procurement by the EPA.  However biobased acoustical tiles and panels are currently a cost premium to industry standard mineral or glass fiber acoustical tiles and panels.  In addition use of biobased products in wet areas, clean rooms and/or laboratories should be used with caution.  Include following paragraph only if use of biobased product is cost effective and will not impact the environmental quality or programmatic requirements of the proposed usage.
*************************************************************************************************************

    - [Biobased Tiles and Panels:  Minimum 37% biobased content.]

    - Acoustical Tile and Panel Standard: Provide manufacturer’s standard tiles and panels of configuration indicated that comply with ASTM E 1264 classifications as designated by types, patterns, acoustical ratings, and light reflectance unless otherwise indicated.

- Mounting Method for Measuring NRC: Type E-400; plenum mounting in which face of test specimen is 15-3/4 inches away from test surface according to ASTM E 795.

    - Acoustical Tiles and Panel Colors and Patterns: Match appearance characteristics indicated for each product type.

      - Where appearance characteristics of acoustical tiles and panels are indicated by referencing pattern designations in ASTM E 1264 and not manufacturer’s proprietary product designations, provide products selected by Architect from each manufacturer’s full range that comply with requirements indicated for type, pattern, color, light reflectance, acoustical performance, edge detail, and size.

  - acoustical TILES AND PANELS

    - Acoustic Tile: [ASTM E 1264,] conforming to the following:

      - Size: 12 x 12 inches.

      - Thickness: [5/8] [_________] inches.

      - Composition: [Mineral] [_________].

      - Density: [________] lb/cu.ft.

******************************************************************************************** Comply with LANL ESM Chapter 7, Electrical Section D5020, paragraph 7.1.B to obtain initial surface reflectance recommended in the IES Lighting Handbook (90%).
********************************************************************************************

      - Light Reflectance: [________] percent.

      - NRC Range: [________] to [________].

      - STC Range: [________] to [________].

      - Joint: [Kerfed] [Rabbeted] [_________].

      - Edge: [Square] [Beveled].

      - Surface Color: [White] [________].

      - Surface Finish: [Perforated] [Non-directional fissured] [Directional fissured] [________], [plastic wrapped].

******** [AND/OR] ********

    - Acoustic Panels: [ASTM E 1264,] conforming to the following:

      - Size: [12 x 24] [24 x 48] [24 x 24] [____x____] inches.

      - Thickness: [3/4] [5/8] [________].

      - Composition: [Mineral] [________________]

      - Density: [_______] lb/cu.ft.

******************************************************************************************** Comply with LANL ESM Chapter 7, Electrical Section D5020, paragraph 7.1.B to obtain initial surface reflectance recommended in the IES Lighting Handbook (90%).
********************************************************************************************

      - Light Reflectance: [________] percent.

      - NRC Range: [________] to [________].

      - STC Range: [________] to [________].

      - Edge: [Square.] [Rabbeted.] [________________]

      - Surface Color: [White] [________] color [as selected].

  - metal suspension systems, general

    - Recycled Content:

      - Steel:  Minimum 25% recycled content.

      - Aluminum: Minimum 50% recycled content.

    - Metal Suspension-System Standard: Provide manufacturer’s standard direct-hung metal suspension system and accessories according to ASTM C 635 and designated by type, structural classification, and finish indicated.

- High-Humidity Finish: Comply with ASTM C 635 requirements for “Coating Classification for Severe Environment Performance” where high-humidity finishes are indicated.

  - metal suspension system

    - Non-fire Rated Grid: [ASTM C 635, [light] [intermediate] [heavy] duty]; [exposed T] [exposed T/one direction] [concealed T and G] [concealed H and T] [paired access T] [downward access removable T] [concealed Z] [concealed T] [metal pan T] [________]; components die cut and interlocking.

******** [AND/OR] ********

    - Fire Rated Grid: [ASTM C 635, [light] [intermediate] [heavy] duty], listed by UL for use in [________] hour assembly, [two directional concealed] [exposed T] [exposed T/one direction] [________]; components die cut and interlocking.

****************************************************************************************************
Only steel grid material can be used in fire rated systems.
****************************************************************************************************

    - Grid Materials: [Commercial quality cold rolled steel with galvanized coating.] [Cold rolled aluminum.] [Extruded aluminum.] [________].

    - Exposed Grid Surface Width: [15/16] [9/16] [________] inch [with reveal].

****************************************************************************************************

Include the “seismic-design option” in following paragraph if ceiling isn’t “exempt from seismic.” ****************************************************************************************************

    - Perimeter/Edge Molding and Trim:  Type and profile indicated or, if not indicated, manufacturer's standard moldings for edges and penetrations [that comply with seismic design requirements]; formed from sheet metal of same material, finish, and color as that used for exposed flanges of suspension-system runners.

****************************************************************************************************

Include the 1st & 3rd of the following subparas. if ceiling is exempt from seismic design.

Delete these subparas, and retain the 2nd one if ceiling isn’t exempt.

If retaining the 2nd subpara., select the 1st option if SDC D applies, and select the 2nd option if SDC C applies.

NOTE 1:  With regard to 2nd subpara, if SDC D applies there is more to compliance with ASCE 7 subpara. 13.5.6.2.2.a, than merely providing min. 2”-width perimeter support if/ when perimeter support clips are used.  And, for ceiling areas > 2500 ft2, “the more” might be required for compliance with 13.5.6.2.2.b.

NOTE 2:  With regard to 3rd subpara, ASCE 7 para. 13.5.6.3 doesn’t require large clearances around sprinkler piping penetrations for “non-exempt ceilings” if “Integral Construction” is used in lieu of “Industry Standard Construction.”

****************************************************************************************************

      - Perimeter Molding Width: Match grid width.

      - Perimeter Molding Width: Minimum [2] [7/8] inches.

      - For circular penetrations of ceiling, provide edge moldings fabricated to diameter required to fit penetration exactly.

    - Grid Finish: [White] [Anodized] [________].] [[________] color [as selected].]

  - accessories

*************************************************************************************************************

Include the “seismic-design option” in following paragraph if ceiling isn’t “exempt from seismic.”

*************************************************************************************************************

    - Attachment Devices:  Size for five times the design load indicated in ASTM C 635, Table 1, "Direct Hung," unless otherwise indicated.  [Comply with seismic design requirements.]

*************************************************************************************************************

Include the following subparagraph if post-installed (P-I) anchors are to be used to attach the ceiling to the supporting structure.  If this is the case then the P-I anchors shall be specified in the appropriate Division-3 Section.

*************************************************************************************************************

      - Post-Installed Anchors: Provide anchors indicated and specified in Section 05 0520 [05 0521].

*************************************************************************************************************

Include the following subparagraph if power-actuated fasteners (PAFs) are to be used to attach the ceiling to the supporting structure, and select from the options provided.

Each option is backed by an ICC-ES Report that requires design calculations.  Use of other products is allowed provided they have similar “backing.”

If the ceiling isn’t exempt from seismic, and if the SDC is D, ASCE 7 para. 13.4.5 limits the use of PAFs in concrete and steel to service loads, on any individual fastener, of 90 and 250 lb, respectively.

*************************************************************************************************************

      - Power-Actuated Fasteners in Concrete: [Hilti Low-velocity Power-actuated Fasteners] [Ramset and Duo-Fast Power-Actuated Fasteners and Ceiling Clip Assemblies] [Insert product].

    - Wire Hangers, Braces, and Ties: Provide wires complying with the following requirements:

*************************************************************************************************************

Include 1 or more of the next 3 subparagraphs.  If more than 1 type of wire is required, indicate locations for each type on Drawings. See the AIA MasterSpec Evaluations doc (for 095113) for discussion of humidity considerations in corrosive environments. Revise hangers to strap type if required by LANL STR.

*************************************************************************************************************

      - Zinc-Coated, Carbon-Steel Wire: ASTM A 641, Class 1 zinc coating, soft temper.

      - Stainless-Steel Wire: ASTM A 580, Type 304, nonmagnetic.

      - Nickel-Copper-Alloy Wire: ASTM B 164, nickel-copper-alloy UNS No. N04400.

************************************************************************************************************

Retain 2nd option in "Size" subparagraph below if required by LANL STR or if desired for extra security and quality (including an allowance for corrosion). Large sizes are difficult to work with, and could result in difficulty leveling the ceiling. 
*************************************************************************************************************

      - Size: Select wire diameter so its stress at three times hanger design load (ASTM C 635, Table 1, “Direct Hung”) will be less than yield stress of wire, but provide not less than [0.106-inch] [0.135-inch] [Insert dimension] diameter wire.

************************************************************************************************************

If retaining paragraph below, select an option, and insert sizes or indicate on Drawings. 
*************************************************************************************************************

    - [Hanger Rods] [Flat Hangers]: Mild steel, zinc coated or protected with rust-inhibitive paint.

*************************************************************************************************************

If retaining paragraph below, select an option, and insert sizes or indicate on Drawings. 
*************************************************************************************************************

    - Angle Hangers: Angles with legs not less than 7/8 inch wide; formed with 0.04-inch thick, galvanized-steel sheet complying with ASTM A 653, G90 coating designation; with bolted connections and 5/16-inch diameter bolts.

*************************************************************************************************************

Retain paragraph below if ceiling is direct-concealed suspended system, isn’t exempt from seismic, and if SDC D applies.  For more detail, refer to ASTM E560 para. 5.2.5.

If ceiling is exempt from seismic, but stabilizer bars are needed to improve stability of the suspension system and unit alignment, retain Para. and revise as necessary. 
*************************************************************************************************************

    - Seismic Stabilizer Bars: Manufacturer’s standard perimeter stabilizers designed to accommodate seismic forces.

*************************************************************************************************************

Retain paragraph below if ceiling isn’t exempt from seismic & if SDC D applies.  For more detail, refer to ASTM E560 para. 5.2.8.  Coordinate with manufacturer's requirements and LANL STR. 
*************************************************************************************************************

    - Seismic Struts: Manufacturer’s standard compression struts designed to accommodate seismic forces.

*************************************************************************************************************

Retain paragraph below if ceiling isn’t exempt from seismic and if SDC D applies.  For more detail, refer to ASCE 7 para. 13.5.6.2.2.a.  Coordinate with manufacturer's requirements and LANL STR.  
*************************************************************************************************************

    - Seismic Clips: Manufacturer’s standard seismic clips designed to secure acoustical panels in place during a seismic event.

*************************************************************************************************************

Retain paragraph below if required. Fire-resistance-rated panels generally weigh more than 1 lb/sq. ft., and hold-down clips are not required to comply with UL design requirements. Verify weight of panels selected for UL fire-resistant designs, and revise below to require hold-down clips for fire-resistance-rated ceilings with panels weighing less than 1 lb/sq. ft. 
*************************************************************************************************************

    - Hold-Down Clips: Manufacturer’s standard hold-down.

*************************************************************************************************************

Retain paragraph below if required. 
*************************************************************************************************************

    - Impact Clips: Manufacturer’s standard impact-clip system designed to absorb impact forces against acoustical panels.

*************************************************************************************************************
Acoustic batt insulation placed over acoustic suspension ceiling systems may absorb moisture over time and induce loads or collapse ceiling systems.  Use with caution
*************************************************************************************************************

    - [Acoustic Batt Insulation: Specified in Section 07 2100.]

    - [Gypsum Board: Fire rated type; [5/8] [________] inch thick, ends and edges square, paper faced.]

    - Acoustic Sealant For Perimeter Moldings: Specified in Section 07 9200.

***** [OR] *****

    - Gasket for Perimeter Moldings: [Closed cell rubber sponge tape.] [________________.]

*************************************************************************************************************

Touch-up paint is required when field cutting and exposing edges of tegular acoustic units.
*************************************************************************************************************

    - Touch-up Paint: Type and color to match acoustic and grid units.

- EXECUTION

EXAMINATION

Examine substrates, areas, and conditions, including structural framing to which acoustical ceilings attach or abut, with Installer present, for compliance with requirements specified in this and other Sections that affect ceiling installation and anchorage and with requirements for installation tolerances and other conditions affecting performance of acoustical ceilings.

Examine acoustical tiles and/or panels before installation. Reject acoustical materials that are physically damaged, wet, moisture damaged, or mold damaged.

Verify layout of hangers will not interfere with other work.

Proceed with installation only after unsatisfactory conditions have been corrected.

DEMOLITION

*************************************************************************************************************Use this article for demolition work of limited scope. For major or complicated demolition, consider specifying demolition in Section 02 4119 Selective Structure Demolition only.

Carefully coordinate work specified in this article to avoid duplication in other sections. 
*************************************************************************************************************

Extend existing acoustical ceiling installations using materials and methods as specified.

Clean and repair existing acoustical ceilings which remain or are to be reinstalled.

Ceiling tile or panel removal.

Verify with LANL STR that asbestos and radiological surveys have been completed and the results allow free release.

Remove ceiling tiles or panels and separate clean (untreated, unpainted, and uncontaminated with water, adhesives, oils, solvents, mastics, and like products) ceiling tile or panels for recycling. Coordinate potential LANL reuse with LANL STR.

Stack clean ceiling tiles or panels on pallets for handling.

Store clean ceiling tiles or panels off ground and under cover to prevent contamination of materials by water, freezing, foreign matter or other causes.

preparation

Measure each ceiling area and establish layout of acoustical tiles or panels to balance border widths at opposite edges of each ceiling. Avoid using less-than-half-width tiles or panels at borders, and comply with layout shown on reflected ceiling plans.

Layout openings for penetrations centered on the penetrating items.

Installation

General: Install acoustical panel ceilings to comply with ASTM C 636 and manufacturer’s written instructions.

Fire-Rated Assembly: Install fire-rated ceiling systems according to tested fire-rated design.

************************************************************************************************************* Select and edit paras. B and/or C for lay-in or concealed grid.
*************************************************************************************************************

Lay-In Grid Suspension System:

************************************************************************************************************ The following two (2) subparagraphs are required for ceilings that aren’t exempt from seismic.

In the 2nd subpara., retain the 1st option if SDC is D, and retain 2nd option if SDC is C. 
************************************************************************************************************

Install suspension system in accordance with ASTM C 635, ASTM C 636, and as supplemented in this section.

Install suspension system in accordance with ASTM E 580 Section [5] [4].

Install system capable of supporting imposed loads of deflection of [1/360] [1/240] [_________] maximum.

************************************************************************************************************* Include 1st paragraph below when reflected ceiling plan is not included with drawings; or subsequent paragraph when reflected ceiling plan is included.
*************************************************************************************************************

Lay out system to balanced grid design with edge units no less than 50 percent of acoustic unit size. Arrange system with long dimension of panel[parallel] [perpendicular] to long dimension of the space.

***** [OR] *****

Locate system on room axis according to reflected ceiling plan.

Install after major above ceiling work is complete. Coordinate location of hangers with other work.

************************************************************************************************************* Certain metal deck types are fabricated to accommodate ceiling hanger tabs. When tabs are not provided, include following paragraph.
*************************************************************************************************************

Install hanger clips during steel deck erection. Install additional hangers and inserts as required.

Hang suspension system independent of walls, columns, ducts, pipes and conduit. Where carrying members are spliced, avoid visible displacement of face plane of adjacent members.

Where ducts or other equipment prevent regular spacing of hangers, reinforce nearest affected hangers [and related carrying channels] to span extra distance.

Do not support components on main runners or cross runners when weight causes total dead load to exceed deflection capability. [Support fixture loads by supplementary hangers located within [6] [insert number] inches of each corner; or support components independently.]

Do not eccentrically load system, or produce rotation of runners.

Perimeter Molding:

Install edge molding at intersection of ceiling and vertical surfaces [into bed of acoustic sealant] [with continuous gasket].

Use longest practical lengths.

[Miter] [Overlap [and rivet]] corners.

Install at junctions with other interruptions.

Form expansion joints [as detailed] [________]. Form to accommodate plus or minus [1] [insert number] inch movement. Maintain visual closure.

************************************************************************************************************ UL requirements for fire-rated ceilings may necessitate constructing gypsum board boxes over ceiling light fixtures to ensure continuity of fire resistance at suspension system level. Refer to assembly requirements.
*************************************************************************************************************

Install light fixture boxes constructed of [gypsum board] [acoustic panel] above light fixtures in accordance with UL assembly requirements and light fixture ventilation requirements.

***** [OR] ******

Concealed Grid Suspension System:

Install suspension system in accordance with ASTM C 635, ASTM C 636 and as supplemented in this section.

************************************************************************************************************* The following paragraph is required for ceilings that aren’t exempt from seismic.  Retain the 1st option if SDC is D, and retain 2nd option if SDC is C.
*************************************************************************************************************

Install system in accordance with the Contract Drawings and ASTM E 580 Section [5] [4].

Install system capable of supporting imposed loads of deflection of [1/360] [1/240] [________] maximum.

************************************************************************************************************* Include 1st t paragraph below when reflected ceiling plan is not included with drawings; or subsequent paragraph when reflected ceiling plan is included.
*************************************************************************************************************

Lay out system to balanced grid design with edge units no less than 50 percent of acoustic unit size.

***** [OR] ******

Locate system on room axis according to reflected ceiling plan.

Install after major above ceiling work in complete. Coordinate location of hangers with other work.

************************************************************************************************************* Certain metal deck types are fabricated to accommodate ceiling hanger tabs. When tabs are not provided, include following paragraph.
*************************************************************************************************************

Install hanger clips during steel deck erection. Install additional hangers and inserts as required.

Hang suspension system independent of walls, columns, ducts, pipes and conduit. Where carrying members are spliced, avoid visible displacement of face plane of adjacent members.

Where ducts or other equipment prevent regular spacing of hangers, reinforce nearest affected hangers [and related carrying channels] to span extra distance.

Do not support components on main runners or cross runners when weight causes total dead load to exceed deflection capability. Support fixture loads by supplementary hangers located within [6] [________] inches of each corner; or support components independently.

Do not eccentrically load system, or produce rotation of runners.

Perimeter Molding:

Install [concealed] edge molding at intersection of ceiling and vertical surfaces [into bed of acoustic sealant] [with continuous gasket].

Use longest practical lengths.

[Miter] [Overlap [and rivet]] corners.

Install [concealed] at junctions with other interruptions.

Form expansion joints [as detailed] [________]. Form to accommodate plus or minus [1] [insert number] inch movement. Maintain visual closure.]

Acoustic Units:

Fit acoustic units in place, free from damaged edges or other defects detrimental to appearance and function.

Lay directional patterned units [one way with pattern parallel to [longest] [shortest] room axis] [in basket weave pattern]. Fit border trim neatly against abutting surfaces.

Install units after above ceiling work is complete.

Install acoustic units level, in uniform plane, and free from twist, warp, and dents.

Cutting Acoustic Units:

Cut to fit irregular grid and perimeter edge trim.

Cut [square reveal] [bevel] edges to field cut units.

[Double cut and field paint exposed edges of tegular units.]

Where [bullnose concrete block corners] [round obstructions] occur, install preformed closures to match perimeter molding.

************************************************************************************************************* Include the following paragraph when acoustic insulation is required above suspended ceiling system and adjacent to acoustic partitions. Coordinate with partition section. 
*************************************************************************************************************

[Lay acoustic insulation for distance of [48] [<insert number>] inches on both sides of acoustic partitions [as indicated on Drawings].]

************************************************************************************************************* Include the following paragraph for fire rated ceiling assemblies; most UL assemblies require hold-down clips throughout system. This paragraph may be waived when acoustic units are in excess of 1 lb/sq.ft, depending on UL rating.
*************************************************************************************************************

Install hold-down clips to retain panels tight to grid system [within [20] [<insert number>] ft of exterior door] [________].]

erection tolerances

************************************************************************************************************* Retain this article for installation tolerances more restrictive than required by ASTM C 636, which requires ¼” in 10’ for the main runners only. Consult manufacturers before inserting tighter tolerances.
*************************************************************************************************************

Suspended Ceilings: Install main and cross runners level to a tolerance of [1/8 inch in 12 feet] [Insert dimensions], non-cumulative.

Moldings and Trim: Install moldings and trim to substrate and level with ceiling suspension system to a tolerance of [1/8 inch in 12 feet] [Insert dimensions], non-cumulative.

field quality control

*************************************************************************************************************

Retain this Article if ceiling isn’t seismically exempt.   The primary purpose of the Article is to alert the Subcontractor that he/she is responsible for quality control (QC) and that, in addition to QC, the ceiling is subject to the quality assurance (QA) indicated in the Project’s Statement of Special Inspections.
*************************************************************************************************************

Inspection Agency: Engage a qualified inspection agency to perform inspections.

Perform inspections during the installation of suspended ceiling grids as necessary to ensure that the applicable provisions of ASCE 7 are met.

Prepare an inspection report.

Acoustical panel ceiling hangers, braces, anchors and fasteners will be considered defective if they do not pass the Special Inspections indicated in the Project’s Statement of Special Inspections.

cleaning

Clean exposed surfaces of acoustical panel ceilings, including trim, edge moldings, and suspension-system members. Comply with manufacturer’s written instructions for cleaning and touchup of minor finish damage.

Remove and replace ceiling components that cannot be successfully cleaned and repaired to permanently eliminate evidence of damage.

END OF SECTION

****************************************************************

Do not delete the following reference information:

****************************************************************

THE FOLLOWING STATEMENT IS FOR LANL USE ONLY

This project specification section is based on LANL Master Specification Section 09 5100 Rev. 6, dated April 29, 2021.