SECTION 13 3419

METAL BUILDING SYSTEMS

****************************************************************************************************************

This template must be edited for each project.  In doing so, specifier must add job-specific requirements.  Brackets are used in the text to indicate designer choices or locations where text must be supplied by the designer.  Once the choice is made or text supplied, remove the brackets.  The specifications must also be edited to delete specification requirements for processes, items, or designs that are not included in the project -- and specifier’s notes such as these.  To seek a variance from requirements in the specifications that are applicable, contact the Engineering Standards Manual Structural and/or Architectural POCs. Please contact POCs with suggestions for improvement as well.

When assembling a specification package, include applicable specifications from all Divisions, especially Division 1, General requirements.

Specification developed for ML-4 projects.  For ML-1, 2, and 3 applications, additional requirements and independent reviews should be added if increased confidence in procurement or execution is desired; see ESM Chapter 1 Section Z10 Specifications and Quality sections.

This Section includes standard package pre-engineered steel building frame, metal wall, and sloped roof system.  Due to extensive use of profiled steel wall and roof on this building type, this section does not include options for other materials, but can be edited to include them.  Specifications for exterior doors or windows are included.  This section does not include foundations, floor slab, or interior finishing.

This template includes performance, proprietary, and descriptive type specification methods. Edit to avoid conflicting requirements.

As just one example, if the design of the metal building itself is to be performed by a designer/fabricator, then certain notes related to necessary design decisions and documentation must be made requirements for that firm either (e.g., by this spec’s modification or through the statement of work).  An example of a note to make a requirement (from 2.3 PERFORMANCE / DESIGN CRITERIA):

“Verify criteria below.  XXX must be indicated on drawings.  All site features that could influence XXX should be clearly identified in the subcontract documents.”

Structural design of PC-1 and PC-2 buildings must comply with the IBC subject to amendments to it by LANL ESM.  The IBC places the following seismic requirements on steel structures regardless of the value of the Response Modification Coefficient (R) for a seismic-force -resisting system (SFRS):

- Values of R and types of SFRSs are specified in ASCE 7 (i.e., each SFRS has a specific R).

- Structural steel structures assigned to Seismic Design Category D (LANL) shall be designed and detailed in accordance with AISC 341, Part I.

- Light-framed, cold-formed steel walls and diaphragms shall be designed in accordance with AISI-Lateral.  The same requirement applies for resistance to wind loads (Note:  this construction type is allowable but not addressed in this template currently)

While IBC-compliant seismic design is mentioned herein, the EOR is responsible for ensuring that any/all requirements/provisions are specifically addressed during his/her review of the Project-Record-Documents submittals.  Refer to IBC Ch. 22 and LANL Master Spec Sections 05 1000 and 05 4000 for details on seismic-related requirements.

****************************************************************************************************************

GENERAL

SUMMARY

Section includes pre-engineered, shop fabricated structural steel building frame; [insulated] metal wall and sloped roof system including [soffits,] [gutters and downspouts,] [roof mounted equipment curbs,] [and] [________]; and exterior doors [windows,] [skylights,] [overhead doors,] [louvers,] [and] [________].

Related Sections:

****************************************************************************************************************

Retain Sections in subparagraphs below that contain requirements Construction Subcontractor might expect to find in this Section but are specified in other Sections.

****************************************************************************************************************

Section 01 4444 Off-Site Welding and Joining

Section 01 4445 On-Site Welding and Joining

Section 03 3001 Reinforced Concrete

[Section 08 1100 Metal Doors and Frames]

[Section 08 3323 Overhead Coiling Doors]

[Section 08 5113 Aluminum Windows]

[Section 08 7100 Door Hardware]

[Section 08 8000 Glazing]

[Section 08 9100 Louvers]

Section [ __  ____] [Fire Suppression]

Section [ __ ____] [Plumbing Rough-in]

Section [23 2113] [Natural Gas Rough-in]

Section [ __ ____] [Mechanical Rough-in]

Section [ __ ____] [Electrical Rough-in]

Section [27 1000] [Structured Cabling]

Section [27 1500.18] [Protected Transmission System Rough-In]

Section [27 3000] [Voice Communication Rough-In]

Section [28 0528] [Pathway for Electronic Security]

Section [28 1321] [Administrative Access Control System Rough-In]

Section [28 3100] [Fire Alarm Detection and Alarm Rough-In]

REFERENCES

**************************************************************************************************************

List reference standards included within text of this section.  Edit the following for Project conditions.

**************************************************************************************************************

American Architectural Manufacturers Association

- AAMA 621 – Voluntary Specifications for High Performance Organic Coatings on Coil Coated Architectural Hot Dipped Galvanized (HDG) and Zinc-Aluminum Coated Steel Substrates.

- AAMA 701/702 - Combined Voluntary Specifications for Pile Weatherstripping and Replaceable Fenestration Weatherseals.

American Architectural Manufacturers Association/Window & Door Manufacturers Association/Canadian Standards Association

AAMA/WDMA/CSA 101/I.S.2/A440 – Standard/Specification for Windows, Doors, and Unit Skylights.

American Institute of Steel Construction

AISC 360 - Specification for Structural Steel Buildings.

AISC 341 – Seismic Provisions for Structural Steel Buildings.

American Society of Civil Engineers

ASCE 7 – Minimum Design Loads for Buildings and Other Structures.

ASTM International

ASTM A36 - Standard Specification for Carbon Structural Steel.

ASTM A123 - Standard Specification for Zinc (Hot-Dip Galvanized) Coatings on Iron and Steel Products.

ASTM A153 - Standard Specification for Zinc Coating (Hot-Dip) on Iron and Steel Hardware.

ASTM A307 - Standard Specification for Carbon Steel Bolts and Studs, 60 000 PSI Tensile Strength.

ASTM A325 - Standard Specification for Structural Bolts, Steel, Heat Treated, 120/105 ksi Minimum Tensile Strength.

ASTM A475 - Standard Specification for Zinc-Coated Steel Wire Strand.

ASTM A490 - Standard Specification for Heat-Treated Steel Structural Bolts, 150 ksi Minimum Tensile Strength.

ASTM A500 - Standard Specification for Cold-Formed Welded and Seamless Carbon Steel Structural Tubing in Rounds and Shapes.

ASTM A529 - Standard Specification for High-Strength Carbon-Manganese Steel of Structural Quality.

ASTM A563 – Standard Specification for Carbon and Alloy Steel Nuts.

ASTM A572 - Standard Specification for High-Strength Low-Alloy Columbium-Vanadium Structural Steel.

ASTM A653 - Standard Specification for Steel Sheet, Zinc-Coated (Galvanized) or Zinc-Iron Alloy-Coated (Galvannealed) by the Hot-Dip Process.

ASTM A755 – Standard Specification for Steel Sheet, Metallic Coated by the Hot-Dip Process and Prepainted by the Coil-Coating Process for Exterior Exposed Building Products.

ASTM A780 – Standard Practice for Repair of Damaged and Uncoated Areas of Hot-Dip Galvanized Coatings.

ASTM A792 - Standard Specification for Steel Sheet, 55% Aluminum-Zinc Alloy-Coated by the Hot-Dip Process.

ASTM A1008 – Standard Specification for Steel, Sheet, Cold-Rolled, Carbon, Structural, High-Strength Low-Alloy and High-Strength Low-Alloy with Improved Formability, Solution Hardened, and Bake Hardenable.

ASTM A1011 – Standard Specification for Steel, Sheet and Strip, Hot-Rolled, Carbon, Structural, High Strength, Low-Alloy and High-Strength Low Alloy with Improved Formability, and Ultra-High Strength.

ASTM B221 – Standard Specification for Aluminum and Aluminum-Alloy Extruded Bars, Rods, Wire, Profiles, and Tubes.

ASTM B695 – Standard Specification for Coatings of Zinc Mechanically Deposited on Iron and Steel.

ASTM C273 – Standard Test Method for Shear Properties of Sandwich Core Materials.

ASTM C297 – Standard Test Method for Flatwise Tensile Strength of Sandwich Constructions.

ASTM C423 – Standard Test Method for Sound Absorption and Sound Absorption Coefficients by the Reverberation Room Method.

ASTM C665 - Standard Specification for Mineral-Fiber Blanket Thermal Insulation for Light Frame Construction and Manufactured Housing.

ASTM C991 - Standard Specification for Flexible Glass Fiber Insulation for Pre-Engineered Metal Buildings.

ASTM C1036 – Standard Specification for Flat Glass.

ASTM C1048 – Standard Specification for Heat-Treated Flat Glass - Kind HS, Kind FT Coated and Uncoated Glass.

ASTM C1107 - Standard Specification for Packaged Dry, Hydraulic-Cement Grout (Nonshrink).

ASTM C1136 – Standard Specification for Flexible, Low Permeance Vapor Retarders for Thermal Insulation.

ASTM C1289 – Standard Specification for Faced Rigid Cellular Polyisocyanurate Thermal Insulation Board.

ASTM D1494 – Standard Test Method for Diffuse Light Transmission Factor of Reinforced Plastics Panels.

ASTM D1621 – Standard Test Method for Compressive Properties of Rigid Cellular Plastics.

ASTM D 1622 - Standard Test Method for Apparent Density of Rigid Cellular Plastics.

ASTM D 2126 - Standard Test Method for Response of Rigid Cellular Plastics to Thermal and Humid Aging.

ASTM D 2244 - Standard Test Method for Calculation of Color Tolerances and Color Differences from Instrumentally Measured Color Coordinates.

ASTM D 3656 - Standard Specification for Insect Screening and Louver Cloth Woven from Vinyl-Coated Glass Yarns.

ASTM D 3841 - Standard Specification for Glass-Fiber-Reinforced Polyester Plastic Panels.

ASTM D 4214 - Standard Test Methods for Evaluating the Degree of Chalking of Exterior Paint Films.

ASTM D 6226 - Standard Test Method for Open-Cell Content of Rigid Cellular Plastics.

ASTM E84 - Standard Test Method for Surface Burning Characteristics of Building Materials.

ASTM E94 – Standard Guide for Radiographic Examination.

ASTM E96 - Standard Test Methods for Water Vapor Transmission of Materials.

ASTM E108 - Standard Test Methods for Fire Tests of Roof Coverings.

ASTM E 119 - Standard Test Methods for Fire Tests of Building Construction and Materials.

ASTM E 136 - Standard Test Method for Behavior of Materials in a Vertical Tube Furnace at 750°C.

ASTM E 164 - Standard Practice for Ultrasonic Contact Examination of Weldments.

ASTM E 165 - Standard Test Method for Liquid Penetrant Examination.

ASTM E 283 - Standard Test Method for Determining Rate of Air Leakage through Exterior Windows, Curtain Walls, and Doors under Specified Pressure Differences across the Specimen.

ASTM E 329 - Standard Specification for Agencies Engaged in Construction Inspection and/or Testing.

ASTM E 331 - Standard Test Method for Water Penetration of Exterior Windows, Skylights, Doors, and Curtain Walls by Uniform Static Air Pressure Difference.

ASTM E709 – Standard Guide for Magnetic Particle Examination.

ASTM E1646 – Standard Test Method for Water Penetration of Exterior Metal Roof Panel Systems by Uniform Static Air Pressure Difference.

ASTM E1680 – Standard Test Method for Rate of Air Leakage through Exterior Metal Roof Panel Systems.

ASTM E1980 - Standard Practice for Calculating Solar Reflectance Index of Horizontal and Low-Sloped Opaque Surfaces.

ASTM E2190 – Standard Specification for Insulating Glass Unit Performance and Evaluation.

ASTM F436 – Standard Specification for Hardened Steel Washers.

ASTM F844 – Standard Specification for Washers, Steel, Plain (Flat), Unhardened for General Use.

ASTM F1554 – Standard Specification for Anchor Bolts, Steel, 36, 55, and 105-ksi Yield Strength.

ASTM F 1852 – Standard Specification for "Twist Off" Type Tension Control Structural Bolt/Nut/Washer Assemblies, Steel, Heat Treated, 120/105 ksi Minimum Tensile Strength.

American Welding Society

AWS A2.4 - Standard Symbols for Welding, Brazing, and Nondestructive Examination.

AWS D1.1 - Structural Welding Code - Steel.

Code of Federal Regulations

16 CFR 201 - Safety Standard for Architectural Glazing Materials.

International Accreditation Service

IAS AC472 – Accreditation Criteria for Inspection Programs for Manufacturers of Metal Building Systems.

International Code Council

IBC – International Building Code.

Federal Specification

FS RR-W-365 - Wire Fabric (Insect Screening).

Green Seal

GS-11 - Paints and Coatings.

Los Alamos National Laboratory

LANL ESM – Engineering Standards Manual.

Metal Building Manufacturers Association

MBMA - Metal Building System Manual.

North American Insulation Manufacturers Association

NAIMA 202 - Standard for Flexible Fiber Glass Insulation to Be Laminated for Use in Metal Buildings.

National Fire Protection Association

NFPA 80 - Fire Doors and Fire Windows.

NFPA 252 – Fire Tests for Door Assemblies.

Research Council on Structural Connections

RCSC - Specification for Structural Joints Using ASTM A 325 or A 490 Bolts.

Steel Door Institute

SDI A250.3 - Test Procedure and Acceptance Criteria for Factory Applied Finish Painted Steel Surfaces for Steel Doors and Frames (ANSI).

SDI A250.8 - Recommended Specifications for Standard Steel Doors and Frames (ANSI).

SDI A250.10 - Test Procedure and Acceptance Criteria for Prime Painted Steel Surfaces for Steel Doors and Frames (ANSI).

Steel Joist Institute

SJI - Standard Specifications and Load Tables for Steel Joists and Joist Girders.

The Society for Protective Coatings

SSPC Paint 15 - Paint Specification No. 15: Steel Joist Shop Primer.

SSPC SP-2 – Surface Preparation Specification No. 2:  Hand Tool Cleaning.

SSPC SP-3 – Surface Preparation Specification No. 3:  Power Tool Cleaning.

Underwriters Laboratories Inc.

UL 10C - Standard for Positive Pressure Fire Tests of Door Assemblies.

UL 580 - Tests for Uplift Resistance of Roof Assemblies.

U.S. Environmental Protection Agency

ENERGY STAR - ENERGY STAR Voluntary Labeling Program.

ADMINISTRATIVE REQUIREMENTS

****************************************************************************************************************Retain article below if Work of this Section is extensive or complex enough to justify a pre-installation meeting.
****************************************************************************************************************

- Pre-Installation Meeting

  - Convene minimum [one] [_______] week prior to commencing work of this Section at [Project site] [_______].

****************************************************************************************************************Retain subparagraphs below if additional requirements are necessary; include information about meeting.
****************************************************************************************************************

  - Review methods and procedures related to Metal Building Systems including, but not limited to, the following:

    - Condition of foundations and other preparatory work performed by other trades.

    - Structural load limitations.

    - Construction schedule.  Verify availability of materials and erector’s personnel, equipment, and facilities needed to make progress and avoid delays.

****************************************************************************************************************Coordinate first subparagraph below with Section 01 4000, Quality Requirements, and with “Source Quality Control” and “Field Quality Control” articles in this Section.  Insert requirements to suit Project.
****************************************************************************************************************

    - Required tests, inspections, and certifications.

    - Unfavorable weather and forecasted weather conditions.

    - Welding and inspection.

  - Review methods and procedures related to metal roof panel assemblies including, but not limited to the following:

    - Compliance with requirements for purlin and rafter conditions, including flatness and attachment to structural members.

    - Structural limitations of purlins and rafters during and after roofing.

    - Flashings, special roof details, roof drainage, roof penetrations, equipment curbs, and condition of other construction that will affect metal roof panels.

    - Temporary protection requirements for metal roof panel assembly during and after installation.

    - Roof observation and repair after metal roof panel installation.

  - Review methods and procedures related to metal wall panel assemblies including, but not limited to the following:

    - Compliance with requirements for support conditions, including alignment between and attachment to structural members.

    - Structural limitations of girts and columns during and after wall panel installation.

    - Flashings, special siding details, wall penetrations, openings, and condition of other construction that will affect metal wall panels.

    - Temporary protection requirements for metal wall panel assembly during and after installation.

    - Wall observation and repair after metal wall panel installation.

ACTION SUBMITTALS/INFORMATIONAL SUBMITTALS

***************************************************************************************************************Only request submittals needed to verify compliance with Project requirements.  Delegated design documents must be in accordance with the LANL Engineering Standards Manual, Chapter 5, Section I (e.g., paragraph 1.6 requirements on format, content, signature/sealing, etc.).
****************************************************************************************************************

- Product Data:  For each type of Metal Building System component. Include construction details, material descriptions, dimensions of individual components and profiles, and finished for the following:

  - Structural wall panels.

  - Metal roof panels.

  - Metal wall panels.

  - Metal liner panels.

  - Translucent panels.

- Shop Drawings

  - Shop or Erection Drawings:  Indicate assembly dimensions, locations of structural members, connections, attachments, openings, cambers, loads [and] [_______]; wall and roof system dimensions, panel layout, general construction details, anchorages and method of anchorage installation [and] [_______], and include details of edge conditions, joints, panel profiles, corners, trim, flashings, closures and special details, distinguishing between factory-and field assembled work; framing anchor bolt settings, sizes, and locations from datum, [and foundation loads]; indicate welded connections with AWS A2.4 welding symbols, distinguishing between shop and field applications; indicate net weld lengths.

    - Show provisions for attaching [roof curbs] [service walkways] [platforms] [and] [pipe racks].

***************************************************************************************************************Metal building manufacturers layout drawings often do not include the items in first subparagraph below.  Retain if contractor must insert this information.
***************************************************************************************************************

    - Show roof –mounted items including roof hatches, equipment supports, pipe supports and penetrations, lighting fixtures, and items mounted on roof curbs.

    - Show wall-mounted items including doors, windows, louvers, and lighting fixtures.

    - Show translucent panels.

****************************************************************************************************************Retain subparagraph below for large-scale details if product data from manufacturer are inadequate. Retain specific scale if required.
****************************************************************************************************************

  - Accessory Drawings: Include details of the following items, at a scale of not less than [1-1/2 inches per 12 inches (1:8)] [_________].

    - Flashing and Trim

    - Gutters

    - Downspouts

    - Roof ventilators

    - Louvers

    - Service walkways

  - Door Schedule:  For doors and frames. Use same designations indicated on Drawings. Include details of reinforcement.

- Samples

**************************************************************************************************************** Include the first and/or the second paragraph below for submission of physical samples for selection of finish, color, texture, and other properties. Delete “Samples for Initial Selection” Paragraph if colors and other characteristics are preselected and specified or scheduled. Regardless of this decision, retain “Samples for Verification” Paragraph.
****************************************************************************************************************

  - Samples for Initial Selection: For units with factory-applied color finish.

  - Samples for Verification: For each type of exposed finish required, prepared on samples of sizes indicated thusly:

    - Metal Panels: Nominal 12 inches long x actual panel width. Include fasteners, closures, and other exposed panel accessories.

    - Translucent Panels: Nominal 12 inches long x actual panel width.

    - Flashing and Trim: Nominal 12 inches long. Include fasteners and other exposed accessories.

    - Vapor-Retarder Facings: Nominal 6-inch square samples.

    - Windows: Full-size, nominal 12-inch-long frame samples showing typical profile.

    - Accessories: Nominal 12-inch-long samples for each type of accessory.

- Certificates

**************************************************************************************************************** Retain the following paragraph if retaining “Erector” paragraph in “Qualifications” Article.
****************************************************************************************************************

  - Erector Certificates: For each project, from manufacturer.

**************************************************************************************************************** Retain the following paragraph if retaining “Manufacturer” paragraph in “Qualifications” Article.
****************************************************************************************************************

  - Manufacturer Certificates: For each product, from manufacturer.

- Delegated Design Submittals

  - Structural Design Basis Document.

    - In addition to content required by LANL ESM, include the following:

      - Order Number

      - Name of Manufacturer

      - Name of Subcontractor

      - IAS Accreditation (AC472)

        - Include a statement that Metal Building System and components were designed and produced in an IAS-Accredited Facility by an IAS-Accredited Manufacturer.

  - Structural-design calculations for the Metal Building, and for the seismic design of the nonstructural components within / on it.

  - Statement of Structural Tests and Special Inspections (i.e., Test and Inspection Plan per LANL ESM Chapter 16).

  - Anchor bolt placement plan, column reactions [,and] [______] in advance of erection drawings.

- Test and Evaluation Reports

****************************************************************************************************************Retain the following paragraph for material test reports that are Subcontractor’s responsibility.
****************************************************************************************************************

  - Material Test Reports:

    - Structural steel including chemical and physical properties.

    - Bolts, nuts, and washers including mechanical properties and chemical analysis.

    - Tension-control, high strength, bolt-nut-washer assemblies.

    - Shop primers.

    - Nonshrink grout.

  - Product Test Reports:  Based on evaluation of comprehensive tests performed by manufacturer and witnessed by a qualified testing agency, for insulation and vapor-retarder facings.  Include reports for thermal resistance, fire-test-response characteristics, water-vapor transmission, and water absorption.

  - Source Quality-Control Reports.

****************************************************************************************************************Retain the following paragraph if testing is required by article “Source Quality Control” in Part 2, and / or article “Field Quality Control” in Part 3.
****************************************************************************************************************

  - Field Quality-Control Reports.

****************************************************************************************************************When Manufacturer’s instructions for specific installation requirements are referenced in Part 3, include the paragraph below. Edit Part 3 statements to avoid conflict with Manufacturer’s instructions.
****************************************************************************************************************

- Manufacturer’s Installation Instructions:  Indicate preparation requirements, assembly sequence [and] [_________].

- Special Procedure Submittals

****************************************************************************************************************Retain the following paragraph if survey is required.
****************************************************************************************************************

  - Surveys: Show final elevations and locations of major members.  Indicate discrepancies between actual installation and the Subcontract Documents.  Have surveyor who performed surveys certify their accuracy.

****************************************************************************************************************Coordinate the following paragraph with qualification requirements in Section 01 4000, Quality Requirements, and as supplemented in “Quality Assurance” Article.
****************************************************************************************************************

- Qualification Data:  For qualified [erector] [manufacturer] [professional engineer] [land surveyor] [testing agency].

SUSTAINABLE DESIGN SUBMITTALS

Manufacturer’s Certificate:  Certify products meet or exceed specified sustainable design requirements.

Sustainable Sites Certificates:

Certify roofing materials solar reflectance index.

Materials Resources Certificates:

Certify recycled material content for recycled content products.

Certify source for local and regional materials and distance from Project site.

Indoor Air Quality Certificates:

Certify volatile organic compound content for each interior paint and coating.

Product Cost Data: Submit cost of products to verify compliance with Project sustainable design requirements.  Exclude cost of labor and equipment to install products.

Provide cost data for the following products:

****************************************************************************************************************Edit list of material cost data to suit products specified in this section and Project sustainable design requirements.  Specific cost data requirements are specified in ESM Chapter 14.
****************************************************************************************************************

- Products with recycled material content.

- Local and regional products.

- [ __________________ ].

CLOSEOUT SUBMITTALS

Maintenance Data:  for metal panel finishes, to include in maintenance manuals.

Warranties:  Normal and special warranties.

Section 01 7839 Project Record Documents: Record actual locations of concealed components and utilities.

QUALITY ASSURANCE

Qualifications

Manufacturer: The company manufacturing the products specified in this Section shall have a minimum of [5] [3] [__] year[s] documented experience in the manufacture of Metal Building Systems.

IAS Accreditation: The manufacturing company shall be accredited under IAS AC472 and shall produce the Metal Building System and components in an IAS-Accredited Facility.

****************************************************************************************************************Edit Section 01 7839, Project Record Documents, as necessary to ensure that its content is consistent with requirements contained herein (i.e., paragraphs 1.6 and 1.10.B).
****************************************************************************************************************

Structural Engineer: Design structural components, and seismic restraint for nonstructural components; develop Project Record Documents (reference article “Delegated Design Submittals,” which consists of documents that must be in accordance with LANL ESM Chapter 5, Section I (e.g., paragraph 1.6); and perform shop and site work under direct supervision of Professional Engineer experienced in design of this work and licensed in State of NM.

Erector: Erector shall have specialized experience in the erection of Metal Building Systems for a period of at least [5] [___] years [documented] experience] [approved by manufacturer.]

****************************************************************************************************************Qualification requirements in paragraph below are in addition to those specified in Section 01 4000, Quality Requirements.
****************************************************************************************************************

Testing Agency: Qualified according to ASTM E 329 for testing indicated.

****************************************************************************************************************Include the following article for projects adjacent to, or involving additions to, existing structures.
****************************************************************************************************************

Mockups: Build mockups to verify selections made under sample submittals and to demonstrate aesthetic effects and set quality standards for materials and execution.

***************************************************************************************************************Retain first subparagraph below for large-scale mockup. Indicate portion of wall represented by mockup on Drawings or draw mockup as separate element.
***************************************************************************************************************

Build mockup of typical wall area as shown on Drawings.

****************************************************************************************************************
Retain first subparagraph below for limited mockups.
****************************************************************************************************************

Build mockups for typical wall metal panel including accessories.

Size: [48 inches] [______] long x [48 inches] [______] wide.

****************************************************************************************************************
Retain subparagraph below if mockups are not only for establishing appearance factors.
****************************************************************************************************************

Approval of mockups does not constitute approval of deviations from the Subcontract Documents contained in mockups unless LANL STR specifically approves such deviations in writing.

DELIVERY, STORAGE, AND HANDLING

Deliver to project site in manufacturer’s unopened containers or bundles, fully identified with name, brand, type and grade.  Store off the ground in a dry ventilated space or protect with impervious covering.  Protect from rusting and damage.

warranty

***************************************************************************************************************
This article contains extended warranties, which increase construction costs and Owner-enforcement responsibilities. Specify warranties with caution.
***************************************************************************************************************

Special Warranty on Metal Panel Finishes:  Manufacturer’s standard from in which manufacturer agrees to repair finish or replace metal panels that show evidence of deterioration of factory-applied finishes within specified warranty period.

Exposed Panel Finish:  Deterioration includes, but is not limited to, the following:

Color fading more than 5 Hunter units when tested according to ASTM D 2244.

Chalking in excess of a No. 8 rating when tested according to ASTM D 4214.

Cracking, checking, peeling, or failure of paint to adhere to bare metal.

***************************************************************************************************************
Verify available warranties and warranty periods for units and components with manufacturers listed in Part 2. 20-year period is common for fluoropolymer finish; 25- and 30-year periods are available from some manufacturers. 10-year period is usually available for siliconized polyester.
***************************************************************************************************************

Finish Warranty Period: [20] [10] [__] years from date of Substantial Completion.

Special Weathertightness Warranty for Standing-Seam Metal Roof Panels:  Metal Building subcontractor agrees to repair or replace standing-seam metal roof panel assemblies that leak or otherwise fail to remain weathertight within specified warranty period.

**************************************************************************************************************
Verify available warranties and warranty periods for units and components with manufacturers listed in Part 2. 
**************************************************************************************************************

Warranty Period: [20] [10] [5] [__] years from date of Substantial Completion.

PRODUCTS

MANUFACTURERS

****************************************************************************************************************

In this article, list manufacturers acceptable for this Project.

****************************************************************************************************************

Manufacturers List:

[Butler Manufacturing Co.] Model [__________].

[Ceco Building Systems]  Model [__________].

[Star Building Systems, Inc.] Model [__________].

[Whirlwind Building Systems] Model [__________].

[___________________________] Model [__________].

****************************************************************************************************************

Click here to find manufacturers making products specified in this section.

****************************************************************************************************************

DESCRIPTION

System Description

****************************************************************************************************************
Use this article carefully; restrict statements to describe components used to assemble system.  Do not repeat statements made in SUMMARY Article, “Section Includes” Paragraph.
****************************************************************************************************************

[Single-span moment frame.] [Tapered beam.] [Continuous beam frame.] [Truss frame.] [Lean-to] [_______________.]

[________ minimum clearance at knee.] [_______ minimum clearance haunch to haunch.] [______ inch depth straight exterior columns]  [________ critical dimension at ______]

****************************************************************************************************************
Include the following paragraph when Drawings do not indicate bay spacing.
****************************************************************************************************************

Bay Spacing: [_________] ft.

Primary Framing:  Moment frame of rafter beams and columns, [canopy beams,] [intermediate columns,] [braced end frames,] [end wall columns,] [_________________,] and lateral-load bracing.

Secondary Framing: [Purlins,] [girts,] [eave struts,] [flange bracing,] [sill supports,] [_______________,] clips, and other items detailed.

****************************************************************************************************************
When making choices in the following paragraph, keep in mind that horizontal diaphragms in metal building systems tend to differ from those used in conventional buildings.  Per the MBMA Manual, “Horizontal diaphragm systems in metal buildings might consist of either the metal cladding of the roof itself or horizontal bracing systems beneath the roof alone.  Examples of horizontal bracing systems used include rods, angles, cables, or other structural members and are often tension-only bracing.”

The preceding also needs to be kept in mind when editing paragraph 2.4.E (Structural Steel Framing, Bracing).
**************************************************************************************************************

Lateral Bracing: Horizontal loads not resisted by main frame action shall be resisted by [cable] [rod] and/or [diaphragm] [portal frames] [fixed-base columns] [    ] in the sidewall. [Diaphragm] and/or [cable] [rod] [portal frame] [fixed-base columns] [    ] in the endwall. [Cable] [rod] and/or [diaphragm] [    ] in the roof.

Wall System: Preformed metal panels of [horizontal] [vertical] [_______] profile, [with subo-girt framing/anchorage assembly,] [insulation] [liner sheets,] and accessory components.

Roof System: Preformed metal panels of [upslope] [parallel to eave] [______] profile, [with sub-girt framing/anchorage assembly,] [insulation,] [linear sheets,] and accessory components.

****************************************************************************************************************
Include the following paragraph when Drawings do not indicate roof slope.
****************************************************************************************************************

Roof Slope: [1/8] [1] [2] [4] [____] inches in 12 inches.

Accessories: [Ventilators], [louvers], [windows], [doors], [hardware], [     ].

Sustainability Characteristics

******************************************************************************************************
Edit sustainable design requirements to suit content of this section and Project sustainable design requirements specified in ESM Chapter 14.
******************************************************************************************************

Steel

Post Consumer Content: 16 percent (Basic Oxygen Furnace (BOF), 67 percent (Electric Arc Furnace (EAF)).

Total Recovered Materials:  25-30 percent (BOF), 100 percent (EAF).

Aluminum

Post Consumer Content: 25-95 percent

Total Recovered Materials: 20-95 percent.

Metallic-Coated Steel Sheet: Provide steel sheet with average recycled content such that postconsumer recycled content plus on-half of preconsumer recycled content is not less than 25 percent.

Rubber

Post Consumer Content: 12-100 percent

Total Recovered Materials: 100 percent

Plastic or Plastic/Rubber Composite

Post Consumer Content: 100 percent.

Total Recovered Materials Content: 100 percent.

Energy Performance: Provide roof panels with Solar Reflectance Index not less than [78] [29] when calculated according to ASTM E 1980 based on testing identical products by a qualified testing agency.

**************************************************************************************************************
Retain first paragraph below for roofs that must comply with ENERGY STAR requirements.  ENERGY STAR Roof products Qualified Product List is available at www.energystar.gov.  First option below is for roofs with slopes of 2:12 or less; second option is for roofs with slopes steeper than 2:12.
**************************************************************************************************************

Energy Performance: Provide roof panels that are listed on the DOE’s ENERGY STAR Roof Products Qualified Product List for [low] [steep]-slope roof products.

***************************************************************************************************************
Usually retain the following paragraph for roofs that must comply with CEC-Title 24 or equivalent.  Options are values required for low-slope roofs by prescriptive approach; insert other values if required for building-envelope trade-off approach or for whole building performance approach. Low-slope roofs are those with slopes of 2:12 or less.  A list of products tested according to CRRC, with their test values, is available at www.coolroofs.org. 
***************************************************************************************************************

Energy Performance: Provide roof panels with initial solar reflectance not less than [0.70] [____] and emissivity not less than [0.75] [____] when tested according to Cool Roof Rating Council.

Maintain [one copy] [[_______] copies] of [each] document on site.

PERFORMANCE / DESIGN CRITERIA

Design Requirements

  - Perform work in accordance with the applicable steel specification per IBC Chapter 22 (e.g., AISC 360 and 341 for structural steel, etc.).

Fabrication of structural members shall be in accordance with MBMA, and for items not covered therein, AISC 360.

****************************************************************************************************************

Use this article carefully; restrict statements to identify system design requirements only.  Refer to Part 2 for specification of insulation thickness.

****************************************************************************************************************

The Metal Building shall be designed by the Manufacturer as a complete system.

Thermal resistance of [Calculated] [Installed] Wall System: R-Value of [________].

Thermal Resistance of [Calculated] [Installed] Roof System: R-Value of [________].

Design Code:  Design shall be in accordance with the LANL Engineering Standards Manual.

****************************************************************************************************************

LANL ESM Chapter 5, Section II, does not contain dead-load requirements that would apply to one-story Metal Building Systems.  For projects involving something other than ‘1 story,’ consult this document for “Future floor dead load.”

**************************************************************************************************************

Dead Loads:   The dead load shall be the weight of the Metal Building System and as determined by the system manufacturer.

****************************************************************************************************************

Collateral loads consist of fire-suppression systems; and architectural, mechanical and electrical components / systems.

****************************************************************************************************************

Collateral Loads:  The collateral load shall be [         psf]  [as shown on the drawings].  Collateral loads shall not be applied to the roof panels.

****************************************************************************************************************

The default live load is from LANL ESM Chapter 5, Section II:  It is the minimum roof live load for buildings, which would be the live-load requirement for a one-story Metal Building System.  For projects involving something other than ‘1 story,’ change paragraph below to Roof Live Load and add a new paragraph for Live Loads.

****************************************************************************************************************

Live Loads:  The Metal Building System shall be capable of supporting a minimum uniform live load of [30 psf, non-reducible.] [        psf.]

****************************************************************************************************************

The ground snow load is from LANL ESM Chapter 5, Section II.  Consult same for additional factors related to determining snow loads required for design (e.g., Exposure Factor, CC; Thermal Factor, CT; Importance Factor, I; etc.), which must be indicated on the drawings.  All sources of snow drifting should be clearly identified in the subcontract documents (e.g., adjacent structures, site features, roof height changes, etc.).

****************************************************************************************************************

Snow Loads:  The design ground snow load shall be 16 psf.

****************************************************************************************************************

The design wind speed and Exposure Category are from LANL ESM Chapter 5, Section II.  Consult same for additional factors related to determining wind loads required for design (e.g., Topographic Effects Factor, Kzt; Importance Factor, I; etc.), which must be indicated on the drawings.  All site features that could influence the design wind loads should be clearly identified in the subcontract documents (e.g., isolated hills, ridges, escarpments, etc.).

****************************************************************************************************************

Wind Loads:  The design wind speed shall be 90 mph, 3-second gust, and the Exposure Category shall be Exposure C.

****************************************************************************************************************

The seismic design category and spectral-response-acceleration factors are from LANL ESM Chapter 5, Section II.  Consult same for additional information related to determining seismic loads required for building design (e.g., period values for response spectrum, T0; Response Modification Factor, R; Importance Factor, I; etc.), which must be indicated on the drawings.

****************************************************************************************************************

Metal Building Seismic Loads:  Seismic loads acting on the Metal Building shall be determined based upon Seismic Design Category D; and design spectral-response-acceleration factors, SDS and SD1, of 0.75 and 0.64 g, respectively.

****************************************************************************************************************

The seismic design category and spectral-response-acceleration factor are from LANL ESM Chapter 5, Section II.  Consult same for additional information related to determining seismic loads required for design of nonstructural components within / on the building (e.g., Amplification Factor, ap; Response Modification Factor, Rp; Importance Factor, I; etc.), which must be indicated on the drawings.  The heights of all components should be clearly indicated in the subcontract documents.

By reference to IBC and ASCE 7, LANL ESM Chapter 5, Section II requires some nonstructural components to be designed as nonbuilding structures.  For projects involving such, edit below accordingly, and provide all information required to perform the design(s) in the subcontract documents.

****************************************************************************************************************

Nonstructural Component Seismic Loads:  Seismic loads acting on the nonstructural components within / on the Metal Building shall be determined based upon Seismic Design Category D; and design spectral-response-acceleration factor, SDS, of 0.75.

****************************************************************************************************************

The rainfall intensities 5-year recurrence interval for five-minute duration and 25-year recurrence interval for five-minute duration, respectively are from MBMA’s Metal Building Systems Manual for Los Alamos County (ref. Section IX).

****************************************************************************************************************

Rainfall Intensity:  All exterior gutters and downspouts shall be designed for 4-inches per hour.  All interior gutters, valleys and downspouts shall be designed for 6-inches per hour.

Provide drainage to exterior for water entering or condensation occurring within wall or roof system.

****************************************************************************************************************

L is the span of the element between support points, and H is the eave height of the building.  For 10-year wind values, use 75% of the 50-year wind pressure.  The 50-year wind pressure is the load (in psf) acting on the building as a result of the paragraph called “Wind Loads.”

****************************************************************************************************************

Deflections shall be limited as follows:

Primary framing:

L/[180] [____] for roof snow load, but not less than 30 psf.

H/[60] [____] for 10-year wind load.

Secondary framing

L/ [150] [____] for roof dead load + roof snow load (but not less than 30 psf); but not less than that required to maintain positive drainage for dead load + ½ roof snow load (but not less than 30 psf).

L/[120] [         ] for 10-year wind load on walls and roof.

L/[180] [         ] for roof snow load (but not less than 30 psf) on sheeting.

Thermal Effects:  Standing Seam roof panels shall be free to move in response to the expansion and contraction forces resulting from a temperature variation.  Assembly to permit movement of components without buckling, failure of joint seals, undue stress on fasteners or other detrimental effects, when subject to temperature range of [________] degrees F.

Size and fabricate wall and roof systems free of distortion or defects detrimental to appearance or performance.

****************************************************************************************************************

Include all dimensions /details necessary for design to account for all applicable site conditions.  Only adjacent structures are currently accounted for in the following paragraph; therefore, if site features such as isolated hills, ridges, escarpments, etc. are applicable (per the paragraph called “Wind Loads”) then the following paragraph must be modified accordingly.

****************************************************************************************************************

Site Conditions:  The following site features and adjacent structures must be considered in the design.

Metal Building is [     ] feet away from a [        ] wide x [        ] long x [        ] high adjacent building, as shown on the drawings.

[                                                       .]

PERFORMANCE REQUIREMENTS

Conform to the LANL Engineering Standards Manual for preparation and/or submission of design calculations, reviewed shop and erection drawings, and documentation / reports related to inspections, tests, and quality assurance as required for acquiring Certificate of Occupancy.

All components of the system shall be supplied or specified by the same manufacturer, and components of each type shall be compatible with adjacent materials.

****************************************************************************************************************

ASTM E96 permits testing using desiccant and water methods. Samples may be tested with one surface wetted when using water method. Samples may be tested with low humidity on one side and high humidity on opposite side. Single material tested using various conditions will produce different test results.

Select test method and service conditions when necessary to suit application.

****************************************************************************************************************

Vapor Retarder Permeance: Maximum [1 perm] [[________] perms] when tested in accordance with ASTM E 96, [desiccant method] [water method].

****************************************************************************************************************

Per IBC Ch. 15 and ESM Ch. 4, some roof decks and roof coverings must be designed to withstand ‘structural’ wind loads (i.e., ) and meet certain uplift resistance ratings (i.e., the following paragraph).

Based on the standard / code requirements, and the specifics of the Project, edit the paragraph below as necessary.  If the UL rating applies, verify that products are listed in UL's "Roofing Materials and Systems Directory."  Do likewise for ratings by other organizations.

Delete the following paragraph if uplift resistance ratings are not applicable to the Project.

****************************************************************************************************************

Wind Uplift Resistance for Roof Assemblies:  Provide metal roof panel assemblies that comply with [UL 580, Uplift Class 90.] [_________.]

****************************************************************************************************************

Pressure differences in first two paragraphs below are examples only.  Revise to suit Project.  Value shown for test-pressure difference for metal roof panels is for roofs with slope less than or equal to 30 degrees.

****************************************************************************************************************

Air Infiltration for Metal Roof Panels:  Air leakage through assembly of not more than [0.06 cfm/sq. ft.] [______] of roof area when tested according to ASTM E 1680 at negative test-pressure difference of [1.57 lbf/sq. ft.] [______].

****************************************************************************************************************

Value in the following paragraph below is ASTM E 283 default; revise to suit Project.

****************************************************************************************************************

Air Infiltration for Metal Wall Panels:  Air leakage through assembly of not more than [0.06 cfm/sq. ft.] [________] of wall area when tested according to ASTM E 283 at static-air-pressure difference of [1.57 lbf/sq. ft.] [_______].

****************************************************************************************************************

Pressure differences in first two paragraphs below are examples only.  Revise to suit Project.  Value shown for test-pressure difference for metal roof panels is for roofs with slope less than or equal to 30 degrees.  Locations where high winds and heavy rains frequently occur simultaneously require higher test pressures.

****************************************************************************************************************

Water Penetration for Metal Roof Panels:  No water penetration when tested according to ASTM E 1646 at test-pressure difference of [2.86 lbf/sq. ft.] [_______].

***************************************************************************************************************

Value in first paragraph below is ASTM E 331 default; revise to suit Project.

****************************************************************************************************************

Water Penetration for Metal Wall Panels:  No water penetration when tested according to ASTM E 331 at a wind-load design pressure of not less than [2.86 lbf/sq. ft.] [_________].

****************************************************************************************************************

If fire resistance is required, indicate on Drawings the fire-resistance rating of each assembly and the designated testing and inspecting agency that has established the assembly's fire-test-response characteristics.

ASHRAE/IESNA 90.1 includes maximum U-factors for opaque elements of overall assemblies and minimum R-values for insulation of metal buildings, depending on the climate where Project is located.

****************************************************************************************************************

Thermal Performance:  Provide insulated metal panel assemblies with the following maximum U-factors and minimum R-values for opaque elements when tested according to ASTM C 1363 or ASTM C 518:

Metal Roof Panel Assemblies:

U-Factor:  [____].

R-Value:  [____].

Metal Wall Panel Assemblies:

U-Factor:  [____].

R-Value:  [____].

***************************************************************************************************************

Retain one of three paragraphs below to specify cool-roof performance if required.

Retain first paragraph below if required for LEED-NC Credit SS 7.2.  First option is minimum for roofs with slopes of 2:12 or less; second option is minimum for roofs with slopes steeper than 2:12.

***************************************************************************************************************

Insulation Installed in Concealed Locations Surface Burning Characteristics:

****************************************************************************************************************

For IBC, surface burning rating is not required for insulation facings installed in Construction Type III, Type IV, and Type V. Facing must be in substantial contact with ceiling, wall, or floor finish.

****************************************************************************************************************

Batt Insulation: Maximum 25/450 flame spread/smoke developed index when tested in accordance with ASTM E84.

Insulation Installed in Exposed Locations Surface Burning Characteristics: 25/450 flame spread/smoke developed index when tested in accordance with ASTM E84.

****************************************************************************************************************Retain first paragraph below only if products specified in Part 2 are part of a fire-resistance-rated assembly.  Indicate rating, testing agency, and testing agency’s design designation on Drawings.
****************************************************************************************************************

Fire Resistance Rating: Where indicated, provide metal panel assemblies identical to those of assemblies tested for fire resistance per ASTM E 119 by a qualified testing agency.  Identify products with appropriate markings of applicable testing agency.

Indicate design designations from UL’s “Fire Resistance Directory” or from the listings of another qualified testing agency.

Fire-Rated Door Assemblies: Assemblies complying with NFPA 80 that are listed and labeled by a qualified testing agency, for fire-protection ratings indicated, based on testing and positive pressure according to NFPA 252 or UL 10C.

****************************************************************************************************************Retain subparagraph below if applicable and acceptable to authorities having jurisdiction.
****************************************************************************************************************

Oversize Fire-Rated Door Assemblies: For units exceeding sizes of tested assemblies, provide certification by a qualified testing agency that doors comply with standard construction requirements for tested and labeled fire-rated door assemblies except for size.

STRUCTURAL STEEL FRAMING

***********************************************************************************************************

Manufacturer’s products consist of certain types of Metal Building structural systems.  Use of this knowledge, in combination with manufacturers’ catalogs or product data, will allow for insertion of series, type, model, and designations of other characteristics below.

Review this article for compliance with design concept and revise to suit Project. Consult manufacturers for standard framing details.

***********************************************************************************************************

Primary Framing: Manufacturer’s standard primary-framing system, designed to withstand required loads and specified requirements.  Primary framing includes transverse and lean-to frames; rafter, rake, and canopy beams; sidewall, intermediate, end-wall, and corner columns; and lateral-force bracing.

General: Provide frames with attachment plates, bearing plates, and splice members. Factory drill for field-bolted assembly.  Provide frame span and spacing indicated.

****************************************************************************************************************Retain first subparagraph below if allowed.
****************************************************************************************************************

Slight variations in span and spacing may be acceptable if necessary to comply with manufacturer’s standard, as approved by LANL STR.

****************************************************************************************************************
Retain one of first five subparagraphs below.
****************************************************************************************************************

Single-Span Moment Frames: I-shaped frame sections fabricated from shop-welded, built-up steel plates or structural-steel shapes. Interior columns are not permitted.

Modular Moment Frames: I-shaped frame sections fabricated from shop-welded, built-up steel plates or structural-steel shapes.  Provide interior columns fabricated from round steel pipes or tubes, or shop-welded, built-up steel plates.

Truss-Frame, Single-Span Frames:  Rafter frames fabricated from joist girders, and I-shaped column sections fabricated from shop-welded, built-up steel plates or structural-steel shapes.

Truss-Frame Modular Frames: Rafter frames fabricated from joist girders, and I-shaped column sections fabricated from shop-welded, built-up steel plates or structural-steel shapes. Provide interior columns fabricated from round steel pipes or tubes, or shop-welded, built-up steel plates.

****************************************************************************************************************Long-bay frames in first subparagraph below are used where bay spacing exceeds 30 feet.  Steel joist rafters are typically used with long-bay frames.
****************************************************************************************************************

Long-Bay Frames: I-shaped frame sections fabricated from shop-welded, built-up steel plates or structural-steel shapes.  Provide interior columns fabricated from round steel pipes or tubes, or shop-welded, built-up steel plates.

****************************************************************************************************************Retain first subparagraph below if Drawings do not adequately indicate requirements.
****************************************************************************************************************

Frame Configuration: [Single gable] [One-directional sloped] [Lean to, with high side connected to and supported by another structure] [Multiple gable] [Load-bearing-wall type] [Multistory].

Exterior Column Type: [Uniform depth] [Tapered].

Rafter Type: [Uniform depth] [Tapered].

****************************************************************************************************************Retain first paragraph below if required or delete if using half-load primary frames.
****************************************************************************************************************

End-Wall Framing: Manufacturer’s standard primary end-wall framing fabricated for field-bolted assembly to comply with the following:

****************************************************************************************************************Retain first subparagraph below and delete second subparagraph if using full-load frames.
****************************************************************************************************************

End-Wall and Corner Columns: I-shaped sections fabricated from structural-steel shapes; shop-welded, built-up steel plates; or C-shaped, cold-formed, structural-steel sheet.

End-Wall Rafters:  C-shaped, cold-formed, structural-steel sheet; or I-shaped sections fabricated from shop-welded, built-up steel plates or structural-steel shapes.

Secondary Framing: Manufacturer’s standard secondary framing, including purlins, girts, eave struts, flange bracing, base members, gable angles, clips, headers, jambs, and other miscellaneous structural members.  Unless otherwise indicated, fabricate framing from either cold-formed, structural-steel sheet or roll-formed, metallic-coated steel sheet, prepainted with coil coating, to comply with the following:

***************************************************************************************************************Retain one of two “Purlins” subparagraphs below.
***************************************************************************************************************

Purlins: C-or Z-shaped sections; fabricated from built-up steel plates, steel sheet, or structural-steel shapes; minimum 2-1/2-inch-wide flanges.

Purlins: Steel joists of depths indicated.

Girts: C- or Z-shaped sections; fabricated from built-up steel plates, steel sheet, or structural-steel shapes. Form ends of Z-sections with stiffening lips angled 40 to 50 degrees from flange, with minimum 2-1/2-inch-wide flanges.

****************************************************************************************************************Retain depths in first subparagraph below if manufacturer does not determine depths.  Insert manufacturer’s proprietary size if required.
****************************************************************************************************************

Depth: [As indicated] [As required to comply with system design and/or performance requirements] [______].

Eave Struts: Unequal-flange, C-shaped sections; fabricated from built-up steel plates, steel sheet, or structural-steel shapes; to provide adequate backup for metal panels.

Flange Bracing: Minimum 2 x 2 x 1/8-inch structural-steel angles or 1-inch diameter, cold-formed structural tubing to stiffen primary-frame flanges.

Sag Bracing: Minimum 1 x 1 x 1/8-inch structural-steel angles.

****************************************************************************************************************Revise first subparagraph below if channel shape is required instead of base angles.
****************************************************************************************************************

Base or Sill Angles: Minimum 3 x 2-inch zinc-coated (galvanized) steel sheet.

Purlin and Girt Clips: Manufacturer’s standard clips fabricated from steel sheet. Provide galvanized clips where clips are connected to galvanized framing members.

Secondary End-Wall Framing: Manufacturer’s standard sections fabricated from [zinc-coated (galvanized) steel sheet] [structural-steel sheet].

Framing for Openings: Channel shapes; fabricated from cold-formed, structural-steel sheet or structural-steel shapes. Frame head and jamb of door openings and head, jamb, and sill of other openings.

Miscellaneous Structural Members: Manufacturer’s standard sections fabricated from cold-formed, structural-steel sheet; built-up steel plates; or zinc-coated (galvanized) steel sheet; designed to withstand required loads.

Canopy Framing: Manufacturer’s standard structural-framing system, designed to withstand required loads; fabricated from shop-welded, built-up steel plates or structural-steel shapes. Provide frames with attachment plates and splice members, factory drilled for field-bolted assembly.

Type: [Straight-beam, eave type] [Purlin-extension type] [Tapered-beam, below-eave type] [As indicated].

Bracing:  Provide adjustable lateral-force bracing as follows:

****************************************************************************************************************Retain one of first six subparagraphs below, or retain more than one and seventh subparagraph if type of bracing is manufacturer’s option.

AISC 341, the requirements of which must be met regardless of whether or not wind load controls over seismic (per IBC), contains prohibitions on bracing types and bracing members used in braced frames.  Based on the specifics of the Project, edit the following as necessary to meet AISC 341 requirements.
****************************************************************************************************************

Rods:  ASTM A 36 [; ASTM A 572, Grade 50; or ASTM A 529, Grade 50]; minimum ½-inch-diameter steel; threaded full length or threaded a minimum of 6 inches at each end.

Cable: ASTM A 475, ¼-inch-diameter, extra-high-strength grade, Class B, zinc-coated, seven-strand steel; with threaded end anchors.

Angles: Fabricated from structural-steel shapes to match primary framing, of size required to withstand design loads.

Rigid Portal Frames: Fabricated from shop-welded, built-up steel plates or structural-steel shapes to match primary framing of size required to withstand design loads.

Fixed-Base Columns: Fabricated from shop-welded, built-up steel plates or structural-steel shapes to match primary framing; of size required to withstand design loads.

Diaphragm Action of Metal Panels: Design metal building to resist lateral forces through diaphragm action of metal panels.

************************************************************************************************************** Retain subparagraph below if retaining two or more subparagraphs above.  Bracing below costs less but transfers design control to manufacturer.
**************************************************************************************************************

Bracing: Provide lateral-force bracing using any method specified above, at Manufacturer’s option.

Bolts: Provide plain-finish bolts for structural-framing components that are primed or finish painted.  Provide [zinc-plated] [or] [hot-dip galvanized] bolts for structural-framing components that are galvanized.

**************************************************************************************************************** Retain and revise first paragraph below to suit Project.
****************************************************************************************************************

Materials:

W-Shapes: ASTM A 992 [; ASTM A 572, Grade 50 or 55; or ASTM A 529, Grade 50 or 55].

Channels, Angles, M-Shapes, and S-Shapes: ASTM A 36 [; ASTM A 572, Grade 50 or 55; or ASTM A 529, Grade 50 or 55].

Plate and Bar: ASTM A 36 [; ASTM A 572, Grade 50 or 55; or ASTM A 529, Grade 50 or 55].

****************************************************************************************************************

Usually retain first two subparagraphs below only for interior columns of modular moment-resisting, or truss-frame modular, framing systems.

****************************************************************************************************************

Steel Pipe: ASTM A 53, Grade B.

Cold-Formed Hollow Structural Sections: ASTM A 500, Grade B [or C], structural tubing.

Structural-Steel Sheet: Hot-rolled, ASTM A 1011, Structural Steel (SS), Grades 30 through 55, or High-Strength Low-Alloy Steel (HSLAS), Grades 45 through 70; or cold-rolled, ASTM A 1008, Structural Steel (SS), Grades 25 through 80, or High-Strength Low-Alloy Steel (HSLAS), Grades 45 through 70.

Metallic-Coated Steel Sheet: ASTM A 653, Structural Steel (SS), Grades 33 through 80, or High-Strength Low-Alloy Steel (HSLAS), Grades 50 through 80; with G60 coating designation; mill phosphatized.

**************************************************************************************************************** Retain first subparagraph below for secondary framing if required.
****************************************************************************************************************

Metallic-Coated Steel Sheet Prepainted with Coil Coating: Steel sheet, metallic coated by the hot-dip process and prepainted by the coil-coating process to comply with ASTM A 755.

Zinc-Coated (Galvanized) Steel Sheet: ASTM A 653, Structural Steel (SS), Grades 33 through 80, or High-Strength Low-Alloy Steel (HSLAS), Grades 50 through 80; with G90 coating designation.

Aluminum-Zinc Alloy-Coated Steel Sheet; ASTM A 792, Structural Steel (SS), Grade 50 or 80; with Class AZ50 coating.

**************************************************************************************************************** Retain first subparagraph below instead of built-up steel plates or structural-steel shapes if required for primary framing.
****************************************************************************************************************

Joist Girders: Manufactured according to “Standard Specifications for Joist Girders,” in SJI; with steel-angle, top- and bottom-chord members, and end- and top-chord arrangements as indicated and required for primary framing.

**************************************************************************************************************** Retain first subparagraph below instead of cold-formed steel sheet if required for rafters or purlins.
****************************************************************************************************************

Steel Joists: Manufactured according to “Standard Specifications for Open Web Steel Joists, K-Series,” in SJI; with steel-angle, top and bottom-chord members, and end- and top-chord arrangements as indicated and required for secondary framing.

Non-High-Strength Bolts, Nuts, and Washers: ASTM A 307, Grade A, carbon-steel, hex-head bolts; ASTM A 563 carbon-steel hex nuts; and ASTM F 844 plain (flat) steel washers.

Finish: [Plain] [Hot-dip zinc coating, ASTM A153, Class C] [Mechanically deposited zinc coating, ASTM B 695, Class 50].

High-Strength Bolts, Nuts, and Washers: ASTM A 325, Type 1, heavy-hex steel structural bolts; ASTM A 563 heavy-hex carbon steel nuts; and ASTM F 436 hardened carbon-steel washers.

Finish: [Plain] [Hot-dip zinc coating, ASTM A 153, Class C] [Mechanically deposited zinc coating, ASTM B 695, Class 50].

*************************************************************************************************************** Retain option in first subparagraph below if applicable. Indicate locations if using bolts below for some connections and ASTM A 325 bolts in subparagraph above for others.
***************************************************************************************************************

High-Strength Bolts, Nuts, and Washers: ASTM A 490, Type 1, heavy-hex steel structural bolts [or tension-control, bolt-nut-washer assemblies with spline ends]; ASTM A 563 heavy-hex carbon-steel nuts; and ASTM F 436 hardened carbon-steel washers, plain.

**************************************************************************************************************** Retain first subparagraph below if required. Tension-control (twist-off) bolt assemblies correspond to strength of ASTM A 325 bolts.
****************************************************************************************************************

Tension-Control, High-Strength Bolt-Nut-Washer Assemblies: ASTM F 1852, Type 1, heavy-hex head steel structural bolts with spline ends.

Finish: [Plain] [Mechanically deposited zinc coating, ASTM B 695, Class 50] [Mechanically deposited zinc coating, ASTM B 695, Class 50, baked-epoxy coated.]

*************************************************************************************************************** Retain appropriate materials in first subparagraph below or revise if other materials are required. AISC uses the generic term “anchor rods” to include unheaded rods and headed bolts.  Plate washers are used with oversized baseplate holes to resist nut pull-through and to transfer shear from baseplate to anchor rod. 
***************************************************************************************************************

Unheaded Anchor Rods:  ASTM F 1554, Grade [36] [___] [; ASTM A 572, Grade 50] [; ASTM A 36] [; ASTM A 307, Grade C] [______].

Configuration: Straight.

Nuts: ASTM A 563 [heavy-] hex carbon steel.

Plate Washers: ASTM A 36 carbon steel.

Washers: ASTM F 436 hardened carbon steel.

Finish: [Plain] [Hot-dip zinc coating, ASTM A 153, Class C] [Mechanically deposited zinc coating, ASTM B 695, Class 50].

Headed Anchor Rods: ASTM F 1554, Grade [36] [___] [; or ASTM A 307, Grade A] [________].

Configuration: Straight.

Nuts: ASTM A 563 [heavy -] hex carbon steel.

Plate Washers: ASTM A 36carbon steel.

Washers: ASTM F 436 hardened carbon steel.

Finish; [Plain] [Hot-dip zinc coating, ASTM A 153, Class C] [Mechanically deposited zinc coating, ASTM B 695, Class 50].

Threaded Rods: ASTM A 36 [ASTM A 572, Grade 50] [ASTM A 307, Grade C] [______].

Nuts: ASTM A 563 [heavy-] hex carbon steel.

Washers: [ASTM F 436 hardened] [ASTM A 36] carbon steel.

Finish: [Plain] [Hot-dip zinc coating, ASTM A 153, Class C] [Mechanically deposited zinc coating, ASTM B 695, Class 50].

Finish: Factory primed. Apply specified primer immediately after cleaning and pretreating.

Apply primer to primary and secondary framing to a minimum dry film thickness of 1 mil.

Prime secondary framing formed from uncoated steel sheet to a minimum dry film thickness of 0.5 mil on each side.

Prime galvanized members with specified primer after phosphoric acid pretreatment.

**************************************************************************************************************** Verify that primer in subparagraph below is compatible with fireproofing if required.
****************************************************************************************************************

Primer: SSPC-Paint 15, Type I, red oxide.

**************************************************************************************************************** Sustainable design requirements normally specify maximum VOC content for products that affect indoor air quality.  Delete option to extend requirement to exterior applications.
****************************************************************************************************************

[Interior] Anti-Corrosive Paints: Maximum volatile organic compound content in accordance with GS-11.

**************************************************************************************************************** If required, insert requirements for crane runway beams, supports, and bracing; mezzanine framing and decking; and floor framing for multistory applications.
****************************************************************************************************************

METAL ROOF PANELS

**************************************************************************************************************** Manufacturer’s products consist of certain types of Metal Building roof panels. Use of this knowledge, in combination with manufacturers’ catalogs or product data, will allow for insertion of series, type, model, and designations of other characteristics below.

This article includes Metal Building System manufacturers’ standard metal roof panels. Specify other types of metal roof panels and custom metal panels in Section 07 4113, Metal Roof Panels.

Profile requirements in this article are often better described graphically than verbally.  If profiles are indicated on Drawings, delete profile descriptions and retain types of metals and metal thickness.

Retain one or more of first three paragraphs below.  Revise to suit Project, such as adding yield strength.
****************************************************************************************************************

Vertical-Rib, Standing-Seam Metal Roof Panels [Drawing ______]: Formed with vertical ribs at panel edges and [intermediate stiffening ribs symmetrically spaced] [flat pan] between ribs; designed for sequential installation by mechanically attaching panels to supports using concealed clips located under one side of panels and engaging opposite edge of adjacent panels.

***************************************************************************************************************

Metal thickness options in first subparagraph below correspond to obsolete 26, 24, and 22 gage, respectively.

***************************************************************************************************************

Material:  [Zinc-coated (galvanized)] [Aluminum-zinc alloy-coated] steel sheet, [0.022-inch (0.56-mm)] [0.028-inch (0.71-mm)] [0.034-inch (0.86-mm)] nominal thickness Certify roofing materials solar reflectance index.

    - Exterior Finish:  [Fluoropolymer] [Siliconized polyester].

    - Color:  [As indicated by manufacturer's designations] [As selected by Architect from manufacturer's full range] [_______]

Clips: Manufacturer’s standard, [fixed type] [floating type to accommodate thermal movement]; fabricated from [zinc-coated (galvanized) steel] [aluminum-zinc alloy-coated steel] [stainless-steel] [zinc-coated (galvanized) steel, aluminum-zinc alloy-coated steel, or stainless-steel] sheet.

**************************************************************************************************************** Retain one of first two subparagraphs below.
****************************************************************************************************************

Joint Type: Panels snapped together.

Joint Type: Mechanically seamed, [single folded] [double folded] [folded according to manufacturer’s standard].

Panel Coverage: [16 inches] [_________].

Panel Height: [2 inches] [_______].

Uplift Rating: [UL580, Uplift Class 90.] [________.]

Trapezoidal-Rib, Standing-Seam Metal Roof Panels [Drawing _______]: Formed with raised trapezoidal ribs at panel edges and [intermediate stiffening ribs symmetrically spaced] [flat pan] between ribs; designed for sequential installation by mechanically attaching panels to supports using concealed clips located under one side of panels and engaging opposite edge of adjacent panels.

**************************************************************************************************************** Metal thickness options in first subparagraph below correspond to obsolete 26, 24, and 22 gage, respectively.
****************************************************************************************************************

Material: [Zinc-coated (galvanized)] [Aluminum-zinc alloy-coated] steel sheet, [0.022-inch] [0.028-inch] [0.034-inch] nominal thickness.

Exterior Finish:  [Fluoropolymer] [Siliconized polyester].

Color:  [As indicated by manufacturer's designations] [As selected from manufacturer's full range] [_________].

**************************************************************************************************************** If required, insert requirements for aluminum. Verify availability with manufacturers.
****************************************************************************************************************

Clips: Manufacturer’s standard, [fixed type] [floating type to accommodate thermal movement]; fabricated from [zinc-coated (galvanized) steel] [aluminum-zinc alloy-coated steel] [stainless-steel] [zinc-coated (galvanized) steel, aluminum-zinc alloy-coated steel, or stainless-steel] sheet.

**************************************************************************************************************** Retain one of first two subparagraphs below.
****************************************************************************************************************

Joint Type: Panels snapped together.

Joint Type: Mechanically seamed, [single folded] [double folded] [folded according to manufacturer’s standard].

Panel Coverage: [24 inches] [________].

Panel Height: [3 inches] [________].

Uplift Rating: [UL 580, Uplift Class 90.] [_______.]

Tapered-Rib-Profile, Lap-Seam Metal Roof Panels [Drawing _______: Formed with raised, trapezoidal major ribs and [intermediate stiffening ribs symmetrically spaced] [flat pan] between major ribs; designed to be installed by lapping side edges of adjacent panels and mechanically attaching panels to supports using exposed fasteners in side laps.

***************************************************************************************************************Metal thickness options in first subparagraph below correspond to obsolete 26, 24, and 22 gage, respectively.
***************************************************************************************************************

Material: [Zinc-coated (galvanized)] [Aluminum-zinc alloy-coated] steel sheet, [0.022-inch] [0.028-inch] [0.034-inch] nominal thickness.

Exterior Finish: [Fluoropolymer] [Siliconized polyester].

Color: [As indicated by manufacturer’s designations] [As selected from manufacturer’s full range] [_________].

Major-Rib Spacing: [6 inches] [12 inches] [_______] o.c.

Panel Coverage: [36 inches] [_______].

Panel Height: [0.75 inches] [1.125 inches] [1.188 inches] [1.25 inches] [1.5 inches] [_______]

**************************************************************************************************************** Retain first paragraph below if insulated system is required and insulation must be concealed.
****************************************************************************************************************

Tapered-Rib-Profile, Metal Liner Panels [Drawing ________]: Formed with raised, trapezoidal major ribs and [intermediate stiffening ribs symmetrically spaced] [flat pan] between major ribs; designed to be installed by lapping side edges of adjacent panels and mechanically attaching panels to supports using exposed fasteners in side laps.

**************************************************************************************************************** Metal thickness options in first subparagraph below correspond to obsolete 26, 24, and 22 gage, respectively.
****************************************************************************************************************

Material: [Zinc-coated (galvanized)] [Aluminum-zinc alloy-coated] steel sheet, [0.022-inch] [0.028-inch] [0.034-inch] nominal thickness.

Exterior Finish: [Fluoropolymer] [Siliconized polyester].

Color: [As indicated by manufacturer’s designations] [As selected from manufacturer’s full range] [_________]

Major-Rib Spacing: [6 inches] [12 inches] [_______] o.c Panel Coverage:

Panel Coverage: [36 inches] [_______]Materials:

Panel Height: [1.25 inches] [1.5 inches] [__________].

Materials:

Metallic-Coated Steel Sheet: Restricted-flatness steel sheet, metallic coated by the hot-dip process and prepainted by the coil-coating process to comply with ASTM A 755.

**************************************************************************************************************** Retain one of first two subparagraphs below. Coordinate with products specified.
****************************************************************************************************************

Zinc-Coated (Galvanized) Steel Sheet: ASTM A 653, G9) coating designation; structural quality.

Aluminum-Zinc Alloy-Coated Steel Sheet: ASTM A 792, Class AZ50 coating designation, Grade 40); structural quality.

Surface: [Smooth, flat] [Embossed] finish.

Finishes:

Exposed Coil-Coated Finish:

**************************************************************************************************************** Retain one of first three subparagraphs below. Verify availability of finishes for products specified. If retaining more than one, indicate location of each on Drawings or by inserts.  For exact finish, insert names of coating manufacturers and products.

Revise requirements in first two subparagraphs below if performance levels indicated in AAMA 621 are insufficient. Refer to manufacturers’ catalogs or product data.
****************************************************************************************************************

Two-coat Fluoropolymer: AAMA 621. Fluoropolymer finish containing not less than 70 percent PVDF resin by weight in color coat.  Prepare, pretreat, and apply coating to exposed metal surfaces to comply with coating and resin manufacturers’ written instructions.

Three-Coat Fluoropolymer: AAMA 621. Fluoropolymer finish containing not less than 70 percent PVDF resin by weight in both color coat and clear topcoat. Prepare, pretreat, and apply coating to exposed metal surfaces to comply with coating and resin manufacturers’ written instructions.

**************************************************************************************************************** Finish in first subparagraph below is usually an economy system, although performance of newer, more expensive formulations can approach that of high-performance organic coatings.
****************************************************************************************************************

Siliconized Polyester: Epoxy primer and silicone-modified, polyester-enamel topcoat; with a dry film thickness of not less than 0.2 mil for primer and 0.8 mil for topcoat.

**************************************************************************************************************** Finish in subparagraph below is frequently used as a factory finish for interior surfaces.
****************************************************************************************************************

Concealed Finish:  Apply pretreatment and manufacturer’s standard white or light-colored acrylic or polyester backer finish, consisting of prime coat and wash coat with a minimum total dry film thickness of 0.5 mil.

METAL WALL PANELS

**************************************************************************************************************** Manufacturers’ products consist of certain types of Metal Building uninsulated metal wall panels. Use this knowledge, in combination with manufacturers’ catalog or product data, to insert series, type, model, and designations of other characteristics below.

This article includes Metal Building System manufacturers’ standard metal wall panels. If the Project requires other types of metal wall panels and custom metal panels then they must be specified in a new Division 07 Section, Metal Wall Panels.

Profile requirements in this article are often better described graphically than verbally. If profiles are indicated on Drawings, delete profile descriptions and retain types of metals and metal thicknesses.

Retain one or more of first three paragraphs below.  Revise to suit Project, such as adding yield strength.
****************************************************************************************************************

Tapered-Rib-Profile, Exposed-Fastener Metal Wall Panels [Drawing _________]; Formed with raised, trapezoidal major ribs and [intermediate stiffening ribs symmetrically spaced] [flat pan] between major ribs; designed to be installed by lapping side edges of adjacent panels and mechanically attaching panels to supports using exposed fasteners in side laps.

**************************************************************************************************************** Metal thickness options in first subparagraph below correspond to obsolete 26, 24, and 22 gage, respectively.
****************************************************************************************************************

Material: [Zinc-coated (galvanized)] [Aluminum-zinc alloy coated] steel sheet, [0.022-inch] [0.028-inch] [0.034-inch] nominal thickness.

Exterior Finish: [Fluoropolymer] [Siliconized polyester].

Color: [As indicated by manufacturer’s designations] [As selected from manufacturer’s full range] [__________].

Major-Rib Spacing: [6 inches] [12 inches] [__________] o.c.

Panel Coverage: [36 inches] [__________].

Panel Height: [0.75 inch] [1.125 inches] [1.188 inches] [1.25 inches] [1.5 inches] [______].

Reverse-Rib-Profile, Exposed-Fastener Metal Wall Panels [Drawing ________]: Formed with recessed, trapezoidal major valleys and [Intermediate stiffening valleys symmetrically spaced] [flat pan] between major valleys; designed to be installed by lapping side edges of adjacent panels and mechanically attaching panels to supports using exposed fasteners in side laps.

**************************************************************************************************************** Metal thickness options in first subparagraph below correspond to obsolete 26, 24, and 22 gage, respectively.
****************************************************************************************************************

Material: [Zinc-coated (galvanized)] [Aluminum-zinc alloy-coated] steel sheet, [0.022-inch] [0.028-inch] [0.034-inch] nominal thickness.

Exterior Finish: [Fluoropolymer] [Siliconized polyester].

Color: [As indicated by manufacturer’s designations] [As selected from manufacturer’s full range] [________].

Major-Rib Spacing: [12 inches] [________] o.c.

Panel Coverage: [36 inches] [________].

Panel Height: [1.125 inches] [1.188 inches] [1.25 inches] [1.5 inches] [_______].

Concealed-Fastener Metal Wall Panels [Drawing ________]: Formed with vertical panel edges and [a single wide recess, centered between panel edges] [flush surface]; with flush joint between panels; with 1-inch- wide flange for attaching interior finish; designed to be installed by lapping and interconnecting side edges of adjacent panels and mechanically attaching through panel to supports using concealed fasteners [and factory-applied sealant] in side laps.

Material: [Zinc-coated (galvanized)] [Aluminum-zinc alloy-coated] steel sheet, [0.028-inch] [0.034-inch] nominal thickness

Exterior Finish: [Fluoropolymer] [Siliconized polyester].

Color: [As indicated by manufacturer’s designations] [As selected from manufacturer’s full range] [________]

Panel coverage: [16 inches] [________].

Panel Height: [3 inches] [________].

**************************************************************************************************************** Retain one of first two paragraphs below if insulated system is required and insulation must be concealed.
****************************************************************************************************************

Tapered-Rib-Profile, Metal Liner Panels [Drawing __________]: Formed with raised, trapezoidal major ribs and [intermediate stiffening ribs symmetrically spaced] [flat pan] between major ribs; designed to be installed by lapping side edges of adjacent panels and mechanically attaching panels to supports using exposed fasteners in side laps.

Material: [Zinc-coated (galvanized)] [Aluminum-zinc alloy-coated] steel sheet, [0.022-inch] [0.028-inch] [0.034-inch] nominal thickness.

Exterior Finish: [Siliconized polyester] [Acrylic enamel].

Color: [As indicated by manufacturer’s designations] [As selected from manufacturer’s full range] [________].

Major-Rib Spacing: [6 inches] [12 inches] [________] o.c.

Panel Coverage: [36 inches] [________].

Panel Height: [1.25 inches] [1.5 inches] [_______].

Flush-Profile, Metal Liner Panels [Drawing _________]: [Solid] [Perforated] panels formed with vertical panel edges and [intermediate stiffening ribs symmetrically spaced] [flat pan] between panel edges; with flush joint between panels; designed for interior side of metal wall panel assemblies and installed by lapping and interconnecting side edges of adjacent panels and mechanically attaching through panel to supports using concealed fasteners [and factory-applied sealant] in side laps.

**************************************************************************************************************** Metal thickness options in first subparagraph below correspond to obsolete 24, and 22 gage, respectively.
****************************************************************************************************************

Material: [Zinc-coated (galvanized)] [Aluminum-zinc alloy-coated] steel sheet, [0.028-inch] [0.034-inch] nominal thickness.

Exterior Finish: [Siliconized polyester] [Polyester] [Acrylic enamel].

Color: [As indicated by manufacturer’s designations] [As selected from manufacturer’s full range] [________].

**************************************************************************************************************** Retain first subparagraph below if required.
****************************************************************************************************************

Sound Absorption: NRC not less than [0.65] [0.85] [1.00] [________] when tested according to ASTM C 423.

Panel Coverage: [12 inches] [________].

Panel Height: [1.5 inches] [________].

Materials:

Metallic-Coated Steel Sheet: Restricted-flatness steel sheet, metallic coated by the hot-dip process and prepainted by the coil-coating process to comply with ASTM A 755.

**************************************************************************************************************** Retain one of first two subparagraphs below. Coordinate with products specified.
****************************************************************************************************************

Zinc-Coated (Galvanized) Steel Sheet: ASTM A 653, G90 coating designation; structural quality.

Aluminum-Zinc Alloy-Coated Steel Sheet; ASTM A 792, Class AZ50 coating designation, Grade 40; structural quality.

Surface: [Smooth, flat] [Embossed] finish.

Finishes:

Exposed Coil-Coated Finish:

*************************************************************************************************************** Retain one of first three subparagraphs below. Verify availability of finishes for products specified. If retaining more than one, indicate location of each on Drawings or by inserts. For exact finish, insert names of coating manufacturers and products.

Revise requirements in first two subparagraphs below if performance levels indicated in AAMA 621 are insufficient. Refer to manufacturers’ catalogs or product data.
***************************************************************************************************************

Two-Coat Fluoropolymer: AAMA 621. Fluoropolymer finish containing not less than 70 percent PVDF resin by weight in color coat.  Prepare, pretreat, and apply coating to exposed metal surfaces to comply with coating and resin manufacturers’ written instructions.

Three-Coat Fluoropolymer: AAMA 621. Fluoropolymer finish containing not less than 70 percent PVDF resin by weight in both color coat and clear topcoat.  Prepare, pretreat, and apply coating to exposed metal surfaces to comply with coating and resin manufacturers’ written instructions.

**************************************************************************************************************** Finish in first subparagraph below is usually an economy system, although performance of newer, more expensive formulations can approach that of high-performance organic coatings.
****************************************************************************************************************

Siliconized Polyester: Epoxy primer and silicone-modified, polyester-enamel topcoat; with a dry film thickness of not less than 0.2 mil for primer and 0.8 mil for topcoat.

**************************************************************************************************************** Finish in subparagraph below is frequently used as a factory finish for interior surfaces.
****************************************************************************************************************

Concealed Finish: Apply pretreatment and manufacturer’s standard white or light-colored acrylic or polyester backer finish, consisting of prime coat and wash coat with a minimum total dry film thickness of 0.5 mil.

FOAM-INSULATION-CORE METAL WALL PANELS

**************************************************************************************************************** This article includes Metal Building System manufacturers’ standard insulated metal wall panels. If the Project requires other types of metal wall panels and custom metal panels then they must be specified in a new Division 07 Section, Metal Wall Panels.

Products in this article are factory assembled.
****************************************************************************************************************

Description: Provide factory-formed and –assembled, metal wall panels fabricated from two metal facing sheet and an insulation core foamed n place during fabrication, with joints between panels designed to form weathertight seals. Include accessories required for weathertight installation.

Concealed-Fastener, Foam-Insulation-Core Metal Wall Panels [Drawing _______]: Formed with tongue-and-groove panel edges; designed for sequential installation by interlocking panel edges and mechanically attaching panels to supports using concealed clips or fasteners.

Facings: Fabricate panel with exterior and interior facings of same material and thickness.

Exterior Surface: [Smooth, flat] [Striated] [Shallow ribs] [Shallow V grooves].

Panel Coverage: [36 inches] [42 inches] [________] nominal.

Panel Thickness: [2 inches] [2.5 inches] [3 inches] [4 inches] [5 inches] [6 inches] [________].

Thermal- Resistance Value (R-Value): [_________].

Panel Performance:

Flatwise Tensile Strength: 30 psi when tested according to ASTM C 297.

Humid Aging: Volume increase not greater than 6.0 percent and no delamination or metal corrosion when tested for seven days at 140 deg F and 100 percent relative humidity according to ASTM D 2126.

Heat Aging: Volume increase not greater than 2.0 percent and no delamination, surface blistering, or permanent bowing when tested for seven days at 200 deg F according to ASTM D 2126.

Cold Aging: Volume decrease not more than 1.0 percent and no delamination, surface blistering, or permanent bowing when tested for seven days at minus 20 deg F according to ASTM D 2126.

Fatigue: No evidence of delamination, core cracking, or permanent bowing when tested to a 20-lbf/sq. ft. positive and negative wind load and with deflection of L/180 for two million cycles.

Autoclave: No delamination when exposed to 2 –psi pressure at a temperature of 212 deg F for 2-1/2 hours.

Fire-Test-Response Characteristics: Class A according to ASTM E 108.

Polyisocyanurate Insulation-Core Performance:

Density: 2.0 to 2.6 lb/cu.ft. when tested according to ASTM D 1622.

Compressive Strength: Minimum 20 psi when tested according to ASTM D 1621.

Shear Strength: 26 psi when tested according to ASTM C 273.

Materials:

Polyisocyanurate Insulation: Modified polyisocyanurate foam using a non-CFC blowing agent, foamed-in-place or board type as indicated, with maximum flame-spread and smoke-developed indexes of 25 and 450, respectively.

Closed-Cell Content: 90 percent when tested according to ASTM D 6226.

Metallic-Coated Steel Sheet: Restricted-flatness steel sheet, metallic coated by the hot-dip process and pre-painted by the coil-coating process to comply with ASTM A 755.

***********************************************************************************************************

Retain one of first two subparagraphs below. Coordinate with products specified.

***********************************************************************************************************

Zinc-Coated (Galvanized) Steel Sheet: ASTM A 653, G90 coating designation; structural quality.

Aluminum-Zinc Alloy-Coated Steel Sheet: ASTM A 792, Class AZ50 coating designation, Grade 40; structural quality.

Surface: [Smooth, flat] [Embossed] finish.

Finishes:

Exposed Coil-Coated Finish:

***************************************************************************************************************Retain one of first three subparagraphs below. Verify availability of finishes for products specified. If retaining more than one, indicated location of each on Drawings or by inserts. For exact finish, insert names of coating manufacturers and products.

Revise requirements in first two paragraphs below if performance levels indicated in AAMA 621 are insufficient. Refer to manufacturers’ catalogs or product data.
****************************************************************************************************************

Two-Coat Fluoropolymer: AAMA 621, Fluoropolymer finish containing not less than 70 percent PVDF resin by weight in color coat. Prepare, pretreat, and apply coating to exposed metal surfaces to comply with coating and resin manufacturer’s written instructions.

Three-Coat Fluoropolymer: AAMA 621. Fluoropolymer finish containing not less than 70 percent PVDF resin by weight in both color coat and clear topcoat. Prepare, pretreat, and apply coating to exposed metal surfaces to comply with coating and resin manufacturer’s written instructions.

**************************************************************************************************************** Finish in first subparagraph below is usually an economy system, although performance of newer, more expensive formulations can approach that of high-performance organic coatings.
****************************************************************************************************************

Siliconized Polyester: Epoxy primer and silicone-modified, polyester-enamel topcoat; with a dry film thickness of not less than 0.2 mil for primer and 0.8 mil for topcoat.

**************************************************************************************************************** Finish in subparagraph below is frequently used as a factory finish for interior surfaces.
****************************************************************************************************************

Concealed Finish: Apply pretreatment and manufacturer’s standard white or light-colored acrylic or polyester backer finish, consisting of prime coat and wash coat with a minimum total dry film thickness of 0.5 mil.

TRANSLUCENT PANELS

**************************************************************************************************************** Retain one of first two paragraphs below. “Limited flammability” is not a fire-hazard classification but indicates material is less flammable than general-purpose material.
****************************************************************************************************************

Uninsulated Translucent Panels: Glass-fiber-reinforced polyester, translucent plastic; complying with ASTM D 3841, [Type CC2 (general purpose)] [Type CC1 (limited flammability)], Grade 1 (weather resistant); smooth finish on both sides. Match profile of adjacent metal panels.

**************************************************************************************************************
Verify, with manufacturers, panel weights in first two subparagraphs below.
**************************************************************************************************************

Roof Panel Weight: Not less than 8 oz./sq.ft.

Wall Panel Weight: Not less than 6 oz./sq.ft.

Light Transmittance: Not less than [55] [______] percent according to ASTM D 1494.

Metal Edge: Fabricate full length of each side of panel with metal edge for seaming into standing-seam roof panel joint.

Color: [White] [________].

Insulated Translucent Panels: Fabricate insulating units of two sheets of glass-fiber-reinforced polyester, translucent plastic separated by an air space; complying with ASTM D 3841, Type CC1 (limited flammability), Grade 1 (weather resistant); smooth finish on both sides. Match profile of adjacent metal panels.

**************************************************************************************************************** Verify, with manufacturers, panel weights in first two subparagraphs below.
****************************************************************************************************************

Exterior Panel Weight: Not less than [8 oz./sq.ft.] [6 oz./sq.ft.]

Interior Panel Weight: Not less than [8 oz./sq.ft.] [6 oz./sq.ft.] [4 oz./sq.ft.]

Light Transmittance: Not less than [42] [______] percent according to ASTM D 1494.

Metal Edge: Fabricate full length of each side of panel with metal edge for seaming into standing-seam roof panel joint.

Color: [White] [________].

Mastic for Translucent Panels: Nonstaining, saturated vinyl polymer as recommended by translucent panel manufacturer for sealing laps.

Performance:

Structural Design: Translucent panels shall be designed by their manufacturer to withstand the wind loads specified in paragraph “Wind Loads” in Part 1 (i.e., for ASCE 7 Components and Cladding).

Translucent roof panels shall also be capable of sustaining a 200-pound concentrated load on a one-foot square located anywhere on the panel without rupture.

Surface-Burning Characteristics: As determined by testing identical products according to ASTM E 84 by a qualified testing agency. Identify products with appropriate markings of applicable testing agency.

Flame-Spread Index: [25] [_____] or less.

Smoke-Developed Index: [450] [______] or less.

METAL SOFFIT PANELS

**************************************************************************************************************** This article includes Metal Building System manufacturers’ standard metal soffit panels. Specify other types of metal soffit panels and custom metal panels in Section 07 4113, Metal Roof Panels or in a new Division 07 Section, “Metal Wall Panels.”

Profile requirements in this article are often better described graphically than verbally. If profiles are indicated on Drawings, delete profile descriptions and retain types of metals and metal thicknesses.
****************************************************************************************************************

General: Provide factory-formed metal soffit panels designed to be installed by lapping and interconnecting side edges of adjacent panels and mechanically attaching through panel to supports using concealed fasteners [and factory-applied sealant] in side laps. Include accessories required for weathertight installation.

Metal Soffit Panels: Match profile and material of metal [roof] [wall] panels.

Finish: [Match finish and color of metal roof panels] [Match finish and color of metal wall panels] [As indicated on Drawings].

****************************************************************************************************************

Retain paragraph above or one or both paragraphs below. Retain remainder of this article if not retaining paragraph above and if metal soffit panels are not required to match metal roof or wall panels.

****************************************************************************************************************

Tapered-Rib-Profile, Exposed-Fastener Metal Soffit Panels [Drawing ______]: Formed with raised, trapezoidal major ribs and [intermediate stiffening ribs symmetrically spaced] [flat pan] between major ribs; designed to be installed by lapping side edges of adjacent panels and mechanically attaching panels to supports using exposed fasteners in side laps.

*************************************************************************************************************** Metal thickness options in first subparagraph below correspond to obsolete 26, 24, and 22 gage, respectively.
***************************************************************************************************************

Material: [Zinc-coated (galvanized)] [Aluminum-zinc alloy-coated] steel sheet, [0.022-inch] [0.028-inch] [0.034-inch] nominal thickness.

Exterior Finish: [Fluoropolymer] [Siliconized polyester].

Color: [As indicated by manufacturer’s designations] [As selected from manufacturer’s full range] [________].

Major-Rib Spacing: [6 inches] [12 inches] [________] o.c.

Panel Coverage: [36 inches] [________].

Panel Height: [0.75 inch] [1.125 inches] [1.188 inches] [1.25 inches] [1.5 inches] [_______].

Concealed-Fastener Metal Soffit Panels [Drawing ___________]: Formed with vertical panel edges and [a single wide recess, centered between panel edges] [flush surface]; with flush joint between panels; with 1-inch wide flange for attaching interior finish; designed to be installed by lapping and interconnecting side edges of adjacent panels and mechanically attaching through panel to supports using concealed fasteners [and factory-applied sealant] in side laps.

**************************************************************************************************************** Metal thickness options in first subparagraph below correspond to obsolete 24 and 22 gage, respectively.
****************************************************************************************************************

Material: [Zinc-coated (galvanized)] [Aluminum-zinc alloy-coated] steel sheet, [0.028-inch] [0.034-inch] nominal thickness.

Exterior Finish: [Fluoropolymer] [Siliconized polyester].

Color: [As indicated by manufacturer’s designations] [As selected from manufacturer’s full range] [________].

Panel Coverage: [12 inches] [16 inches] [________].

Panel Height: [1 inch] [1.5 inches] [_______].

THERMAL INSULATION

**************************************************************************************************************** Retain one of first four paragraphs below. Many Metal Building System manufacturers do not provide insulation as part of their Metal Building package; verify availability. Even for those that do, the specifier may elect instead to specify insulation n Section 07 2100, Thermal Insulation. Verify type of insulation needed to obtain a fire-resistance rating if required.

Metal Building insulation in first two paragraphs below is most common type of insulation used for Metal Building Systems, especially if it is to be exposed on the interior.
****************************************************************************************************************

Faced Metal Building Insulation: ASTM C 991, Type II, glass-fiber blanket insulation; 0.5-lb/cu. ft density; 2-inch wide, continuous, vapor-tight edge tabs; with a flame-spread index of 25 or less.

Unfaced Metal Building Insulation: ASTM C 991, Type I, or NAIMA 202, glass-fiber-blanket insulation; 0.5-lb/cu.ft. density; 2-inch-wide, continuous, vapor-tight edge tabs; with a flame-spread index of 25 or less.

****************************************************************************************************************

Vapor-retarder facing in subparagraph below for blanet insulation is often provided separately and may be laminated to insulation before arriving at Project site, or it may be installed concurrently with insulation. NAIMA recommends that metal building insulation have a vapor-retarder facing with a permeance not greater than 0.10 perm. Facing selection may also be affected by light reflectivity and cold-weather workability.

****************************************************************************************************************

Vapor-Retarder Facing: ASTM C 1136, with permeance not greater than 0.02 perm when tested according to ASTM E 96, Desiccant Method.

**************************************************************************************************************** Retain one of four subparagraphs below or delete all and insert manufacturer’s proprietary product.
****************************************************************************************************************

Composition: White metalized-polypropylene film facing, fiberglass scrim reinforcement, and kraft-paper backing.

Composition: Aluminum foil facing, elastromeric barrier coating, fiberglass scrim reinforcement, and kraft-paper backing.

Composition: White [polypropylene] [vinyl] film facing, fiberglass scrim reinforcement, and metalized-polyester film backing.

****************************************************************************************************************

Composition in subparagraph below is one of the most expensive facings but offers very high puncture resistance.

****************************************************************************************************************

Composition: White polypropylene film facing and fiberglass-polyester-blend fabric backing.

Mineral-Fiber-Blanket Insulation: ASTM C 665, type indicated below; consisting of fibers manufactured from glass, slag wool, or rock wool.

**************************************************************************************************************** Retain one of three subparagraphs below.
****************************************************************************************************************

Nonreflective Faced: Type II (blankets with nonreflective membrane covering), Category 1 (membrane is a vapor retarder), Class A (membrane-faced surface with a flame-spread index of 25 or less).

Reflective Faced: Type III (blankets with reflective membrane covering), Category 1 (membrane is a vapor retarder), Class A (membrane-faced surface with a flame-spread index of 25 or less).

Unfaced: Type I (blankets without membrane covering), passing ASTM E 136 for combustion characteristics.

**************************************************************************************************************** Vapor-retarder facing in subparagraph below for blanket insulation is often provided separately and may be laminated to insulation before arriving at Project site, or it may be installed concurrently with insulation.  NAIMA recommends that Metal Building insulation have a vapor retarder facing with a permeance not greater than 0.10 perm. Facing selection may also be affected by light reflectivity and cold-weather workability.
****************************************************************************************************************

Vapor-Retarder Facing: ASTM C 1136, with permeance not greater than 0.02 perm when tested according to ASTM E 96, Desiccant Method.

****************************************************************************************************************Retain one of four subparagraphs below or delete all and insert manufacturer’s proprietary product.
****************************************************************************************************************

Composition: White metalized-polypropylene film facing, fiberglass scrim reinforcement, and kraft-paper backing.

Composition: Aluminum foil facing, elastomeric barrier coating, fiberglass scrim reinforcement, and kraft-paper backing.

Composition: White [polypropylene] [vinyl] film facing, fiberglass scrim reinforcement, and metalized-polyester film backing.

****************************************************************************************************************

Composition in subparagraph below is one of the most expensive facings but offers very high puncture resistance.

****************************************************************************************************************

Composition: White polypropylene film facing and fiberglass-polyester-blend fabric backing.

Faced, Polyisocyanurate Board Insulation: ASTM C 1289, Type I (foil facing), Class 2, with maximum flame-spread and smoke-developed indexes of 75 and 450, respectively, based on tests performed on unfaced core. Provide units tested for interior exposure without an approved thermal barrier.

************************************************************************************************************** Retain first paragraph below with insulation that is to be left exposed to the interior.
**************************************************************************************************************

Retainer Strips: 0.025-inch nominal-thickness, formed, metallic-coated steel or PVC retainer clips colored to match insulation facing.

Vapor-Retarder Tape: Pressure-sensitive tape of type recommended by vapor-retarder manufacturer for sealing joints and penetrations in vapor retarder.

DOORS AND FRAMES

Structural Design: Doors and frames shall be designed by their manufacturer to withstand the wind loads specified in paragraph “Wind Loads” in Part 1 (i.e., for ASCE 7 Components and Cladding).

[B.	Swinging Personnel Doors and Frames: As specified in Section 08 1100, Metal Doors and Frames]

********[OR]********

*************************************************************************************************************** Retain first paragraph below if personnel doors are not specified with other doors in Section 08 1100, Metal Doors and Frames. Personnel doors below are standard with Metal Building System manufacturers.
***************************************************************************************************************

[B.	Swinging Personnel Doors and Frames: Metal Building System manufacturer’s standard doors and frames; prepared and reinforced at strike and at hinges to receive factory-and field-applied hardware according to BHMA A156 Series.

**************************************************************************************************************** If required, revise first subparagraph below to include compliance with SDI for types, styles, and design requirements. Only a limited number of manufacturers provide doors that meet SDI standards.
****************************************************************************************************************

Steel Doors: 1-3/4 inches thick; fabricated from 0.040-inch nominal-thickness, metallic-coated steel face sheets; of [seamed] [seamless], hollow-metal construction; with 0.064-inch nominal-thickness, inverted metallic-coated steel channels welded to face sheets at top and bottom of door.

Design: [Flush panel] [As indicated] [______].

**************************************************************************************************************** Retain one of first three subparagraphs below.
****************************************************************************************************************

Core: Kraft honeycomb with U-factor rating of at least 0.47 Btu/sq.ft x h x deg F.

Core: Polystyrene foam with U-factor rating of at least 0.16 Btu/sq.ft x h x deg F.

Core: Polyurethane foam with U-factor rating of at least 0.07 Btu/sq.ft x h x deg F.

**************************************************************************************************************** Retain first two subparagraphs below if doors have glazed panel.
****************************************************************************************************************

Glazing Frames: Steel frames to receive field-installed glass.

Glazing: As specified in Section 08 8000, Glazing.

Steel Frames: Fabricate 2-inch-wide face frames from 0.064-inch nominal thickness, metallic-coated steel sheet.

Fabricate concealed stiffeners, reinforcement, edge channels, and moldings from either cold- or hot-rolled steel sheet.]

- Finishes for Personnel Doors and Frames:

**************************************************************************************************************** Retain one of two finish subparagraphs below.
****************************************************************************************************************

  - Prime Finish: Factory-apply manufacturer’s standard primer immediately after cleaning and pretreating.

    - Shop Primer: Manufacturer’s standard, fast-curing, lead- and chromate-free primer complying with SDI A250.10 acceptance criteria; recommended by primer manufacturer for substrate; compatible with substrate and field-applied coatings despite prolonged exposure.

  - Factory-Applied Paint Finish: Manufacturer’s standard, complying with SDI A250.3 for performance and acceptance criteria.

    - Color and Gloss: [As indicated by manufacturer’s designations] [Match sample] [As selected from manufacturer’s full range] [_______________].

WINDOWS

Structural Design: Windows shall be designed by their manufacturer to withstand the wind loads specified in paragraph “Wind Loads” in Part 1 (i.e., for ASCE 7 Components and Cladding).

**************************************************************************************************************** Retain first paragraph below and delete remainder of article if the aluminum windows specified in Section 08 5113, Aluminum Windows, are satisfactory for the Project.
****************************************************************************************************************

[B.	Aluminum Windows: As specified in Section 08 5113, Aluminum Windows]

********[OR]********

[B.	Aluminum Windows: Metal Building System manufacturer’s standard, with self-flashing mounting fins, and as follows:

- Type, Performance Class, and Performance Grade: Comply with AAMA/WDMA/CSA 101/I.S.2/A440 and as follows:

**************************************************************************************************************** Retain one or more types of units from first three subparagraphs below. Revise performance class and grade to suit Project.
****************************************************************************************************************

  - Horizontal-Sliding Units: [HS-LC25] [HS-C30] [_________].

  - Single-Hung Units: [H-LC25] [H-C30] [___________].

  - Fixed Units: [F-LC25] [F-C30] [_________].

- Aluminum Extrusions: ASTM B 221, alloy and temper recommended by manufacturer for strength, corrosion resistance, and application of required finish, but not less than 0.064-inch thickness at any location for main frame and sash members.

**************************************************************************************************************** Retain first subparagraph below if required to minimize condensation in cold climates.
****************************************************************************************************************

  - Thermally Improved Construction: Fabricate window units with an integral, concealed, low-conductance thermal barrier; located between exterior materials and window members exposed on interior side; in a manner that eliminates direct metal-to-metal contact.

**************************************************************************************************************** Retain first subparagraph below if required.
****************************************************************************************************************

- Mullions: Between adjacent windows, fabricated of extruded aluminum matching finish of window units.

- Fasteners: Anchors, and Clips: Nonmagnetic stainless steel, aluminum, or other noncorrosive material, compatible with aluminum window members, trim, hardware, anchors, and other components of window units. Fasteners shall not be exposed, except for attaching hardware.

  - Reinforcement: Where fasteners screw-anchor into aluminum less than 0.128 inch thick, reinforce interior with aluminum or nonmagnetic stainless steel to receive screw threads, or provide standard, noncorrosive, pressed-in, spline grommet nuts.

- Hardware: Manufacturer’s standard; of aluminum, stainless steel, die-cast steel, malleable iron, or bronze; including the following:

**************************************************************************************************************** Retain applicable hardware types from list below.
****************************************************************************************************************

  - Cam-action sweep sash lock and keeper at meeting rails.

  - Spring-loaded, snap-type lock and jambs.

  - Pole-operated, cam-action locking device on meeting rail where rail is more than 72 inches above floor.

  - Lift handles for single-hung units.

  - Nylon sash rollers for horizontal-sliding units.

  - Steel or bronze operating arms.

**************************************************************************************************************** Retain two subparagraphs below for horizontal-sliding and single-hung units.
****************************************************************************************************************

- Sliding-Type Weather Stripping: Woven-pile weather stripping of wool, polypropylene, or nylon pile and resin-impregnated backing fabric; complying with AAMA 701/702.

- Insect Screens: Provide removable insect screen on each operable exterior sash, with screen frame finished to match window unit, and as follows:

**************************************************************************************************************** Retain one of three subparagraphs below.
****************************************************************************************************************

  - Aluminum Wire Fabric: 18-by-18, 18-by-16 or 18-by-14 mesh of 0.013-inch-diameter, coated aluminum wire; complying with FS RR-W-365, Type VII.

  - Glass-Fiber Mesh Fabric: 18-by-16 or 18-by-14 mesh of PVC-coated, glass-fiber threads, woven and fused to form a fabric mesh; complying with ASTM D 3656.

  - Fabric: Manufacturer’s standard aluminum wire fabric or glass-fiber mesh fabric.]

****************************************************************************************************************

If needed, insert requirements for steel windows. Aluminum windows are most common with manufacturers.

Retain one of first two paragraphs below.

****************************************************************************************************************

[C.	Glazing: Comply with requirements specified in Section 08 8000, Glazing]

[C.	Glazing:

**************************************************************************************************************** Retain one or more types of glass from first six subparagraphs below. Materials are standard with Metal Building System manufacturers. If retaining more than one, indicate location of each on Drawings.
****************************************************************************************************************

- Float Glass: ASTM C 1036, Type I, Quality-Q3, Class I (clear), 3 mm thick.

- Heat-Treated Float Glass: ASTM C 1048, Type I, Quality-Q3, Class I (clear), Condition A, 3 mm thick.

- Tinted Float Glass: ASTM C 1036, Type I, Quality-Q3, Class 2, 3 mm thick.

- Patterned Glass: ASTM C 1036, Type II, Quality-Q6, Class 1 (clear), Form 3, Pattern P3 (random), 3 mm thick.

- Insulating-Glass Units: Factory-assembled units consisting of sealed lites of 2.5-mm-thick clear float glass separated by a dehydrated interspace, qualified according to ASTM E 2190.

- Safety Glass: Category II materials complying with testing requirements in 16 CFR 1201.

**************************************************************************************************************** Retain first subparagraph below if required.
****************************************************************************************************************

- Provide safety glazing labeling.

- Glazing Stops: Screw-applied or snap-on glazing stops coordinated with Section 08 8000, Glazing and with glazing system indicated. Match material and finish of window frames.

**************************************************************************************************************** Retain subparagraph below unless preglazing is impractical. Occasionally, anchorage system will not permit preglazing.
****************************************************************************************************************

- Factory-Glazed Fabrication: Glaze window units in the factory to greatest extent possible and practical for applications indicated. Comply with requirements in Section 08 8000, Glazing]

- Finish:

- Mill finish.

- Baked-Enamel Finish: Organic Coating: Thermosetting, modified-acrylic enamel primer/topcoat system complying with AAMA 2603 except with a minimum dry film thickness of 0.7 mil, medium gloss.

  - Color: [As indicated by manufacturer’s designations] [As selected from manufacturer’s full range] [_________________].

- ACCESSORIES

**************************************************************************************************************** This article includes Metal Building System manufacturers’ standard accessories. Retain accessories required to suit Project. If more stringent requirements are needed for some accessories, revise descriptions.
****************************************************************************************************************

- General: Provide accessories as standard with Metal Building System manufacturer and as specified. Fabricate and finish accessories at the factory to greatest extent possible, by manufacturer’s standard procedures and processes. Comply with indicated profiles and with dimensional and structural requirements.

  - Form exposed sheet metal accessories that are without excessive oil-canning, buckling, and tool marks and that are true to line and levels indicated, with exposed edges folded back to form hems.0

- Roof Panel Accessories: Provide components required for a complete metal roof panel assembly including copings, fasciae, corner units, ridge closures, clips, sealants, gaskets, fillers, closure strips, and similar items. Match material and finish of metal roof panels unless otherwise indicated.

  - Closures: Provide closures at eaves and ridges, fabricated of same material as metal roof panels.

  - Clips: Manufacturer’s standard, formed from [steel] [stainless-steel] sheet, designed to withstand negative-load requirements.

  - Cleats: Manufacturer’s standard, mechanically seamed cleats formed from [steel] [stainless-steel sheet or nylon-coated aluminum] sheet.

**************************************************************************************************************** Retain first two subparagraphs below only with standing-seam metal roof panels. 
****************************************************************************************************************

- Wall Panel Accessories: Provide components required for a complete metal wall panel assembly including copings, fasciae, mullions, sills, corner units, clips, sealants, gaskets, fillers, closure strips, and similar items. Match material and finish of metal wall panels unless otherwise indicated.

  - Closures: Provide closures at eaves and rakes, fabricated of same material as metal wall panels.

****************************************************************************************************************Retain first subparagraph below if required; some manufacturers do not provide backing plates for wall panels.
****************************************************************************************************************

  - Backing Plates: Provide metal backing plates at panel end splices, fabricated from material recommended by manufacturer.

  - Closure Strips: Closed-cell, expanded, cellular, rubber or crosslinked, polyolefin-foam or closed-cell laminated polyethylene; minimum 1-inch- thick, flexible closure strips; cut or premolded to match metal wall panel profile. Provide closure strips where indicated or necessary to ensure weathertight construction.

- Flashing and Trim: Formed from 0.022-inch nominal-thickness, metallic-coated steel sheet or aluminum-zinc alloy-coated steel sheet prepainted with coil coating; finished to match adjacent metal panels.

  - Provide flashing and trim as required to seal against weather and to provide finished appearance. Locations include, but are not limited to, eaves, rakes, corners, bases, framed openings, ridges, fasciae, and fillers.

**************************************************************************************************************** Retain second option in subparagraph below if head and jambs of doors are subject to excessive impact. Painted subframing is often more durable. Metal thickness options correspond to obsolete 26 and 22 gage, respectively. 
****************************************************************************************************************

  - Opening Trim: Formed from [0.022-inch] [0.034-inch] nominal-thickness, metallic-coated steel sheet or aluminum-zinc ally-coated steel sheet prepainted with coil coating. Trim head and jamb of door openings, and head, jamb, and sill of other openings.

- Gutters: Formed from 0.022-inch nominal-thickness, metallic-coated steel sheet or aluminum-zinc alloy-coated steel sheet prepainted with coil coating; finished to match roof fascia and rake trim. Match profile of gable trim, complete with end pieces, outlet tubes, and other special pieces as required. Fabricate in minimum 96-inch-long sections, sized according to SMACNA’s “Architectural Sheet Metal Manual.”

  - Gutter Supports: Fabricated from same material and finish as gutters.

  - Strainers: Bronze, copper, or aluminum wire ball type at outlets.

- Downspouts: Formed from 0.022-inch nominal-thickness, zinc-coated (galvanized) steel sheet or aluminum-zinc alloy-coated steel sheet prepainted with coil coating; finished to match metal wall panels. Fabricate in minimum 10-foot-long sections, complete with formed elbows and offsets.

  - Mounting Straps: Fabricated from same material and finish as gutters.

- Roof Ventilators: Gravity type, complete with hardware, flashing, closures, and fittings.

**************************************************************************************************************** Retain one of two subparagraphs below for type.
****************************************************************************************************************

  - Circular-Revolving Type:  Minimum [20-inch-] [________-] diameter throat opening; fabricated from 0.028-inch nominal-thickness, metallic-coated steel sheet or aluminum-zinc alloy-coated steel sheet prepainted with coil coating; finished to match metal roof panels; with matching base and rain cap.

    - Type: [Directional] [Stationary] revolving.

    - Bird Screening: Galvanized steel, ½-inch square mesh, 0.041-inch wire; or aluminum, ½-inch-square mesh, 0.063-inch wire.

**************************************************************************************************************** Retain first subparagraphs below if required.
****************************************************************************************************************

    - Dampers: Spring-loaded, butterfly type; pull-chain operation; with pull chain of length required to reach within 36 inches of floor.

    - Reinforce and brace units, with joints properly formed and edges beaded to be watertight under normal positive-pressure conditions.

    - Mount ventilators on square-to-round bases for ridge or on-slope mounting, designed to match roof pitch and roll formed to match metal roof panel profile.

  - Continuous or Sectional-Ridge Type: Factory-engineered and –fabricated, continuous unit; fabricated from 0.022-inch nominal-thickness, metallic-coated steel sheet or aluminum-zinc alloy-coated steel sheet prepainted with coil coating; finished to match metal roof panels. Fabricated in minimum 10-foot-long sections. Provide throat size and total length indicated, complete with side baffles, ventilator assembly, end caps, splice plates, and reinforcing diaphragms.

    - Bird Screening: Galvanized steel, ½-inch-square mesh, 0.041-inch wire; or aluminum, ½- inch-square mesh, 0.063-inch wire.

**************************************************************************************************************** Retain first subparagraph below if required.
****************************************************************************************************************

    - Dampers: Manually operated, spring-loaded, vertically rising type; chain and worm gear operator; with pull chain of length required to reach within 36 inches of floor.

    - Throat Size: [9 inches] [12 inches] [9 or 12 inches, as standard with manufacturer, and as required to comply with ventilation requirements].

**************************************************************************************************************** Retain first paragraph below if louvers are not specified in Section 08 9100, Louvers. Manufacturers’ standard sizes are typically 3 by 3 feet, 3 by 4 feet, and 4 by 4 feet. Verify availability with manufacturers.
****************************************************************************************************************

- Louvers: Size and design indicated; self-framing and self-flashing. Fabricate welded frames from minimum 0.052-inch nominal-thickness, metallic-coated steel sheet; finished to match metal wall panels. Form blades from 0.040-inch nominal-thickness, metallic-coated steel sheet; folded or beaded at edges, set at an angle that excludes driving rains, and secured to frames by riveting or welding. Fabricate louvers with equal blade spacing to produce uniform appearance.

  - Structural Design: Louvers shall be designed by their manufacturer to withstand the wind loads specified in paragraph “Wind Loads” in Part 1 (i.e., for ASCE 7 Components and Cladding).

************************************************************************************************************** Retain one of two “Blades” subparagraphs below. If retaining both, indicate location of each on Drawings.
***************************************************************************************************************

  - Blades: Fixed.

  - Blades: Adjustable type, with weather-stripped edges, and manually operated by hand crank or pull chain.

  - Free Area: Not less than [7.0 sq. ft.] [________] for 48-inch-wide by 48-inch-high louver.

  - Bird Screening: Galvanized steel, ½-inch-square mesh, 0.041-inch wire; with rewirable frames, removable and secured with clips; fabricated of same kind and form of metal and with same finish as louvers.

**************************************************************************************************************** In first subparagraph below, interior mounting is for interior face of fixed louvers; exterior mounting is for exterior or interior face of adjustable louvers.
****************************************************************************************************************

    - Mounting: [Interior] [Exterior] face of louvers.

    - Vertical Mullions: Provide mullions at spacings recommended by manufacturer, or 72 inches o.c., whichever is less.

**************************************************************************************************************** Retain first paragraphs below if roof curbs are not specified in Section 07 7100, Roof Specialties. Not all manufacturers provide roof curbs; verify availability.
****************************************************************************************************************

- Roof Curbs: Fabricated from minimum 0.052-inch nominal-thickness, metallic-coated steel sheet or aluminum-zinc alloy-coated steel sheet prepainted with coil coating; finished to match metal roof panels; with welded top box and bottom skirt, and integral full-length cricket; capable of withstanding loads of size and height indicated.

  - Curbs shall accommodate the expansion and contraction movement of standing seam roofs.

  - Curb Subframing: Fabricated from 0.064-inch nominal-thickness, angle-, C-, or Z-shaped metallic-coated steel sheet.

**************************************************************************************************************** Retain subparagraph below if required.
****************************************************************************************************************

  - Insulation: 1-inch-thick, rigid type.

**************************************************************************************************************** Service walkways are not available from all manufacturers.
****************************************************************************************************************

- Service Walkways: Fabricated from 0.052-inch nominal-thickness, metallic-coated steel plank grating; with slip-resistant pattern; [18-inch] [24-inch] [36-inch] overall width. Support walkways on framing system anchored to metal roof panels without penetrating panels; with predrilled holes and clamps or hooks for anchoring.

**************************************************************************************************************** Pipe flashing in first paragraph below is not designed for high-temperature applications.
****************************************************************************************************************

- Pipe Flashing: Premolded, EPDM pipe collar with flexible aluminum ring bonded to base.

- Fasteners:

  - Fasteners: Self-tapping screws, bolts, nuts, self-locking rivets and bolts, end-welded studs, and other suitable fasteners designed to withstand design loads. Provide fasteners with heads matching color of materials being fastened by means of plastic caps or factory-applied coating.

**************************************************************************************************************** Retain one of first two subparagraphs below. Stainless-steel fasteners in second subparagraph provide additional corrosion resistance.
****************************************************************************************************************

    - Fasteners for Metal Roof Panels: Self-drilling of self-tapping, zinc-plated, hex-head carbon-steel screws, with a stainless-steel cap or zinc-aluminum-alloy head and EPDM sealing washer.

    - Fasteners for Metal Roof Panels: Self-drilling, Type 410 stainless-steel or self-tapping, Type 304 stainless-steel or zinc-alloy-steel hex washer head, with EPDM washer under heads of fasteners bearing on weather side of metal panels.

**************************************************************************************************************** Retain one of first two subparagraphs below. Stainless-steel fasteners in second subparagraph provide additional corrosion resistance. Retain washers if required; washers are usually omitted from wall panels.
****************************************************************************************************************

    - Fasteners for Metal Wall Panels: Self-drilling or self-tapping, zinc-plated, hex-head carbon-steel screws [, with EPDM sealing washers bearing on weather side of metal panels].

    - Fasteners for Metal Wall Panels: Self-drilling, Type 410 stainless-steel or self-tapping, Type 304 stainless-steel or zinc-alloy-steel hex washer head [, with EPDM sealing washers bearing on weather side of metal panels].

    - Fasteners for Flashing and Trim: Blind fasteners or self-drilling screws with hex washer head.

    - Blind Fasteners: High-strength aluminum or stainless-steel rivets.

- Corrosion-Resistant Coating: Cold-applied asphalt mastic, compounded for 15-mil dry film thickness per coat. Provide inert-type noncorrosive compound free of asbestos fibers, sulfur components, and other deleterious impurities.

**************************************************************************************************************** Non-shrink grout in the following paragraph is primarily for setting base plates.
****************************************************************************************************************

- Nonmetallic, Shrinkage-Resistant Grout: ASTM C 1107, factory-packaged, nonmetallic aggregate grout, noncorrosive, nonstaining, mixed with water to consistency suitable for application and a 30-minute working time, and capable of developing minimum compressive strength of [2,400] [________] psi in 48 hours and [7,000] [________] psi in 28 days manufactured by [________________________].

- Metal Panel Sealants:

**************************************************************************************************************** Retain first subparagraph below if rated wall construction, units requiring internal boards for structural stability or acoustical ratings, or thermal barrier for board insulation is required.
****************************************************************************************************************

  - Sealant Type: Pressure-sensitive, 100 percent solids, gray polyisobutylene-compound sealant tape with release-paper backing. Provide permanently elastic, nonsag, nontoxic, nonstaining tape of manufacturer’s standard size.

  - Joint Sealant: ASTM C 920; one-part elastomeric; polyurethane or polysulfide; of type, grade, class, and use classifications required to seal joints in metal panels and remain weathertight; and as recommended by metal building system manufacturer.

  - DESIGN COMPONENTS AND FIELD CONNECTIONS

- General: Design components and field connections required for erection to permit easy assembly.

  - Mark each piece and part of the assembly to correspond with previously prepared erection drawings, diagrams, and instruction manuals.

  - Fabricate structural framing to produce clean, smooth cuts and bends. Punch holes of proper size, shape, and location. Members shall be free of cracks, tears, and ruptures.

- Tolerances: Comply with MBMA for fabrication and erection tolerances.

- Primary Framing: Shop-fabricate framing components to indicated size and section, with baseplates, bearing plates, stiffeners, and other items required for erection welded into place. Cut, form, punch, drill, and weld framing for bolted field assembly.

  - Make shop connections by welding or by using high-strength bolts.

  - Join flanges to webs of built-up members by a continuous, submerged arc-welded process.

  - Brace compression flange of primary framing with steel angles or cold-formed structural tubing between frame web and purlin web or girt web, so flange compressive strength is within allowable limits for any combination of loadings.

**************************************************************************************************************** Revise first subparagraph below if other types of attachment are permitted. Welded clips on roof rafters may not be allowed by LANL.
****************************************************************************************************************

  - Weld clips to frames for attaching secondary framing.

  - Shop Priming: Prepare surfaces for shop priming according to SSPC SP-2. Shop prime primary framing with specified primer after fabrication.

- Secondary Framing: Shop fabricate framing components to indicated size and section by roll-forming to break-forming, with baseplates, bearing plates, stiffeners, and other plates required for erection welded into place. Cut, form, punch, drill, and weld secondary framing for bolted field connections to primary framing.

  - Make shop connections by welding or by using non-high-strength bolts.

  - Shop Priming: Prepare uncoated surfaces for shop priming according to SSPC SP-2. Shop prime uncoated secondary framing with specified primer after fabrication.

- Metal Panels: Fabricate and finish metal panels at the factory to greatest extent possible, by manufacturer’s standard procedures and processes, as necessary to fulfill indicated performance requirements. Comply with indicated profiles and with dimensional and structural requirements.

  - Provide panel profile, including major ribs and intermediate stiffening ribs, if any, for full length of metal panel.

  - SOURCE QUALITY CONTROL

**************************************************************************************************************** Note that any / all testing and inspection requirements associated with the Metal Building System’s seismic-force-resisting system(s) will be stipulated in the Project’s Test and Inspection Plan (ref. article “Delegated Design Submittals,” paragraph “Statement of Structural Tests and Special Inspections).
****************************************************************************************************************

- Testing: Test and inspect shop connections for Metal Buildings according to the following:

**************************************************************************************************************** Pertaining to first subparagraph below, RCSC prescribes inspection for snug-tightened joints, and testing and inspection for each method of pretensioning joints, so consult the RCSC Specification in order to appropriately edit the subparagraph.
****************************************************************************************************************

  - Bolted Connections: Shop-bolted connections shall be [tested and] inspected according to RCSC.

  - Welded Connections: In addition to visual inspection, shop-welded connections shall be tested and inspected according to AWS D1.1 and the following inspection procedures, as required by the Engineer of Record:

**************************************************************************************************************** Retain applicable nondestructive testing methods in four subparagraphs below. Revise to indicate extent of weld inspections if applicable and to insert alternative acceptance criteria to AWS D1.1 if required.
****************************************************************************************************************

    - Liquid Penetrant Inspection: ASTM E 165.

    - Magnetic Particle Inspection: ASTM E 709; performed on root pass and on finished weld. Cracks or zones of incomplete fusion or penetration will not be accepted.

    - Ultrasonic Inspection: ASTM E 164.

    - Radiographic Inspection: ASTM E 94.

**************************************************************************************************************** See Section 01 4000, Quality Requirements for retesting and re-inspecting requirements.
****************************************************************************************************************

- Product will be considered defective if it does not pass tests and inspections.

- Prepare test and inspection reports.

EXECUTION

EXAMINATION

Field Measurements:

Metal Building subcontractor [_____] shall verify the field measurements are as indicated [in subcontract] [on erection drawings].] [instructed by the Manufacturer.]

Examine substrates, areas, and conditions, with erector present, for compliance with requirements for installation tolerances and other conditions affecting performance of the Work.

Verify foundation, floor slab, mechanical and electrical utilities, and placed anchors are in correct position.

Before erection proceeds survey elevations and locations of concrete- and masonry- bearing surfaces and locations of anchor rods, bearing plates, and other embedments to receive structural framing, with erector present, for compliance with requirements and Metal Building System manufacturer’s tolerances.

[Engage land surveyor to perform surveying.]

Proceed with erection only after unsatisfactory conditions have been corrected.

PREPARATION

Clean and prepare surfaces to be painted according to manufacturer’s written instructions for each particular substrate condition.

Provide temporary shores, guys, braces, and other supports during erection to keep structural framing secure, plumb, and in alignment against temporary construction loads and loads equal in intensity to design loads. Remove temporary supports when permanent structural framing, connections, and bracing are in place unless otherwise indicated.

Bracing furnished by the manufacturer for the Metal Building System cannot be assumed to be adequate during erection and are not to be used to pull frames into plumb condition.

ERECTION OF STRUCTURAL FRAMING

Erect metal building system according to manufacturer’s written erection instructions and erection drawings.

Use templates for accurate setting of anchor rods.

Ream holes requiring enlargement to admit bolts. Burned holes for bolted connections are not permitted without written approval by the Metal Building System manufacturer’s professional engineer.

Do not field cut, drill, or alter structural members without written approval from metal building system manufacturer’s professional engineer.

Set structural framing accurately in locations and to elevations indicated, according to AISC specifications referenced in this Section. Maintain structural stability of frame during erection.

**************************************************************************************************************** Insert leveling plates in first paragraph below if required.
****************************************************************************************************************

Base [and Bearing] Plates: Clean concrete- ad masonry-bearing surfaces of bond-reducing materials, and roughen surfaces prior to setting plates. Clean bottom surface of plates.

Set plates for structural members of wedges, shims, or setting nuts as required.

Tighten anchor rods after supported members have been positioned and plumbed. Do not remove wedges or shims but, if protruding, cut off flush with edge of plate before packing with grout.

Promptly pack grout solidly between bearing surfaces and plates so no voids remain. Neatly finish exposed surfaces; protect grout and allow to cure. Comply with manufacturer’s written installation instructions for shrinkage-resistant grouts.

Align and adjust structural framing before permanently fastening. Before assembly, clean bearing surfaces and other surfaces that will be in permanent contact with framing. Perform necessary adjustments to compensate for discrepancies in elevations and alignment.

Level and plumb individual members of structure.

Make allowances for difference between temperature at time of erection and mean temperature when structure will be completed and in service.

Primary Framing and End Walls: Erect framing level, plumb, rigid, secure, and true to line. Level baseplates to a true even plane with full bearing to supporting structures, set with double-nutted anchor bolts. Use grout to obtain uniform bearing and to maintain a level base-line elevation. Moist-cure grout for not less than seven days after placement.

Make field connections using high-strength bolts installed according to RCSC for bolt type and joint type specified.

Joint Type: [Snug tightened] [and] [Pretensioned] [and] [Slip-Critical].

Secondary Framing: Erect framing level, plumb, rigid, secure, and true to line. Field bolt secondary framing to clips attached to primary framing as required to satisfy design loads and as shown on Drawings.

Provide rake or gable purlins with tight-fitting closure channels and fasciae.

Locate and space wall girts to suit openings such as doors and windows.

**************************************************************************************************************** Retain first subparagraph below if canopies are required.
****************************************************************************************************************

Locate canopy framing as indicated.

Provide supplemental framing at entire perimeter of openings, including doors, windows, louvers, ventilators, and other penetrations of roof and walls.

**************************************************************************************************************** Retain first paragraph below if steel joist purlins are required; otherwise, delete.
****************************************************************************************************************

Steel Joists [and Joist Girders]: Install joists [, girders,] and accessories plumb, square, and true to line; securely fasten to supporting construction according to SJI, joist manufacturer’s written instructions, and requirements in this Section.

Before installation, splice joists delivered to Project site in more than one piece.

Space, adjust, and align joists accurately in location before permanently fastening.

Install temporary bracing and erection bridging, connections, and anchors to ensure that joists are stabilized during construction.

**************************************************************************************************************** Retain one of first two subparagraphs below.
****************************************************************************************************************

Bolt joists to supporting steel framework using carbon-steel bolts unless otherwise indicated.

Bolt joists to supporting steel framework using high-strength structural bolts unless otherwise indicated. Comply with RCSC for high-strength structural bold installation requirements.

Install and connect bridging concurrently with joist erection, before construction loads are applied. Anchor ends of bridging lines at top and bottom chords if terminating at walls or beams.

Bracing: Install bracing in roof and sidewalls where indicated on erection drawings:

Tighten rod and cable bracing to avoid sag.

Locate interior end-bay bracing only where indicated.

Framing for Openings: Provide shapes of proper design and size to reinforce openings and to carry loads and vibrations imposed, including equipment furnished under mechanical and electrical work. Securely attach to structural framing.

Erection Tolerances: Maintain erection tolerances of structural framing within those permitted by MBMA.

METAL PANEL INSTALLATION, GENERAL

Examination: Examine primary and secondary framing to verify that structural-panel support members and anchorages have been installed within alignment tolerances required by manufacturer.

Examine roughing-in for components and systems penetrating metal panels, to verify actual locations of penetrations relative to seams before metal panel installation.

General: Anchor metal panels and other components of the Work securely in place, aligned level and plumb, with provisions for thermal and structural movement [where indicated on Drawings].

Field cut metal panels as required for doors, windows, and other openings. Cut openings as small as possible, neatly to size required, and without damage to adjacent metal panel finishes.

Field cutting of metal panels by torch is not permitted unless approved in writing by manufacturer.

Exercise care when cutting prefinished material to ensure cuttings do not remain on finish surface.

Install metal panels perpendicular to structural supports unless otherwise indicated.

Flash and seal metal panels with weather closures at perimeter of openings and similar elements. Fasten with self-tapping screws.

Locate and space fastenings in uniform vertical and horizontal alignment.

Locate metal panel splices over, but not attached to, structural supports with end laps in alignment.

Lap metal flashing over metal panels to allow moisture to run over and off the material.

Lap-Seam Metal Panels: Install screw fasteners using power tools with controlled torque adjusted to compress EPDM washers tightly without damage to washers, screw threads, or metal panels. Install screws in predrilled holes.

Arrange and nest side-lap joints so prevailing winds blow over, not into, lapped joints. Lap ribbed or fluted sheets one full rib corrugation. Apply metal panels and associated items for neat and weathertight enclosure. Avoid “panel creep” or application not true to line.

Metal Protection: Where dissimilar metals contact each other or corrosive substrates, protect against galvanic action by painting contact surfaces with corrosion-resistant coating, by applying rubberized-asphalt underlayment to each contact surface, or by other permanent separations as recommended by metal roof panel manufacturer.

Joint Sealers: Install gaskets, joint fillers, and sealants where indicated and where required for weatherproof performance of metal panel assemblies. Provide types of gaskets, fillers, and sealants indicated; or, if not indicated, provide types recommended by metal panel manufacturer.

Seal metal panel end laps with double beads of tape or sealant the full width of panel. Seal side joints where recommended by metal panel manufacturer.

**************************************************************************************************************** Retain subparagraph below if joint-sealant work is part of this Section.
****************************************************************************************************************

Prepare joints and apply sealants to comply with requirements per Section 07 9200, Joint Sealants.

METAL ROOF PANEL INSTALLATION

General: Provide metal roof panels of full length from eave to ridge unless otherwise indicated or restricted by shipping limitations.

Install ridge [and hip] caps as metal roof panel work proceeds.

Flash and seal metal roof panels with weather closures at eaves and rakes. Fasten with self-tapping screws.

Standing Seam Metal Roof Panels: Fasten metal roof panels to supports with concealed clips at each standing-seam joint, at location and spacing and with fasteners recommended by manufacturer.

Install clips to supports with self-drilling or self-tapping fasteners.

Install pressure plates at locations indicated in manufacturer’s written installation instructions.

**************************************************************************************************************** Retain one of first two subparagraphs below: coordinate with products selected in Part 2.
****************************************************************************************************************

Snap Joint: Nest standing seams and fasten together by interlocking and completely engaging factory-applied sealant.

Seamed Joint: Crimp standing seams with manufacturer-approved motorized seamer tool so that clip, metal roof panel, and factory-applied sealant are completely engaged.

Rigidly fasten eave end of metal roof panels and allow ridge end free movement due to thermal expansion and contraction. Predrill panels for fasteners.

Provide metal closures at [peaks] [rake edges] [rake walls] [and] each side of ridge [and hip] caps.

Lap-Seam Metal Roof Panels: Fasten metal roof panels to supports with exposed fasteners at each lapped joint, at location and spacing recommended by manufacturer.

Provide metal-backed sealing washers under heads of exposed fasteners bearing on weather side of metal roof panels.

Provide sealant tape at lapped joints of metal roof panels and between panels and protruding equipment, vents, and accessories.

Apply a continuous ribbon of sealant tape to weather-side surface of fastenings on end laps and on side laps of nesting-type metal panels, on side laps of ribbed or fluted metal panels, and elsewhere as needed to make metal panels weatherproof to driving rains.

At metal panel splices, nest panels with minimum 6-inch end lap, sealed with butyl-rubber sealant and fastened together by interlocking clamping plates.

Metal Fascia Panels: Align bottom of metal panels and fasten with blind rivets, bolts, or self-drilling or self-tapping screws. Flash and seal metal panels with weather closures where fasciae meet soffits, along lower panel edges, and at perimeter of all openings.

****************************************************************************************************************

Generally retain paragraph below only for highly finished metal roof panel assemblies.

****************************************************************************************************************

Metal Roof Panel Installation Tolerances: Shim and align metal roof panels within installed tolerance of ¼ inch in 20 feet on slope and location lines as indicated and within 1/8-inch offset of adjoining faces and of alignment of matching profiles.

METAL WALL PANEL INSTALLATION

General: Install metal wall panels in orientation, sizes, and locations indicated on Drawings. Install panels perpendicular to girts, extending full height of building, unless otherwise indicated. Anchor metal wall panels and other components of the Work securely in place, with provisions for thermal and structural movement.

Unless otherwise indicated, begin metal panel installation at corners with center of rib lined up with line of framing.

Shim or otherwise plumb substrates receiving metal wall panels.

When two rows of metal panels are required, lap panels 4 inches minimum.

When building height requires two rows of metal panels at gable ends, align lap of gable panels over metal wall panels at eave height.

Rigidly fasten base end of metal wall panels and allow eave end free movement due to thermal expansion and contraction. Predrill panels.

Flash and seal metal wall panels with weather closures at eaves, rakes, and at perimeter of all openings. Fasten with self-tapping screws.

Install screw fasteners in predrilled holes.

Install flashing and trim as metal wall panel work proceeds.

Apply elastomeric sealant continuously between metal base channel (sill angle) and concrete, and elsewhere as indicated; or, if not indicated, as necessary for waterproofing.

Align bottom of metal wall panels and fasten with blind rivets, bolts, or self-drilling of self-tapping screws.

Provide weatherproof escutcheons for pipe and conduit penetrating exterior walls.

Metal Wall Panels: Install metal wall panels on exterior side of girts. Attach metal wall panels to supports with fasteners as recommended by manufacturer.

Insulated Metal Wall Panels: Install insulated metal wall panels on exterior side of girts. Attach panels to supports at each panel joint using concealed clip and fasteners at maximum 42 inches o.c., spaced not more than manufacturer’s recommendation. Fully engage tongue and groove of adjacent insulated metal wall panels.

Install clips to supports with self-tapping fasteners.

Apply continuous ribbon of sealant to panel joint on concealed side of insulated metal wall panels as vapor seal; apply sealant to panel joint on exposed side of panels as weather seal.

**************************************************************************************************************** Retain paragraph below only for highly finished metal wall panel assemblies.
****************************************************************************************************************

Installation Tolerances: Shim and align metal wall panels within installed tolerance of ¼ inch in 20 feet, nonaccumulative, on level, plumb, and on location lines as indicated, and within 1/8-inch offset of adjoining faces and of alignment of matching profiles.

TRANSLUCENT PANEL INSTALLATION

Translucent Panels: Attach translucent panels to structural framing with fasteners according to manufacturer’s written instructions. Install panels perpendicular to supports unless otherwise indicated. Anchor translucent panels securely in place, with provisions for thermal and structural movement.

Provide end laps of not less than 6 inches and side laps of not less than 1-1/2-inch corrugations for metal roof panels.

Provide end laps of not less than 6 inches and side laps of not less than 1-1/2-inch corrugations for metal roof panels.

Align horizontal laps with adjacent metal panels.

Seal intermediate end laps and side laps of translucent panels with translucent mastic.

Apply bituminous paint on aluminum surfaces of units in contact with dissimilar metals.

METAL SOFFIT PANEL INSTALLATION

Provide metal soffit panels of full width of soffits. Install panels perpendicular to support framing.

Flash and seal metal soffit panels with weather closures where panels meet walls and at perimeter of all openings.

THERMAL INSULATION INSTALLATION

****************************************************************************************************************

Retain this article if insulation is required; delete if using only factory-assembled, insulated metal panels.

****************************************************************************************************************

General: Install insulation concurrently with metal panel installation, in thickness indicated to cover entire surface, according to manufacturer’s written instructions.

**************************************************************************************************************** Retain first two subparagraphs below if units are furnished with vapor-retarder faces.
****************************************************************************************************************

Set vapor-retarder-faced units with vapor retarder toward warm side of construction unless otherwise indicated. Do not obstruct ventilation spaces except for firestopping.

Tape joints and ruptures in vapor retarder, and seal each continuous area of insulation to the surrounding construction to ensure airtight installation.

**************************************************************************************************************** Retain one of two subparagraphs below. First is for insulation with factory-installed facings; second is for field-installed facings.
****************************************************************************************************************

Install factory-laminated, vapor-retarder-faced blankets straight and true in one-piece lengths, with both sets of facing tabs sealed, to provide a complete vapor retarder.

Install blankets straight and true in one-piece lengths. Install vapor retarder over insulation, with both sets of facing tabs sealed, to provide a complete vapor retarder.

Blanket Roof Insulation: Comply with the following installation method:

**************************************************************************************************************** Retain one of first four subparagraphs below.

****************************************************************************************************************

Over-Framing Installation: Extend insulation and vapor retarder over and perpendicular to top flange of secondary framing. Hold in place by metal roof panels fastened to secondary framing.

****************************************************************************************************************

First subparagraph below accommodates thicker insulation with no compression at purlins; however, thermal bridging occurs through metal roof panels in direct contact with structure.

****************************************************************************************************************

Between-Purlin Installation: Extend insulation and vapor retarder between purlins. Carry vapor-retarder-facing tabs up and over purlin, overlapping adjoining facing of next insulation course and maintaining continuity of retarder. Hold in place with bands and crossbands below insulation.

****************************************************************************************************************

Thermal spacer blocks in first two subparagraphs below can retard heat transfer at purlins. Blocks are typically used with standing-seam systems attached to structural members by clips instead of lap-seam systems attached by screw fasteners.

First subparagraph below accommodates thicker insulation with compression occurring at structure.

****************************************************************************************************************

Over-Purlin-with-Spacer-Block Installation: Extend insulation and vapor retarder over and perpendicular to top flange of secondary framing. Install layer of filler insulation over first layer to fill space formed by metal roof panel standoffs. Hold in place by panels fastened to standoffs.

Thermal Spacer Blocks: Where metal roof panels attach directly to purlins, install thermal spacer blocks.

****************************************************************************************************************

First subparagraph below accommodates thicker insulation with no compression.

****************************************************************************************************************

Two-Layers-between-Purlin-with-Spacer-Block Installation: Extend insulation and vapor retarder between purlins. Carry vapor-retarder-facing tabs up and over purlin, overlapping adjoining facing of next insulation course and maintaining continuity of retarder. Install layer of filler insulation over first layer to fill space between purlins formed by thermal spacer blocks. Hold in place with bands and crossbands below insulation.

Thermal Spacer Blocks: Where metal roof panels attach directly to purlins, install thermal spacer blocks.

Retainer Strips: Install retainer strips at each longitudinal insulation joint, straight and taut, nesting with secondary framing to hold insulation in place.

****************************************************************************************************************

Retain one of two paragraphs below for walls.

****************************************************************************************************************

Blanket Wall Insulation: Extend insulation and vapor retarder over and perpendicular to top flange of secondary framing. Hold in place by metal wall panels fastened to secondary framing.

Retainer Strips: Install retainer strips at each longitudinal insulation joint, straight and taut, nesting with secondary framing to hold insulation in place.

Sound-Absorption Insulation: Where sound-absorption requirement is indicated or metal liner panels, cover insulation with polyethylene film and provide inserts of wire mesh to form acoustical spacer grid.

Board Wall Insulation: Extend board insulation in thickness indicated to cover entire wall. Hold in place by metal wall panels fastened to secondary framing. Comply with manufacturers’ written instructions.

Retainer Strips: Install retainer strips at each longitudinal insulation joint, straight and taut, nesting with secondary framing to hold insulation in place.

DOORS AND FRAME INSTALLATION

**************************************************************************************************************** Retain door types in this article that are specified in Part 2. 
****************************************************************************************************************

General: Install doors and frames plumb, rigid, properly aligned, and securely fastened in place according to manufacturers’ written instructions. Coordinate installation with wall flashings and other components. Seal perimeter of each door frame with elastomeric sealant used for metal wall panels.

Personnel Doors and Frames: Install doors and frames according to SDI A250.8. Fit non-fire-rated doors accurately in their respective frames, with the following clearances:

Between Doors and Frames at Jambs and Head: 1/8 inch.

Between Edges and Pairs of Doors: 1/8 inch.

At Door Sills with Threshold: 3/8 inch.

At Door Sills without Threshold: ¾ inch.

****************************************************************************************************************

Retain subparagraph below if required.

****************************************************************************************************************

At fire-rated openings, install frames according to, and doors with clearances specified in, NFPA 80.

**************************************************************************************************************** Retain first paragraph below if doors are not pre-glazed.
****************************************************************************************************************

WINDOW INSTALLATION

**************************************************************************************************************** Retain this article if windows are not specified in Section 08 5113, Aluminum Windows.
****************************************************************************************************************

General: Install windows plumb, rigid, properly aligned, without warp or rack of frames or sash, and securely fasten in place according to manufacturer’s written instructions. Coordinate installation with wall flashings and other components. Seal perimeter of each window frame with elastomeric sealant used for metal wall panels.

Separate dissimilar materials from sources of corrosion or electrolytic action at points of contact with other materials by complying with requirements specified in AAMA/WDMA/CSA 101/I.S.2/A440.

Set sill members in bed of sealant or with gaskets, as indicated, for weathertight construction.

Install windows and components to drain condensation, water penetrating joints, and moisture migrating within windows to the exterior.

Mount screens directly to frames with tapped screw clips.

**************************************************************************************************************** Retain paragraph below for windows not factory glazed.
****************************************************************************************************************

Field Glazing: Comply with installation requirements in Section 08 8000, Glazing.

ACCESSORY INSTALLATION

General:  Install accessories with positive anchorage to building and weathertight mounting, and provide for thermal expansion. Coordinate installation with flashings and other components.

Install components required for a complete metal roof panel assembly, including trim, copings, ridge closures, seams covers, flashings, sealants, gaskets, fillers, closure strips, and similar items.

Install components for a complete metal wall panel assembly, including trim, copings, corners, seam covers, flashings, sealants, gaskets, fillers, closure strips, and similar items.

Where dissimilar metals contact surfaces each other or corrosive substrates, protect against galvanic action by painting contact surfaces with corrosion-resistant coating, by applying rubberized-asphalt underlayment to each contact surface, or by other permanent separation as recommended by manufacturer.

Flashing and Trim: Comply with performance requirements, manufacturer’s written installation instructions, and SMACNA’s “Architectural Sheet Metal Manual.” Provide concealed fasteners where possible, and set units true to line and level as indicated. Install work with laps, joints, and seams that will be permanently watertight and weather resistant.

Install exposed flashing and trim that is without excessive oil-canning, buckling, and tool marks and that is true to line and level as indicated, with exposed edges folded back to form hems. Install sheet metal flashing and trim to fit substrates and to result in waterproof and weather-resistant performance.

Expansion Provisions: Provide for thermal expansion of exposed flashing and trim. Space movement joints at a maximum of 10 feet with no joints allowed within 24 inches of corner or intersection. Where lapped or bayonet-type expansion provisions cannot be used or  would not be sufficiently weather resistant and waterproof, form expansion joints of intermeshing hooked flanges, not less than 1 inch deep, filled with mastic sealant (concealed within joints).

Gutters: Join sections with riveted-and-soldered or lapped-and-sealed joints. Attach gutters to eave with gutter hangers spaced as required for gutter size, but not more than 36 inches o.c., using manufacturer’s standard fasteners. Provide end closures and seal watertight with sealant. Provide for thermal expansion.

Apply bituminous paint on surfaces in contact with cementitious materials.

Slope gutters minimum [________] inch/ft.

Downspouts: Join sections with 1-1/2-inch telescoping joints. Provide fasteners designed to hold downspouts securely 1 inch away from walls; locate fasteners at top and bottom and at approximately 60 inches o.c. in between.

Apply bituminous paint on surfaces in contact with cementitious materials.

**************************************************************************************************************** Retain one of two subparagraphs below. If retaining the first subparagraph, consider inclusion of splash pans / pads at base of downspout to help get water away from building.
****************************************************************************************************************

Provide elbows at base of downspouts to direct water away from building.

Install splash [pans] [pads] [________] under each downspout.

Tie downspouts to underground drainage system indicated.

Circular Roof Ventilators: Set ventilators complete with necessary hardware, anchors, dampers, weather guards, rain caps, and equipment supports. Mount ventilators on flat level base. Install preformed filler strips at base to seal ventilator to metal roof panels.

Continuous Roof Ventilators: Set ventilators complete with necessary hardware, anchors, dampers, weather guards, rain caps, and equipment supports. Join sections with splice plates and end-cap skirt assemblies where required to achieve indicated length. Install preformed filler strips at base to seal ventilator to metal roof panels.

Louvers: Locate and place louver units level, plumb, and at indicated alignment with adjacent work.

Use concealed anchorages where possible. Provide brass or lead washers fitted to screws where required to protect metal surfaces and to make a weathertight connection.

Provide perimeter reveals and openings of uniform width for sealants and joint fillers.

Protect galvanized- and nonferrous- metal surfaces from corrosion or galvanic action by applying a heavy coating of corrosion-resistant paint on surfaces that will be contact with concrete, masonry, or dissimilar metals.

Install concealed gaskets, flashings, joint fillers, and insulation as louver installation progresses, where weathertight louver joints are required. Comply with Section 07 9200, Joint Sealants for sealants applied during louver installation.

Roof Curbs: Install curbs at locations indicated on Drawings. Install flashing around bases where they meet metal roof panels.

Pipe Flashing: Form flashing around pipe penetration and metal roof panels. Fasten and seal to panel as recommended by manufacturer.

TOLERANCES

All work shall be performed by experienced workmen in a workmanlike manner to published tolerances.

FIELD QUALITY CONTROL

Access

Provide access to the Work as scheduled for LANL-provided inspections.

*************************************************************************************************************** Note that any / all testing and inspection requirements associated with the Metal Building System’s seismic-force-resisting system(s) will be stipulated in the Project’s Test and Inspection Plan (ref. article “Delegated Design Submittals,” paragraph “Statement of Structural Tests and Special Inspections).

Revise first paragraph below to describe tests and inspections to be performed.
****************************************************************************************************************

Tests and Inspections:

**************************************************************************************************************** Pertaining to first subparagraph below, RCSC prescribes inspection for snug-tightened joints, and testing and inspection for each method of pretensioning joints, so consult the RCSC Specification in order to appropriately edit the subparagraph.
****************************************************************************************************************

High-Strength, Field-Bolted Connections: Connections shall be [tested and] inspected during installation according to RCSC.

Per 01 4444 Off-Site Welding & Joining, 01 4495 On-Site Welding & Joining. Welded Connections: In addition to visual inspection, field-welded connections shall be tested and inspected according to AWS D1.1 and the following inspection procedures, as required by the Engineer of Record:

**************************************************************************************************************** Retain applicable nondestructive testing methods in four subparagraphs below. Revise to indicate extent of weld inspections if applicable and to insert alternative acceptance criteria to AWS D1.1 if required.
****************************************************************************************************************

Liquid Penetrant Inspection: ASTM E 165.

Magnetic Particle Inspection: ASTM E 709; performed on root pass and on finished weld. Cracks or zones of incomplete fusion or penetration will not be accepted.

Ultrasonic Inspection: ASTM E 164.

Radiographic Inspection: ASTM E 94.

**************************************************************************************************************** See Section 01 4000, Quality Requirements for retesting and re-inspecting requirements.
****************************************************************************************************************

Product will be considered defective if it does not pass tests and inspections.

Prepare test and Inspection reports.

ADJUSTING

Doors: After completing installation, test and adjust doors to operate easily, free of warp, twist, or distortion.

**************************************************************************************************************** Retain first paragraph below if windows are not fixed or if they are not specified in Section 08 5113, Aluminum Windows.
****************************************************************************************************************

Windows: Adjust operating sashes and ventilators, screens, hardware, and accessories for a tight fit at contact points and at weather stripping to ensure smooth operation and weathertight closure. Lubricate hardware and moving parts.

**************************************************************************************************************** Revise paragraph below if louvers are specified in Section 08 9100, Louvers.
****************************************************************************************************************

[Roof Ventilators] [and] [Adjustable Louvers]: After completing installation, including work by other trades, lubricate, test, and adjust units to operate easily and be free of warp, twist, or distortion as needed to provide fully functioning units.

**************************************************************************************************************** Retain subparagraph below for adjustable louvers.
****************************************************************************************************************

Adjust louver blades to be weathertight when in closed position.

CLEANING AND PROTECTION

***************************************************************************************

Retain first paragraph below if galvanized items are required.

***************************************************************************************

Repair damaged galvanized coatings on galvanized items with galvanized repair paint according to ASTM A 780 and manufacturer's written instructions.

Remove and replace glass that has been broken, chipped, cracked, abraded, or damaged during construction period.

***************************************************************************************

Retain one of first two paragraphs below.

***************************************************************************************

Touchup Painting:  After erection, promptly clean, prepare, and prime or reprime field connections, rust spots, and abraded surfaces of prime-painted structural framing [, bearing plates,] and accessories.

Clean and prepare surfaces by SSPC SP 2, or by SSPC SP 3.

Apply a compatible primer of same type as shop primer used on adjacent surfaces.

Touchup Painting:  Cleaning and touchup painting are specified in Section 09 9100, Painting.

Metal Panels:  Remove temporary protective coverings and strippable films, if any, as metal panels are installed.  On completion of metal panel installation, clean finished surfaces as recommended by metal panel manufacturer.  Maintain in a clean condition during construction.

Replace metal panels that have been damaged or have deteriorated beyond successful repair by finish touchup or similar minor repair procedures.

Doors and Frames:  Immediately after installation, sand rusted or damaged areas of prime coat until smooth and apply touchup of compatible air-drying primer.

Immediately before final inspection, remove protective wrappings from doors and frames.

****************************************************************************************************************

Retain first paragraph below if windows are not specified in Section 08 5113, Aluminum Windows.

****************************************************************************************************************

Windows:  Clean metal surfaces immediately after installing windows.  Avoid damaging protective coatings and finishes.  Remove excess sealants, glazing materials, dirt, and other substances.  Clean factory-glazed glass immediately after installing windows.

****************************************************************************************************************

Retain paragraph below if louvers are not specified in Section 08 9100, Louvers.

****************************************************************************************************************

Louvers:  Clean exposed surfaces that are not protected by temporary covering, to remove fingerprints and soil during construction period.  Do not let soil accumulate until final cleaning.

Restore louvers damaged during installation and construction period so no evidence remains of corrective work.  If results of restoration are unsuccessful, as determined by Architect, remove damaged units and replace with new units.

Touch up minor abrasions in finishes with air-dried coating that matches color and gloss of, and is compatible with, factory-applied finish coating.

END OF SECTION

****************************************************************************************************************

Do not delete the following reference information:

****************************************************************************************************************

THE FOLLOWING REFERENCE IS FOR LANL USE

This project specification is based on LANL Master Specification 13 3419 Rev. 3, dated February 25, 2014.