SECTION 21 1316

DRY-PIPE SPRINKLER SYSTEMS

*************************************************************************************************************

LANL MASTER SPECIFICATION

This template must be edited for each project.  In doing so, specifier must add job-specific requirements.  Brackets are used in the text to indicate designer choices or locations where text must be supplied by the designer.  Once the choice is made or text supplied, remove the brackets.  The specifications must also be edited to delete specification requirements for processes, items, or designs that are not included in the project -- and specifier’s notes such as these.  To seek a variance from requirements in the specifications that are applicable, contact the Engineering Standards Manual Fire POC. Please contact POC with suggestions for improvement as well.

When assembling a specification package, include applicable specifications from all Divisions, especially Division 1, General requirements.

Specification developed for ML-4 projects.  For ML-1, 2, and 3 applications, additional requirements and independent reviews should be added if increased confidence in procurement or execution is desired; see ESM Chapter 1 Section Z10 Specifications and Quality sections.

****************************************************************************************************

As a minimum, include the following specifications in bid package.

01 2500				Substitution Procedures

01 3300		Submittal Procedures

01 3545				Water Discharge Requirements

01 4219				Reference Standards

01 7700				Closeout Procedures

01 7839				Project Record Documents

09 9100				Painting

Div. 21				Applicable fire alarm system specifications

22 0554				Identification for Plumbing, HVAC, and Fire Piping and Equipment

22 0813				Testing Piping Systems

22 0816				Disinfection of Potable Water Piping

*************************************************************************************************************

GENERAL

SECTION INCLUDES

Scope of Work:  Provide design, shop drawings, project record drawings (as-built), equipment, fabrication, labor, transportation and supervision necessary to install, flush, test and place into service a complete hydraulically designed automatic dry pipe sprinkler system.

[Provide a detailed scope of work for existing fire sprinkler systems that are to be remodeled, revised, and/or extended.  Note the design parameters for the existing system]

Components:  The dry pipe fire sprinkler system shall consist of, but not be limited to, interconnecting piping, fittings, control valves, check valves, alarm valve with trim, air supply source and air pressure maintenance equipment, detection system, fire department connection, sprinkler heads, hangers, bracing, inspector's test stations, drains, sprinkler alarm and other devices for a complete installation in accordance with codes, standards and recommended practice referenced in this Section.

LANL PERFORMED WORK

The LANL Fire Protection Division will coordinate with the Los Alamos Fire Department to provide the subcontractor with water supply test data for existing fire protection water supplies.

The subcontractor is responsible for performing hydraulic calculations for the sprinkler system in accordance with NFPA 13 that account for all flow and pressure requirements to the location of the flow test hydrant that was used to determine the static and residual pressures.  The subcontractor is also responsible for determining the location and elevation of the static and residual test gauge relative to the riser reference point and providing this information on the sprinkler design plans in accordance with NFPA 13 (2010 edition, Sections 22.2.1 & 22.1.3(10)).

design

Design system in accordance with the most current edition of NFPA 13.  Modifications to existing systems involving less than 10 sprinklers may be designed in accordance with the Code of Record edition of NFPA 13.  Modifications involving 10 or more sprinklers shall comply with the current edition of NFPA 13.

At a minimum, design the system to an Ordinary Group II Hazard in accordance with NFPA 13 or as specified by the LANL Fire Marshal.  Provide a minimum 500-gpm hose allowance.

Conform to extra or special hazard requirements where required or indicated.

Conform to NFPA 13 for storage occupancies with potential storage height greater than 12 feet and other special hazard occupancies.

System to operate at 7500 feet altitude.

Provide necessary devices and system design to separate system into individual and distinct alarm zones.  Provide a minimum of one zone per floor.

*************************************************************************************************************

The following seismic design requirement applies to fire sprinkler systems located in PC-1 and PC-2 facilities.  Seismic design for sprinkler systems located in PC-3 facilities shall be done in accordance with ESM Chapter 5, Section III in lieu of the following requirement.
*************************************************************************************************************

Seismic Design. Design sprinkler system piping for protection against damage in accordance with NFPA 13-2010 (Section 9.3) subject to the following modifications:

In paragraph 9.3.1.2, replace the phrase “at least equal to” with the following:  greater than.

In paragraph 9.3.5.6.2, replace the phrase “where Cp is…intermediate values of Ss” with the following:  where Cp is 0.53

If paragraph 9.3.5.6.2.1 is used to determine the horizontal force, follow the guidance at the outset of Appendix E, para. E.3 (i.e., the text prior to the discussion of the simplification of ASCE / SEI 7 Fp), and use SDS = 0.75.

Given 2 (above), paragraph 9.3.5.6.3 is not applicable.

SUBMITTALS

Submit the following in accordance with project submittal procedures:

Hydraulic Calculations prepared in accordance with NFPA 13.  Submit calculations with shop drawings.

Provide a minimum 10% or 5 psi, whichever is greater, design safety factor between the calculated sprinkler flow and pressure demand and the design basis water supply curve.  The calculated sprinkler demand shall include a minimum 500 gpm hose stream allowance in accordance with LANL ESM Fire Chapter 2 D4010 (2.0B).

Include in calculations elevation differences between point of water test and base of riser.  Include graphical representation of design basis water supply curve and system demand.

The following preliminary flow data is provided to the Subcontractor for bidding purposes: static ______ psig, residual _____ psig, flow _____ gpm, hydrant number ____, hydrant elevation_______ feet.

Base system design on actual flow test information provided by LANL.  Request actual flow data in a timely manner to maintain project schedules.

Seismic Design Project Record Documents.  Provide the following:

- Calculations, prepared in accordance with LANL AP-341-605, that demonstrate compliance with 1.3.B.

- Drawings, prepared in accordance with the LANL Drafting Manual, that convey the design to the constructor.

- Test and Inspection Plan, prepared in accordance with LANL ESM Chapter 16, as necessary / applicable.

- Items 1-3 above shall be stamped and sealed by a PE licensed by New Mexico.

Catalog Data with selected options marked.

Certifications for welders in accordance with NFPA 13.

Installation Instructions

Materials Part List (Bill of Materials) with manufacturer, model number, and quantity.

Shop Drawings using a minimum scale of 1/8" = 1'0" for plans and 1/4" = 1'0" for details.  All lettering shall be a minimum of 1/8 inch high.

Show information required by NFPA 13, including piping, sprinklers, hangers, flexible couplings, roof construction, electro-mechanical devices, occupancy of each area, and ceiling and roof heights. See Chapter 22 of NFPA 13 for guidance on information required to be included on plans and calculations.

Base working plans on actual survey of existing conditions.

Show hydraulic reference points and remote areas.

Test Reports

Operation and Maintenance Manual:  Submit system description, system final inspection, and Subcontractor's material and test certificates per NFPA 13, of the completed system project record documents.

Include in operation and maintenance manuals, instructions, a brief description of type of system installed, routine maintenance work defined by step-by-step instructions, and recommended frequency of performance.

Also include in instructions, possible malfunctions with diagnostic methods and suggested correction of each.

Describe function of each component or subassembly.

List recommended spare parts (manufacture, model number, and quantity).

Project Record Drawings (as-builts) on CDs and prints reflecting as-built conditions showing Work completed under this Section.

Base as-built drawings on actual survey of the completed installation.

Include notes on all special systems or devices such as dry pendent heads, antifreeze loops and inspector's test stations.

Provide revised hydraulic calculations demonstrating water supply restrictions have not been exceeded when conditions of installation are different from those anticipated during preparation of Project Record Documents.

The project manager shall be responsible for submission of as-built plans and calculations to the LANL Records office in accordance with Section 01 7700 Closeout Procedures and Section 01 7839 Project Record Documents.

QUALITY ASSURANCE

Provide proof that installation firm has satisfactorily performed at least ten projects of equivalent nature and scope of the Projects herein; and is licensed within the USA to engage in design, fabrication and installation of automatic sprinkler systems for fire protection.

DELIVERY, STORAGE, AND HANDLING

Materials and Equipment: Protect materials and equipment from damage during shipping, storage and installation.

Plugs and Cover Plates: Protect threaded ends, flanged openings with gasketed metal cover plates to prevent damage during shipment and to prevent foreign materials from entering.  Cap or plug drains, vents, small piping, and gauge connections.

PRODUCTS

  - PRODUCT OPTIONS AND SUBSTITUTIONS

Alternate products may be accepted; follow Section 01 2500, Substitution Procedures.

MATERIALS

Provide new fire protection materials and equipment, UL Listed or FM Approved, conforming to requirements of NFPA 13.

PIPING AND FITTING MATERIALS

Provide in accordance with NFPA 13, except that piping 2 inches and smaller shall be Schedule 40 minimum.

VALVES AND STRAINERS

Provide Listed or Approved valves and strainers rated at 175 psi or greater working pressure.

Check Valves: In sizes 3 inch and larger, provide 3/4 inch NPT drainage taps.

Strainers: Provide "Y" type strainers with cast iron body and 30 mesh stainless steel screen that are listed for fire protection service.

Dry Pipe Valve: Minimum acceptable size is 4 inches.  Provide 2 water pressure gauges and necessary valves and trim for alarm valve operation.

Provide bypass valve in trim to allow test operation of pressure alarm switch without tripping valve clapper.

Equip dry pipe valve with pressure alarm switch with one normally open contact and one normally closed contact, suitable for 24 VDC.

PRESSURE GAUGES

Provide Listed pressure gauges designed for use with air or water

Gauge Scale: Dial marking subdivision no finer than 1 percent of maximum scale reading and accurate to 3 percent or less.  Provide minimum scale range twice the maximum working pressure.

VALVE SUPERVISION (TAMPER SWITCHES)

Equip valves which control water to automatic sprinkler heads with supervisory switches.

Provide valve supervisory switches with single pole double throw switching contacts, housed in gasketed weather tight enclosure, suitable for 24 VDC.

Supply supervisory device specifically designed to mount on, and operate reliably with, type of control valve being monitored.

Adjust valve position switches to transmit a supervisory signal within two revolutions of valve operating hand wheel or crank (away from its full open position).

Control valves in alarm lines, if provided, shall be electrically supervised.  Provide alarm control valve with supervisory switch, Potter Electric part number BVS, or approved equivalent, suitable for 24 VDC.

SPRINKLERS AND ACCESSORIES

All sprinklers shall be listed by a nationally recognized testing laboratory and shall be selected in accordance with their Listing, manufacture’s instructions, and applicable NFPA requirements.  Provide sprinklers as follows:

Upright Sprinklers: Brass upright type.  Use in areas without suspended ceilings.

Pendent Sprinklers: Chrome plated dry pendent type.  Use below suspended ceilings.

Sprinkler Guards: Provide where sprinklers are exposed to external damage.

Corrosion-Resistant Sprinklers: Provide in locations where chemicals, moisture or other corrosive vapors exist.

Where indicated, provide other types of sprinklers in accordance with their Listing.

WATER SHIELDS

Provide in areas where there is no ceiling, and when multiple level protection is required, e.g., at open grating or open high roofed areas.

Provide compatible Listed/Approved water shields and/or intermediate level sprinklers in accordance with NFPA 13.

FIRE DEPARTMENT CONNECTIONS

Provide fire department connections with 4 inch minimum outlet, two 2-1/2 inch minimum inlets, National Fire Standard threads, cast brass body, clapper in each inlet, plugs, and attached chains.

Fire department connections shall be located on the fire department approach side of the building and be readily visible from the designated fire lanes and where they will remain unobstructed by equipment, landscaping, parking, or other features.

When wall-mounted, locate pumper connections on blank masonry wall, or provide wall with one hour fire barrier for 10 feet in all directions from pumper connection, and identify automatic sprinkler connection.

Identify individual devices by raised letters on the individual devices, or attach escutcheon plates of same material.

Install the fire department connection between the system control valve and the dry pipe valve.

Locate 34 inches (plus or minus 2 inches) from grade level to center of inlet connection.

Erosion Protection

Concrete splash blocks, or other approved method, shall be provided at system exterior drains that do not discharge to a hard covered surface to protect landscape from erosion due to discharge from the drains.

SPRINKLER RISER BACKFLOW PREVENTER

*************************************************************************************************************

Provide a backflow preventer in a new system when the fire protection system is supplied from a potable water system. Systems supplied from a dedicated fire loop or tank (non-potable water) do not require backflow protection. Refer to Fire Protection Standard Drawings ST-D4010-1 for riser detail with backflow preventer.

*************************************************************************************************************

Backflow preventers shall be one of the following:

FEBCO, Model 880V.

Wilkins, Model 475V.

    - Reduced pressure type, vertical orientation, ductile iron body epoxy coated internal and external, with UL/FM OS&Y gate valves, flanged ends, test cocks for in-line field testing, pipe support adaptor, and air gap drain kit.  Maximum water temperature range 33 to 140 degrees F, maximum rated working pressure 175 psi.  Assembly shall be listed in the latest edition of Approved Backflow Prevention Assemblies by the University of Southern California Foundation for Cross Connection Control and Hydraulics Research. Size to match dry pipe valve.

    - Means shall be provided to drain backflow discharge to outside the building or to a floor drain with sufficient capacity to contain the discharge.  The discharge drain pipe size shall be the same nominal diameter as the backflow preventer.  The drain pipe shall be routed to the exterior of the building where the exposed pipe opening shall be covered by ¼-inch hardware cloth.

    - Means shall be provided downstream of all backflow prevention valves for flow tests at system demand (NFPA 13, 2010 ed., Section 8.17.4.6.1) to make sure the backflow prevention device operates correctly  by allowing the fire sprinkler demand, including hose stream demand if required, through the device at the designed pressure loss.

A test header and/or bypass around the fire department connection check valve will be required for Ordinary Hazard and greater sprinkler designs.

- The test header connection shall be clearly and permanently marked as “BACKFLOW TEST CONNECTION”

- The test connection control valve shall be supervised in the closed position. Supervision by locking the valve will be acceptable.

- Means, such as an automatic ball drip valve, shall be provided to prevent accumulations of water at the test connection that are subject to freezing.

pressure switches

The dry pipe system shall be monitored for both high and low air pressure in accordance with NFPA 72, 2010 ed., Section 17.16.2.2.2.  Provide Potter Model PS40A High/Low Pressure Switches, or approved equivalent, (suitable for 24 VDC) to monitor system air pressure.

Provide Potter Model PS10A Pressure Switches, or approved equivalent, (suitable for 24 VDC) to detect a water flow condition in the system.

HEAT TRACING

Heat tracing systems used to provide freeze protection to wet pipe segments shall be UL listed, 120 VAC, and supervised by the fire alarm system.

SUPERVISORY AIR SUPPLY

Provide listed/approved air maintenance device and desiccant dryer compatible with dry pipe valve when building compressed “shop air” will be used for dry system supervisory air pressure.

Provide a listed/approved air maintenance device compatible with the dry pipe valve compressed nitrogen is to be used for dry system supervisory air pressure.  Also, supervise high and low air pressure in accordance with NFPA 72 (2010 edition Section 17.16.2.2.2).  See LANL Standard Detail ST-D4010-1, (see http://engstandards.lanl.gov/Dwgs_Details.shtml for guidance) using a Potter Model PS10A-2A, or approved equivalent, pressure switch.

EXECUTION

  - EXAMINATION

Prior to installation carefully inspect installed Work of other trades, whether pre-existing or part of this Project, and verify that such work is complete to the point where installation of sprinkler system may start.

Notify the LANL Subcontract Technical Representative (STR) should conditions exist, not resulting from Work of this Project, that prohibits the installation from conforming to referenced codes, regulations, standards and approved design.

Install materials and equipment that are free of moisture, scale, corrosion, dirt and other foreign materials.

INSTALLATION

General:

Install system in accordance with NFPA 13.

Do not locate sprinkler heads closer than 12 inches to supply air registers.

Visually examine pipe, fittings, valves, equipment and accessories to ensure they are clean and free of burrs, cracks and other imperfections before installation.  Clean pipe interiors by flushing.

Verify dimensions in field.

Drawings show only approximate building outlines and interior construction details as an aid in understanding the scope of Work.  Investigate structural and finish conditions affecting the Work and arrange Work accordingly, providing such sprinkler heads, fittings, traps, draining valves, piping, and accessories as required to meet such conditions.  Show relevant structural details on Drawings.

Do not render inoperative any system without the prior approval of the LANL STR.  Coordinate necessary shutdowns of existing systems by notifying the LANL STR a minimum of 7 working days before rendering such systems inoperative.

Coordinate sprinkler piping, sprinkler heads and associated equipment with existing ceiling or roof materials, lighting, ductwork, conduit, piping, suspended equipment, structural and other building components.

Dispose of equipment removed for completion of this Project as directed by the LANL STR.

Provide access openings in areas where concealed sprinkler piping is installed.

Piping:

Mark and identify sprinkler piping in accordance with Section 22 0554, Identification for Plumbing, HVAC, and Fire Piping and Equipment.

Conceal sprinkler piping in areas with suspended ceilings.  Install piping in exposed areas as high as possible using necessary fittings and auxiliary drains.  Keep sprinkler piping a minimum of 7 feet 6 inches above finish floor.  Where not possible, run piping at same elevation as existing piping and ducts.  Obtain prior approval from the STR.

Install Inspector’s Test piping at the hydraulically most remote point of the automatic sprinkler system and discharge to exterior of building.  Where possible, conceal test piping in wall and provide access panels for valve and sightglass and protect from freezing. Locate Test Station in an easily accessible location approved by the LANL STR.

Diamond coredrill or sleeve concrete penetrations, then grout and seal with fire-resistive material, securely held in place.  Use Listed/approved through penetration fire stop system assemblies for piping penetrating fire resistance rated construction.

Pipe Support:  Install pipe hangers for pipe supports inside buildings in accordance with NFPA 13.  Seismic bracing shall be installed in accordance with the NFPA 13 (2010 edition Section 9.3). Install concrete anchors in accordance with Division 3 sections on post installed anchors.  Do not use explosive-driven fasteners as a method of installing anchors or hangers.  Do not hang other piping or equipment from sprinkler pipe.

Welding:

Shop weld pipe and fittings using approved welding fittings.  Comply with NFPA 13 for welding methods.

Provide a blind flange or grooved cap at each end of welded headers.

Comply with 01 4444 -- Offsite Welding and Joining Requirements and 01 4455 -- Onsite Welding and Joining Requirements.

Dry Pipe Valve: Set plumb and unobstructed.  Provide minimum clear distances from walls to centerline of pipe valve as follows:

Rear - 16 inches

Sides - 24 inches

Front - 36 inches

System Riser: Install riser from underground so that no joint or fitting occurs within the bearing zone of foundation structures or occurs at least 5 feet from any foundation structure.

Control Valves: Provide Listed OS&Y fire protection control valves.  Installed so open or closed status can be readily seen from finish floor.

Install control valves on supply lines (outside protected area) into elevator shaft and elevator equipment room, computer rooms, and identified special protection areas. Control valve to be accessible from floor level.  Provide valve with tamper supervision switches.

Sprinklers and Accessories:

Provide upright sprinklers on exposed piping below ceiling.  Pendent sprinklers may be used where necessary due to spacing, location, and other requirements.

Align sprinklers below ceiling parallel to ceiling features and walls, and locate as close to center as possible in halls and corridors.

Provide chrome plated escutcheons where exposed piping passes through finished floors, walls, partitions and ceilings.  Secure to pipe with set screws or spring clips.

Protect sprinklers subject to mechanical injury with guards as follows:

Provide guards in mechanical equipment rooms, electrical equipment rooms, janitor's closets, and storage areas where distance from sprinkler deflector to finish floor is less than 15 feet.

In all other areas, provide guards where distance from sprinkler deflector to finish floor is less than 7 feet.

Provide one spare sprinkler cabinet, complete with sprinklers of assorted temperature ratings of the type necessary and in use throughout the installation, at each main riser valve.  Equip each cabinet per NFPA 13.

Signs:

Install as required by NFPA 13.

Post indicator valves (PIVs) shall be provided with a permanent weatherproof placard identifying the building or area protected by the sprinkler system for which the PIV controls the water supply to.

Provide a permanent, weatherproof sign noting “BACKFLOW TEST CONNECTION” located on the exterior of the building in the immediate vicinity of the backflow test connection valves.

Painting: Paint sprinkler risers, unfinished pumper connection piping, exposed sprinkler piping in stairwells, and sprinkler piping in all equipment rooms with 2 coats of Fire Protection Red.  Apply one coat of primer and one coat of paint to match background, on new exposed piping in occupied spaces.  Do not paint sprinkler heads.  Any sprinkler heads receiving paint require replacement.  Comply with Section 09 9100, Painting.

Unsupervised Water Supplies: Install approved water flow detection device on underground water supplies entering buildings when fire protection riser is more than 10 lineal feet from exterior of building.

Water Supply Control Valve: Where not otherwise provided for, provide water supply control valve(s) conforming to the requirements of NFPA 24.

Provide UL Listed or FM approved valves, with listed post indicator valve (PIV).  Locate PIVs a minimum of 40 feet from building. PIVs may be located closer than 40 feet from building providing they are located outside the collapse area of the building’s walls.  Fire hydrants and post indicator valves proposed to be located closer than 40 feet away from a building shall receive prior approval of the location from the LANL Fire Protection Section.

When valve is located less than 20 from building, or a wall post indicating valve is provided, the wall 10 feet in all directions of the valve shall be blank masonry or one hour fire resistance rated construction.

Post indicator valves shall be set so that the top of the post is 32 inches to 40 inches above the final grade.

Post indicator valves shall be protected against mechanical damage.

Special Tools and Devices: Provide one complete set of special tools or special devices required for operation, testing and/or maintenance of equipment furnished under this Section.

EQUIPMENT INSTALLATION

Install devices or equipment not specifically covered by these Specifications in accordance with manufacturer's instructions.

CONNECTIONS TO EXISTING SYSTEMS

Final connection of new systems to existing underground piping systems will be made by LANL with materials furnished by the Subcontractor.

Final connection of new systems to other existing systems above grade shall be done by the Subcontractor after contacting the LANL STR who will implement the Laboratory Fire Protection Impairment Procedure.  Do all final connections of this type with only one outage per existing system.

STERILIZATION

Sterilize sprinkler system underground piping upstream of alarm valve in accordance with Section 22 0816, Disinfection of Potable Water Piping.

Do not sterilize sprinkler system downstream of alarm valve.

EXISTING CONDITIONS

Area Restoration: Restore areas disturbed by the fire protection system installation to the condition existing prior to start of construction.

Field Inspection: Field inspect areas of sprinkler installation for potential interference with ducts, cable trays, electrical or mechanical equipment, and other similar interferences.  Carefully coordinate Work under this section with other Work.

TESTING

Hydrostatically test piping in accordance with Section 22 0813, Testing Piping Systems, and NFPA 13.

Flush system with water in accordance with NFPA 13 and 24.

Comply with the discharge requirements in Section 01 3545, Water Discharge Requirements.

Notify LANL STR and the responsible LANL Fire Protection Division representative at least 5 working days in advance to witness all system tests.

INSPECTION

Inspect new fire protection system in accordance with NFPA 13 and 24, in the presence of the LANL STR.  Give advance notice, as specified below, to the LANL STR prior to any tests.

Notify the LANL STR upon completion of installation of all materials and equipment.  LANL STR will schedule inspection of installation within 5 working days after Subcontractor notification.

Correct deficiencies noted during this inspection and correct prior to further testing.

END OF SECTION

***********************************************************

Do not delete the following reference information:

***********************************************************

FOR LANL USE ONLY

This project specification is based on LANL Master Specification 21 1316 Rev. 3, dated March 23, 2010.