SECTION 22 0548.23

VIBRATION AND SEISMIC CONTROLS FOR MECHANICAL SYSTEMS

*************************************************************************************************************

LANL MASTER SPECIFICATION

Word file at http://engstandards.lanl.gov

This template must be edited for each project.  In doing so, specifier must add project-specific requirements.  Brackets are used in the text to indicate designer choices or locations where text must be supplied by the designer.  Once the choice is made or text supplied, remove the brackets.  The template must also be edited to delete requirements for processes, items, or designs that are not included in the project; and author notes such as these.  Additional tailoring requirements are contained in ESM Chapter 1 Section Z10 Att. F, Specifications.

To seek a variance from requirements in the template that are applicable, contact the Engineering Standards Structural Specifications POC.  Please contact POC with suggestions for improvement as well.

When assembling a specification package, include applicable sections from all Divisions, especially Division 1, General Requirements.

This Section is intended for use with ML-4 projects.  For ML-1, 2, and 3 applications, additional requirements and independent reviews should be added if increased confidence in procurement or execution is desired; see ESM Chapter 1 Section Z10 Specifications and Quality sections.

This Section specifies vibration- and seismic-control devices for Risk Category (RC) I through RC IV plumbing piping, plumbing equipment, and HVAC by describing various device types, and it describes how the devices are attached to these (nonstructural) components and their supporting structure.

The Section was created by combining AIA Master Spec Sections 220548 and 230548, which are very similar with respect to items commonly specified at LANL.

- Air-spring isolators, restrained air-spring isolators, vibration isolation equipment bases, and restrained isolation roof-curb rails, aren’t included herein (since they’re uncommon at LANL).

- If one or more of these items are needed, they should be edited into the Section.  Everything that’s needed to edit them in can be found in AIA 230548.

In the event that only one or the other of the two types of devices herein are applicable to the project, edit the Section accordingly.

*************************************************************************************************************

*************************************************************************************************************

This author note pertains solely to the seismic-controls-portion of this Section.

The Section shall not be used for systems/ components that are seismically exempt per ASCE 7 Ch. 13, or for “non-exempt components” that will comply with ASCE 7 paragraph 13.2.1 via Manufacturer certification.

In order to properly edit the Section for “non-exempt components,” the following two (2) decisions have to have been made first:

- Who is going to be responsible for preparing Project-specific design and documentation (ref. ASCE 7 para. 13.2.1)?

- Whether or not the component(s) a Designated Seismic System (DSS).

I)	There are two (2) options for preparation of Project-specific design and documentation:

- Engineer of Record (EOR), or

- Construction subcontractor (i.e., Delegated Design).

Once it’s known whether I.A or I.B applies to the Project in question, subsequent seismic-related author notes can be properly interpreted and followed through on.

II) 	If a component must function after the design-basis earthquake, it is assigned an Importance Factor (Ip) of 1.5, which makes it a DSS (per ASCE 7 para. 13.1.3).  If the DSS requires Special Certification per ASCE 7 para. 13.2.2, this Section (22 0548.23) shall reference Section 01 8734, SEISMIC QUALIFICATION OF NONSTRUCTURAL COMPONENTS (IBC), and a project-specific version of 01 8734 shall be created and included in the Project Spec.

Seismic control/ restraint is achieved by devices (e.g., supports and attachments, etc.) that provide restraint against excessive movement during an earthquake (without compromising the effectiveness of vibration controls, if applicable).  Since these devices are included herein, if a Project Spec includes this Sect., only devices that differ from those herein (that are required for use) need be included in the Sect. pertaining to the component (e.g., 22 1234, 23 5678, etc.).

*************************************************************************************************************

GENERAL

SUMMARY

Section Includes:

Elastomeric isolation pads.

Elastomeric isolation mounts.

Restrained elastomeric isolation mounts.

Open-spring isolators.

Housed-spring isolators.

Restrained-spring isolators.

Housed-restrained-spring isolators.

Pipe-riser resilient supports.

Resilient pipe guides.

Elastomeric hangers.

Spring hangers.

Snubbers.

Restraint channel bracings.

Restraint cables.

Seismic-restraint accessories.

Related Requirements:

********************************************************************************************Retain subparagraphs below to cross-reference requirements Construction Subcontractor might expect to find in this Section but are specified in other Sections.

Add subparagraphs for specific components (e.g., piping, ductwork, equipment, systems, etc.) that will use the devices specified herein.

********************************************************************************************

********************************************************************************************

Seismic:  Refer to the “seismic author note” on page 1 for details associated with 1st subparagraphs (i.e., Section 01 8734).

- If ASCE 7 para. 13.2.1 is going to be complied with via manufacturer certification, and the component isn’t a DSS requiring Special Certification, then delete the 1st subparagraph.

- If the component is a DSS requiring Special Certification, retain the 1st subparagraph (regardless of how ASCE 7 para. 13.2.1 is going to be complied with).

The 6th subparagraph is required in order to link this Sect. (22 0548.23) with the reason it’s necessary.  In other words, identify the section number and title associated with the component that requires seismic control (and ensure that Sect. refers to this one).  Add as many similar subparagraphs as applicable.
********************************************************************************************

Section 01 8734, Seismic Qualification of Nonstructural Components (IBC), for requirements for manufacturer certification for seismic qualification of components, supports, and attachments; and for special certification of Designated Seismic Systems.

Section 05 0520 Post-Installed Concrete and Grouted-Masonry Anchors – Normal Confidence for products and installation requirements.

Section 05 0521 Post-Installed Concrete Anchors – High Confidence for products and installation requirements.

Section 21 1313 Wet-Pipe Sprinkler Systems for requirements for seismic control of fire-suppression equipment and systems.

Section 22 0529, Hangers and Supports for Electrical Systems, for commonly used mechanical supports and installation requirements.

Section [______] [___________________] for all requirements associated with the component/ system requiring seismic control.]

REFERENCES

American Society of Civil Engineers (ASCE):

ASCE 7 – Minimum Design Loads for Buildings and Other Structures

ASTM International

#### ASTM A 492 - Specification for Stainless Steel Rope Wire

#### ASTM A 603 - Specification for Zinc-Coated Steel Structural Wire Rope

American Welding Society (AWS)

- AWS D1.1 - Structural Welding Code – Steel

International Code Council (ICC)

- International Building Code (IBC)

- Evaluation Service (ES)

##### Evaluation Service Report (ESR)

Manufacturers Standardization Society of The Valve and Fittings Industry Inc. (MSS)

- MSS SP-127 - Bracing for Piping Systems Seismic-Wind-Dynamic Design, Selection, and Application

Metal Framing Manufacturers Association (MFMA)

- MFMA-4 – Metal Framing Standards Publication

State of California Office of Statewide Health Planning and Development (OSHPD).

ACTION SUBMITTALS

Product Data: For each type of product.

Include rated load, rated deflection, and overload capacity for each vibration isolation device.

Illustrate and indicate style, material, strength, fastening provision, and finish for each type and size of [vibration-isolation and seismic-restraint device required.

************************************************************************************************************ Edit the options in the following subparagraph in accordance with the applicable independent third-party evaluator/certifier of the product(s) to be used.  And the same goes for subsequent similar paragraph/subparagraph herein.
************************************************************************************************************

Tabulate types and sizes of seismic restraints, complete with report numbers and rated strength in tension and shear as evaluated [in an ICC-ES ESR] [by OSHPD] [_____].

Annotate to indicate application of each product submitted and compliance with requirements.

Interlocking Snubbers: Include ratings for horizontal, vertical, and combined loads.

Shop Drawings:

- Detail fabrication and assembly of equipment bases. Detail fabrication including anchorages and attachments to structure and to supported equipment.  Include adjustable motor bases, rails, and frames for equipment mounting.

Per the requirements of 01 4444 Offsite Welding and Joining Requirements and/or 01 4455 Onsite Welding and Joining Requirements, submit

****************************************************************************************************

When Offsite only, delete submittals below regarding Onsite welding. For high risk applications such as ML-1 or ML-2, add submittals for “Weld Filler Material Control Procedures” and “Filler Material Certified Material Test Reports (CMTRs)” when required.  Add “Post-Weld Heat Treatment Procedures” when required.

****************************************************************************************************

  - Welding Procedure Specification (WPS) and supporting Procedure Qualification Record (PQR).  [Note:  For Onsite welding use of LANL WPS/PQR is the default; coordinate usage with the LANL CWI; no submittal required]

  - Welder Performance Qualification Records (WPQR) including continuity [Note: For Onsite, welders are tested by LANL who will produce WPQR and track continuity; this includes brazing, bonding and fusing; no submittal required]

  - Inspector qualification records

  - Inspection procedures

  - Shop drawings with weld details/symbols

*************************************************************************************************************

Retain "Delegated-Design Submittal" paragraph below if design services have been delegated to (construction) Subcontractor.

If retaining, and Project includes equipment mounted outdoors, retain the portions of subparagraphs pertaining to “wind.”

If retaining, and Project includes vibration-isolation devices, then retain related text in subparagraphs D.2, D.4.b, and/or D.4.c.

Professional engineer is defined in Sect. 01 4000 Quality Requirements.
*************************************************************************************************************

Delegated-Design Submittal: For each vibration-isolation and seismic-restraint device and, as applicable, for each connection type and/ or connection detail associated with providing adequate flexibility.

Include design calculations and details for selecting vibration isolators and seismic restraints complying with performance requirements, design criteria, and analysis data signed and sealed by the professional engineer, registered in the state of New Mexico, responsible for their preparation.

Design Calculations: Calculate static and dynamic loading due to equipment weight, operation, and seismic [and wind] forces required to select vibration isolators, and seismic [and wind] restraints.  [Calculate anticipated differential movement between adjacent structures, or portions of the same structure that may move independently, required to select a type(s) of, and/ or provide a detail(s) for, flexible connection(s).]

[Coordinate design calculations with wind load calculations required for equipment mounted outdoors. Comply with requirements in other Sections for equipment mounted outdoors.]

Riser Supports: Include riser diagrams and calculations showing anticipated expansion and contraction at each support point, initial and final loads on building structure, spring deflection changes, and seismic loads. Include certification that riser system was examined for excessive stress and that none exists.

********************************************************************************************Retain "Seismic (-and Wind)-Restraint Details" subparagraph below only if seismic design requirements apply but s details or charts on Drawings don’t describe seismic restraints in detail. Retaining subparagraph requires Subcontractor to submit seismic-restraint Shop Drawings prepared by a NM professional engineer.
********************************************************************************************

Seismic[- and Wind]-Restraint Details:

Design Analysis: To support selection and arrangement of seismic [and wind] restraints. Include calculations of combined tensile and shear loads.

Details: Indicate fabrication and arrangement. Detail attachments of restraints to the restrained items and to the structure. Show attachment locations, methods, and spacings. Identify components, list their strengths, and indicate directions and values of forces transmitted to the structure during seismic events. Indicate association with vibration-isolation devices.

Vibration isolators used for component mounting shall comply with the associated “Additional Requirements” in ASCE 7 paragraph 13.6.5.5.]

[Coordinate seismic-restraint and vibration-isolation details with wind-restraint details required for equipment mounted outdoors. Comply with requirements in other Sections for equipment mounted outdoors.]

Preapproval and Evaluation Documentation: [In an ICC-ES ESR] [By OSHPD] [_________], showing maximum ratings of restraint items and the basis for approval (tests or calculations).

*************************************************************************************************************

Retain the subparagraph below if applicable.  Refer to previous author note for guidance.

The decision to retain/ not retain this subparagraph will affect the PART-3 Article, “Accommodation of Differential Seismic Motion.”

*************************************************************************************************************

Details to Provide Adequate Flexibility During a Seismic Event:

The portions of the aforementioned “Seismic-Restraint Details” applicable to compliance with the provisions of ASCE 7 Chapter 13 pertaining to “Seismic Relative Displacements” and “differential displacements” shall be provided/adhered to.

INFORMATIONAL SUBMITTALS

************************************************************************************************************Retain "Coordination Drawings" Paragraph below for situations where limited space necessitates maximum use for efficient installation of different components or if coordination is required for installation of products and materials by separate installers. Coordinate Paragraph with other Sections specifying products listed below. Preparation of coordination drawings requires the participation of each trade involved in installations within the limited space.
*************************************************************************************************************

Coordination Drawings: Show coordination of vibration-isolation device installation and seismic bracing for mechanical components with other systems and equipment in the vicinity, including other supports and devices/ restraints/ bracing, if any.

Field quality-control reports.

QUALITY CONTROL

****************************************************************************************************

Quality Control (QC) is what is contained herein, and is the responsibility of the Subcontractor.

Quality Assurance (QA, which is required by IBC Ch. 17) is contained in the EOR’s Statement of Special Inspections (SSI), and is the responsibility of LANL (i.e., execution of the SSI).  The SSI template is found in ESM Ch. 16, Sect. IBC-IP, Att. B.
****************************************************************************************************

Comply with seismic-restraint requirements in the IBC unless requirements in this Section are more stringent.

****************************************************************************************************Retain appropriate subparagraph(s) under “Welding Qualifications” paragraph below if shop and/or field welding is required. If retaining, also retain "WPQR" Paragraph in "Informational Submittals" Article.
****************************************************************************************************

Welding Qualifications:

Shop.

Prior to shop welding, submit WPQR certification for each welder stating the type of welding and positions qualified for, the code and procedure qualified under, date qualified, and the firm and individual certifying the qualification tests. Refer to Section 01 4444 Offsite Welding and Joining Requirements.

Field.

Refer to Section 01 4455 Onsite Welding and Joining Requirements.

Seismic-restraint devices shall have horizontal and vertical load testing and analysis.  They shall bear preapproval from OSHPD (i.e., “OPA #”), preapproval by ICC-ES (i.e., ESR #), or preapproval by a similar agency, showing maximum seismic-restraint ratings. Ratings based on independent testing are preferred to ratings based on calculations. If preapproved ratings are not available, submittals based on independent testing are preferred. Calculations (including combining shear and tensile loads) to support seismic-restraint designs must be signed and sealed by a professional engineer licensed in the state of New Mexico.

PRODUCTS

*************************************************************************************************************

Edit the following Article in accordance with the same one (i.e., “Seismic Performance Requirements”) in the “component-specific section (e.g., 22 1234, 23 5678, etc.),” and indicate that Sect. number and title.

Add on to/ delete Paragraph A and/or B as applicable.
*************************************************************************************************************

SEISMIC PERFORMANCE REQUIREMENTS

Per the Article, “Seismic Performance Requirements” in Section 2[ ] [____] [_____________], the design of the seismic restraints shall ensure that position retention of the component/ system is achieved.

Per the Article, “Seismic Performance Requirements” in Section 2[ ] [____] [_____________], the design of the seismic restraints shall ensure that position retention of the component/ system is achieved and, to the extent that’s applicable*, that the component is fully operational.

*	Refer to ASCE 7 paragraph 13.6.4, and the portions of paragraph 13.6.5 pertaining to “Ip = 1.5” and “certified” equipment.

*************************************************************************************************************

If the “Delegated-Design Submittal” in PART 1 was retained, retain the following Article, and edit its Paragraphs as applicable to Project.

If retaining Paragraph A, edit options based on Project requirements and ESM Ch. 5 Sect. II, “Section 1609 Wind Loads.”

If retaining Paragraph B, edit options based on Project requirements and ESM Ch. 5 Sect. II, “Section 1613 Earthquake Loads.” Add to this paragraphgraphgraphgraph as required to capture all of the components requiring restraint.

*************************************************************************************************************

DESIGN CRITERIA

- Wind Restraint:  Design loads shall be determined in accordance with IBC Section 1609 and the following parameters:

Building Risk Category: [I] [II] [III] [IV].

Ultimate Design Wind Speed, Vult, miles per hour (mph): [105] [115] [120].

Exposure Category: Exposure C.

Seismic Restraint:  Design loads shall be determined in accordance with IBC Section 1613 and the following parameters:

Building Risk Category:  [I] [II] [III] [IV].

Site Class: DD.

Design Spectral Response Acceleration at Short Periods, SDS, gravity (g):  [0.75] [____].

Design Spectral Response Acceleration at 1.0-Sec. Period, SD1, gravity (g):  [0.64] [____].

Seismic Design Category:  D.

********************************************************************************************
Regarding the “Ip subparagraph" below, per ASCE 7 paras. 13.2.3 and 13.6.6, design and detailing as DSS (i.e., Ip = 1.5) might be required for components that otherwise seem/ appear to be unessential/ noncritical (i.e., Ip = 1.0).
********************************************************************************************

Component Importance Factor, Ip: [1.0] [1.5].

Component Amplification Factor, ap: [1.0] [2.5].

********************************************************************************************

Regarding the “Rp subparagraph" below, per ASCE 7 paragraph 13.1.4, 6.0 is the maximum value that can be used to determine the force in an attachment.  This provision only pertains to components with Rp > 6.0.

********************************************************************************************

Component Response Modification Factor, Rp: [1.5] [2.0] [2.5] [3.0] [6.0].

ELASTOMERIC ISOLATION PADS

****************************************************************************************************Copy "Elastomeric Isolation Pads" Paragraph below and re-edit for each product.

The configuration and materials of elastomeric isolation pads depend on the equipment being supported. It is possible to have more than one type of elastomeric isolation pad on the same Project. Insert Drawing designation for each elastomeric isolation pad type required. Use these designations on Drawings to identify each product.
****************************************************************************************************

Elastomeric Isolation Pads: [Insert drawing designation].

Fabrication: Single or multiple layers of sufficient durometer stiffness for uniform loading over pad area.

Size: Factory or field cut to match requirements of supported equipment.

********************************************************************************************Verify availability of various pad materials and their properties with manufacturers.
********************************************************************************************

Pad Material: Oil and water resistant with elastomeric properties.

Surface Pattern: [Smooth] [Ribbed] [Waffle] pattern.

********************************************************************************************Retain 1st subparagraph below if pad is infused with synthetic fibers.
********************************************************************************************

Infused nonwoven cotton or synthetic fibers.

********************************************************************************************Retain 1st subparagraph below if galvanized-steel baseplates are adhered to the isolation pad to facilitate load distribution.
********************************************************************************************

Load-bearing metal plates adhered to pads.

********************************************************************************************Retain "Sandwich-Core Material" subparagraph below if pad has a sandwich-core material.

Copy "Sandwich-Core Material" subparagraph below and re-edit for each sandwich-core material. Core materials may not be elastomeric. See the "Elastomeric Isolation Pads" Article in the AIA MasterSpec Evaluations documents for 22 0548/23 0548 for more information.
********************************************************************************************

Sandwich-Core Material: [Resilient] [and] [elastomeric] [Insert compound].

********************************************************************************************
Retain "Surface Pattern" subparagraph below if the sandwich-core material has a surface pattern.
********************************************************************************************

Surface Pattern: [Smooth] [Ribbed] [Waffle] pattern.

************************************************************************************Retain subparagraph below if pad is infused with synthetic fibers.
************************************************************************************

Infused nonwoven cotton or synthetic fibers.

ELASTOMERIC ISOLATION MOUNTS

****************************************************************************************************
Copy "Double-Deflection, Elastomeric Isolation Mounts" Paragraph below and re-edit for each product.

The configuration and materials of elastomeric isolation mounts depend on the equipment being supported. It is possible to have more than one type of elastomeric isolation mount on the same Project Insert drawing designation for each elastomeric isolation mount type required. Use these designations on Drawings to identify each product.
****************************************************************************************************

Double-Deflection, Elastomeric Isolation Mounts: [Insert drawing designation].

Mounting Plates:

Top Plate: Encapsulated steel load transfer top plates, factory drilled and threaded [with threaded studs or bolts].

************************************************************************************Retain "Baseplate" subparagraph below if the elastomeric mount being specified has a baseplate.
************************************************************************************

Baseplate: Encapsulated steel bottom plates with holes provided for anchoring to support structure.

Elastomeric Material: Molded, oil-resistant rubber, neoprene, or other elastomeric material.

RESTRAINED ELASTOMERIC ISOLATION MOUNTS

****************************************************************************************************Copy "Restrained Elastomeric Isolation Mounts" paragraph below and re-edit for each product.

The configuration and materials of restrained elastomeric isolation mounts depend on the equipment being supported. It is possible to have more than one type of restrained elastomeric isolation mount on the same project. Insert drawing designation for each restrained elastomeric isolation mount type required. Use these designations on Drawings to identify each product.
****************************************************************************************************

Restrained Elastomeric Isolation Mounts: [Insert drawing designation].

Description: All-directional isolator with seismic restraints containing two separate and opposing elastomeric elements that prevent central threaded element and attachment hardware from contacting the housing during normal operation.

Housing: Cast-ductile iron or welded steel.

Elastomeric Material: Molded, oil-resistant rubber, neoprene, or other elastomeric material.

OPEN-SPRING ISOLATORS

****************************************************************************************************Copy "Freestanding, Laterally Stable, Open-Spring Isolators" paragraph below and re-edit for each product.

The configuration and materials of open-spring isolators depend on the equipment being supported. It is possible to have more than one type of open-spring isolator on the same Project. Insert drawing designation for each open-spring isolator type required. Use these designations on Drawings to identify each product.
****************************************************************************************************

Freestanding, Laterally Stable, Open-Spring Isolators: [Insert drawing designation].

Outside Spring Diameter: Not less than 80 percent of the compressed height of the spring at rated load.

Minimum Additional Travel: 50 percent of the required deflection at rated load.

Lateral Stiffness: More than 80 percent of rated vertical stiffness.

Overload Capacity: Support 200 percent of rated load, fully compressed, without deformation or failure.

Baseplates: Factory-drilled steel plate for bolting to structure with an elastomeric isolator pad attached to the underside. Baseplates shall limit floor load to 500 psi.

Top Plate and Adjustment Bolt: Threaded top plate with adjustment bolt and cap screw to fasten and level equipment.

HOUSED-SPRING ISOLATORS

****************************************************************************************************Copy "Freestanding, Laterally Stable, Open-Spring Isolators in Two-Part Telescoping Housing" Paragraph below and re-edit for each product.

The configuration and materials of housed-spring isolators depend on the equipment being supported. It is possible to have > 1 type of housed-spring isolator on the same Project. Insert drawing designation for each housed-spring isolator type required. Use these designations on Drawings to identify each product.
****************************************************************************************************

Freestanding, Laterally Stable, Open-Spring Isolators in Two-Part Telescoping Housing: [Insert drawing designation].

Outside Spring Diameter: Not less than 80 percent of the compressed height of the spring at rated load.

Minimum Additional Travel: 50 percent of the required deflection at rated load.

Lateral Stiffness: More than 80 percent of rated vertical stiffness.

Overload Capacity: Support 200 percent of rated load, fully compressed, without deformation or failure.

Two-Part Telescoping Housing: A steel top and bottom frame separated by an elastomeric material and enclosing the spring isolators.

Drilled base housing for bolting to structure with an elastomeric isolator pad attached to the underside. Bases shall limit floor load to 500 psi.

Top housing with [attachment and leveling bolt] [threaded mounting holes and internal leveling device] [elastomeric pad].

RESTRAINED-SPRING ISOLATORS

****************************************************************************************************Copy "Freestanding, Laterally Stable, Open-Spring Isolators with Vertical-Limit Stop Restraint" Paragraph below and re-edit for each product.

The configuration and materials of restrained-spring isolators depend on the equipment being supported. It is possible to have more than one type of restrained-spring isolator on the same Project. Insert drawing designation for each restrained-spring isolator type required. Use these designations on Drawings to identify each product.
****************************************************************************************************

Freestanding, Laterally Stable, Open-Spring Isolators with Vertical-Limit Stop Restraint: [Insert drawing designation].

Housing: Steel housing with vertical-limit stops to prevent spring extension due to weight being removed.

Base with holes for bolting to structure with an elastomeric isolator pad attached to the underside. Bases shall limit floor load to 500 psi.

Top plate with [threaded mounting holes] [elastomeric pad].

Internal leveling bolt that acts as blocking during installation.

Restraint: Limit stop as required for equipment and LANL STR.

Outside Spring Diameter: Not less than 80 percent of the compressed height of the spring at rated load.

Minimum Additional Travel: 50 percent of the required deflection at rated load.

Lateral Stiffness: More than 80 percent of rated vertical stiffness.

Overload Capacity: Support 200 percent of rated load, fully compressed, without deformation or failure.

HOUSED-RESTRAINED-SPRING ISOLATORS

****************************************************************************************************Copy "Freestanding, Steel, Open-Spring Isolators with Vertical-Limit Stop Restraint in Two-Part Telescoping Housing" paragraph below and re-edit for each product.

The configuration and materials of housed-restrained-spring isolators depend on the equipment being supported. It is possible to have more than one type of housed-restrained-spring isolator on the same Project. Insert drawing designation for each housed-restrained-spring isolator type required. Use these designations on Drawings to identify each product.
****************************************************************************************************

Freestanding, Steel, Open-Spring Isolators with Vertical-Limit Stop Restraint in Two-Part Telescoping Housing: [Insert drawing designation].

Two-Part Telescoping Housing: A steel top and bottom frame separated by an elastomeric material and enclosing the spring isolators. Housings are equipped with [adjustable] [non-adjustable] snubbers to limit vertical movement.

Drilled base housing for bolting to structure with an elastomeric isolator pad attached to the underside. Bases shall limit floor load to 500 psi.

Threaded top housing with adjustment bolt and cap screw to fasten and level equipment.

Outside Spring Diameter: Not less than 80 percent of the compressed height of the spring at rated load.

Minimum Additional Travel: 50 percent of the required deflection at rated load.

Lateral Stiffness: More than 80 percent of rated vertical stiffness.

Overload Capacity: Support 200 percent of rated load, fully compressed, without deformation or failure.

PIPE-RISER RESILIENT SUPPORT

****************************************************************************************************Copy "Description" paragraph below and re-edit for each product.

The configuration and materials of pipe-riser resilient supports depend on the equipment being supported. It is possible to have more than one type of pipe-riser resilient support on the same Project. Insert drawing designation for each pipe-riser resilient support type required. Use these designations on Drawings to identify each product.
****************************************************************************************************

Description: All-directional, acoustical pipe anchor consisting of two steel tubes separated by a minimum 1/2-inch-thick neoprene: [Insert drawing designation].

Vertical-Limit Stops: Steel and neoprene vertical-limit stops arranged to prevent vertical travel in both directions.

Maximum Load Per Support: 500 psi on isolation material providing equal isolation in all directions.

RESILIENT PIPE GUIDES

****************************************************************************************************Copy "Description" Paragraph below and re-edit for each product.

The configuration and materials of resilient pipe guides depend on the equipment being supported. It is possible to have more than one type of resilient pipe guide on the same Project. Insert drawing designation for each resilient pipe guide type required. Use these designations on Drawings to identify each product.
****************************************************************************************************

Description: Telescopic arrangement of two steel tubes or post and sleeve arrangement separated by a minimum 1/2-inch-thick neoprene: [Insert drawing designation].

********************************************************************************************
Retain "Factory-Set Height Guide with Shear Pin" subparagraph below where vertical motion due to pipe/duct expansion and contraction is required and clearances are not readily visible.
********************************************************************************************

Factory-Set Height Guide with Shear Pin: Shear pin shall be removable and re-insertable to allow for selection of pipe movement. Guides shall be capable of motion to meet location requirements.

ELASTOMERIC HANGERS

****************************************************************************************************Copy "Elastomeric Mount in a Steel Frame with Upper and Lower Steel Hanger Rods" Paragraph below and re-edit for each product.

The configuration and materials of elastomeric hangers depend on the equipment being supported. It is possible to have more than one type of elastomeric hanger on the same Project. Insert drawing designation for each elastomeric hanger type required. Use these designations on Drawings to identify each product.
****************************************************************************************************

Elastomeric Mount in a Steel Frame with Upper and Lower Steel Hanger Rods: [Insert drawing designation].

Frame: Steel, fabricated with a connection for an upper threaded hanger rod and an opening on the underside to allow for a maximum of 30 degrees of angular lower hanger-rod misalignment without binding or reducing isolation efficiency.

Dampening Element: Molded, oil-resistant rubber, neoprene, or other elastomeric material with a projecting bushing for the underside opening preventing steel-to-steel contact.

SPRING HANGERS

****************************************************************************************************Copy "Combination Coil-Spring and Elastomeric-Insert Hanger with Spring and Insert in Compression" paragraph below and re-edit for each product.

The configuration and materials of spring hangers depend on the equipment being supported. It is possible to have more than one type of spring hanger on the same Project. Insert drawing designation for each spring hanger type required. Use these designations on Drawings to identify each product.
****************************************************************************************************

Combination Coil-Spring and Elastomeric-Insert Hanger with spring and Insert in Compression: [Insert drawing designation].

Frame: Steel, fabricated for connection to threaded hanger rods and to allow for a maximum of 30 degrees of angular hanger-rod misalignment without binding or reducing isolation efficiency.

Outside Spring Diameter: Not less than 80 percent of the compressed height of the spring at rated load.

Minimum Additional Travel: 50 percent of the required deflection at rated load.

Lateral Stiffness: More than 80 percent of rated vertical stiffness.

Overload Capacity: Support 200 percent of rated load, fully compressed, without deformation or failure.

Elastomeric Element: Molded, oil-resistant rubber or neoprene. Steel-washer-reinforced cup to support spring and bushing projecting through bottom of frame.

********************************************************************************************Retain "Adjustable Vertical Stop" subparagraph below if a vertical-limit stop is required.
********************************************************************************************

Adjustable Vertical Stop: Steel washer with neoprene washer "up-stop" on lower threaded rod.

Self-centering hanger-rod cap to ensure concentricity between hanger rod and support spring coil.

SNUBBERS

Description: Factory fabricated using welded structural-steel shapes and plates, anchors, and replaceable resilient isolation washers and bushings.

***********************************************************************************************************

Delete following subparagraph if post-installed (P-I) anchors are N/A to snubbers.

***********************************************************************************************************

Post-installed anchors for attaching to concrete shall be as specified in the subsequent “Post-Installed Anchor” Article herein.

Resilient Isolation Washers and Bushings: Oil- and water-resistant neoprene.

Maximum 1/4-inch air gap, and minimum 1/4-inch-thick resilient cushion.

RESTRAINT CHANNEL BRACINGS

Description: MFMA-4, shop- or field-fabricated bracing assembly made of slotted steel channels with accessories for attachment to braced component at one end and to building structure at the other end and other matching components and with corrosion-resistant coating; rated in tension, compression, and torsion forces.

RESTRAINT CABLES

Restraint Cables: [ASTM A603] [ASTM A492] steel cables with end connections made of steel assemblies with thimbles, brackets, swivel, and bolts designed for restraining cable service; with a minimum of two clamping bolts for cable engagement.

SEISMIC-RESTRAINT ACCESSORIES

****************************************************************************************************Retain "Hanger-Rod Stiffener" Paragraph below for strengthening resistance of hanger rods against seismic forces that may cause buckling of rods; delete if detailed on Drawings. Use with either channel- or cable-type bracing assemblies when required to counter seismic forces. Detail fabrication and indicate locations on Drawings.
****************************************************************************************************

Hanger-Rod Stiffener: [Steel tube or steel slotted-support-system sleeve with internally bolted connections] [Reinforcing steel angle clamped] to hanger rod.

Hinged and Swivel Brace Attachments: Multifunctional steel connectors for attaching hangers to [rigid channel bracings] [and] [restraint cables].

Bushings for Floor-Mounted Equipment Anchors: Neoprene bushings designed for rigid equipment mountings, and matched to type and size of anchors and studs.

Bushing Assemblies for Wall-Mounted Equipment Anchorage: Assemblies of neoprene elements and steel sleeves designed for rigid equipment mountings, and matched to type and size of attachment devices used.

Resilient Isolation Washers and Bushings: One-piece, molded, oil- and water-resistant neoprene, with a flat washer face.

POST-INSTALLED ANCHORS

Furnish post-installed expansion, adhesive, and undercut concrete and grouted-masonry anchors as indicated on the Drawings and in Section [05 0520, Post-Installed Concrete and Grouted-Masonry Anchors – Normal Confidence] [and/or] [05 0521, Post-Installed Concrete Anchors – High Confidence].

FLEXIBLE CONNECTIONS

****************************************************************************************************

For information/ education on flex connections, refer to the following:

- Fig. 6.4.3.3-6, Flexible connections and expansion joints (ER), in FEMA E-74.

- ASCE 7 para. C13.6.8, specifically the portion of it on the left-hand side of pp. 452.

****************************************************************************************************

Permissible products include those that permit rotational and/ or translational movement without degradation of performance. Examples include universal joints, bellows expansion joints, and flexible metal hose.

EXECUTION

EXAMINATION

Examine areas and equipment to receive vibration-isolation and seismic [- and wind]-control devices for compliance with requirements for installation tolerances and other conditions affecting performance of the Work.

Examine roughing-in of reinforcement and cast-in-place anchors to verify actual locations before installation.

Proceed with installation only after unsatisfactory conditions have been corrected.

APPLICATIONS

Multiple Pipe Supports: Secure pipes to trapeze member with clamps approved for application [in an ICC-ES ESR] [by OSHPD] [_____].

****************************************************************************************************
Indicate on Drawings, by details, schedules, or a combination of both, the locations where hanger rods for individual pipes/ducts, and hanger rods for trapeze hangers, require hanger-rod stiffeners.
****************************************************************************************************

Hanger-Rod Stiffeners: Install hanger-rod stiffeners where indicated or scheduled on Drawings to receive them and where required to prevent buckling of hanger rods due to seismic forces.

Strength of Support and Seismic-Restraint Assemblies: Where not indicated, select sizes of components so strength is adequate to carry present and future static and seismic loads within specified loading limits.

Equipment:  Each equipment item shall be installed such that it is entirely located and attached on one side only of a building expansion or seismic-control joint.

*************************************************************************************************************

In the following Paragraph, retain the subparagraph if applicable to Project.  If this subparagraph is retained, and Delegated Design isn’t applicable to Project (ref. “Action Submittals” in PART 1), the calcs and drawing detail(s) associated with ASCE 7 paragraph 13.6.6 must be provided by the EOR.

*************************************************************************************************************

Distribution/ Distributed Systems:  Where pipes/ ducts cross building expansion or seismic-control joints, pass from one building to another, or pass from one floor/ story of a building to another, or connect to other nonstructural components that aren’t braced/ rigidly mounted, flexible connections shall be installed.

[For utility / service lines passing from one building to another, or between portions of the same building that may move independently, flexibility shall be provided per the associated drawing detail(s).]

VIBRATION CONTROL AND SEISMIC-RESTRAINT DEVICE INSTALLATION

Coordinate the location of embedded connection hardware with supported equipment attachment and mounting points and with requirements for concrete reinforcement and formwork specified in Section 03 3001, Reinforced Concrete.

Installation of vibration isolators must not cause any change of position of equipment, piping, or ductwork resulting in stresses or misalignment.

*************************************************************************************************************
If applicable, the Sect. referred to in the following paragraph will have to be created “from scratch (since it isn’t included in the LANL Master Spec).”
*************************************************************************************************************

Comply with requirements in Section 07 7200 Roof Accessories for installation of roof curbs, equipment supports, and roof penetrations.

Equipment Restraints:

********************************************************************************************Indicate type and quantity of snubbers described in first subparagraph below on Drawings or in the applicable Vibration-Control and Seismic-Restraint Device Schedule on Drawings.
********************************************************************************************

Install seismic snubbers on equipment mounted on vibration isolators. Locate snubbers as close as possible to vibration isolators and bolt to equipment base and supporting structure.

Install resilient bolt-isolation washers on equipment anchors where clearance between anchor and adjacent surface exceeds 0.125 inch.

Install seismic-restraint devices using methods approved [in an ICC-ES ESR] [by OSHPD] [___ _____] providing required submittals for component.

Piping Restraints:

Comply with requirements in MSS SP-127.

********************************************************************************************In 1st subparagraph below, options for 40 and 80 feet are recommended by MSS SP-127. Revise these dimensions based on the configuration of piping.
********************************************************************************************

Space lateral supports a maximum of [40] [______] feet o.c., and longitudinal supports a maximum of [80] [_____] feet o.c.

Brace a change of direction longer than 12 feet.

Install cables so they do not bend across edges of adjacent equipment or building structure, and such that they are taught (i.e., without slack) when the component they are to control/ restrain is “at rest.”

Install seismic-restraint devices using methods approved [in an ICC-ES ESR] [by OSHPD] [__ _______] providing required submittals for component.

Install bushing assemblies for anchors for floor-mounted equipment, arranged to provide resilient media between anchors and mounting hole in concrete base.

Install bushing assemblies for mounting bolts/ anchors for wall-mounted equipment, arranged to provide resilient media where equipment or equipment-mounting channels are attached to wall.

Attachment to Structure: If specific attachment is not indicated, anchor bracing to structure at flanges of beams, at panel points in upper truss chords of bar joists, or at concrete members.

Post-Installed Anchors:  Install post-installed anchors as specified in Section [05 0520] [05 0521].

ACCOMMODATION OF DIFFERENTIAL SEISMIC MOTION

***************************************************************************************************
Coordinate/edit this article with the PART 1 para “Delegated-Design Submittal,” and the Drawings and, if applicable, other Project Spec sections.

Any/ all applicable seismic relative displacements and seismic drift ratios shall be determined and designed/detailed for in accordance with the Seismic Performance Requirements in PART 2, and the specifics of the Project.

For information/ education on detailing to accommodate these displacements, refer to ASCE 7 para. C13.6.8, specifically the portion of it on the left-hand side of pp. 452.
****************************************************************************************************

Install flexible connections in piping where they cross seismic joints, where adjacent sections or branches are supported by different structural elements, and where the connections terminate with connection to equipment that is anchored to a different structural element from the one supporting the connections as they approach equipment. Comply with requirements in Section(s) [22 ____] [23 _____] for piping flexible connections.

FIELD QUALITY CONTROL

**************************************************************************************************** The primary purpose of the Article is to alert the Subcontractor that he/she is responsible for quality control (QC) and that, in addition to QC, the component is subject to the quality assurance (QA) indicated in the Project’s Statement of Special Inspections.
****************************************************************************************************

Inspection Agency: Engage a qualified inspection agency to perform inspections.

Perform inspections, with the assistance of a factory-authorized service representative(s) as necessary/ required, during the installation (to include anchorage where applicable) of the systems, equipment, etc. associated with/affected by this Section (i.e., 22 0548.13) as necessary to ensure that the applicable provisions of ASCE 7 Chapter 13 are met.

Prepare an inspection report.

Seismic restraints/controls will be considered defective if the affected systems and equipment do not pass the Special Inspections indicated in the Project’s Statement of Special Inspections.

ADJUSTING

Adjust vibration isolators after piping system is at operating weight.

Adjust limit stops on restrained-spring isolators to mount equipment at normal operating height. After equipment installation is complete, adjust limit stops so they are out of contact during normal operation.

END OF SECTION

***********************************************************

Do not delete the following reference information.

***********************************************************

THE FOLLOWING STATEMENT IS FOR LANL USE ONLY

This project specification is based on LANL Master Specification Section 22 0548.23 Rev. 1, dated September 21, 2020.