SECTION 22 1100

FACILITY WATER DISTRIBUTION

*************************************************************************************************************

LANL MASTER SPECIFICATION

Word file at http://engstandards.lanl.gov

This template must be edited for each project.  In doing so, specifier must add job-specific requirements.  Brackets are used in the text to indicate designer choices or locations where text must be supplied by the designer.  Once the choice is made or text supplied, remove the brackets.  The specifications must also be edited to delete specification requirements for processes, items, or designs that are not included in the project -- and specifier’s notes such as these.  To seek a variance from requirements in the specifications that are applicable, contact the Engineering Standards Manual Mechanical POC. Please contact POC with suggestions for improvement as well.

When assembling a specification package, include applicable specifications from all Divisions, especially Division 1, General requirements.

Specification developed for ML-4 projects.  For ML-1, 2, and 3 applications, additional requirements and independent reviews should be added if increased confidence in procurement or execution is desired; see ESM Chapter 1 Section Z10 Specifications and Quality sections. *************************************************************************************************************

GENERAL

SECTION INCLUDES

Building potable [and non-potable] water piping, valves, fittings, water heater, circulator pump, and accessories within the building envelope.

SUBMITTALS

Submit the following in accordance with Project submittal procedures:

Catalog data on pipe materials, pipe fittings, valves, water heater, circulator pump, and accessories.

Submit shop drawings showing pump type, capacity, certified pump curves showing pump performance characteristics with pump and system operating point plotted. Include NPSH curve when applicable. Include electrical characteristics and connection requirements.

Installation instructions for pumps, water heater, valves and accessories.

QUALITY ASSURANCE

Comply with NSF 61 for materials for water-service piping and specialties for domestic potable water.

Comply with NSF 14 for plastic potable-water-service piping.

Piping materials shall bear label, stamp, or other markings of specified testing agency.

PRODUCTS

  - PRODUCT OPTIONS AND SUBSTITUTIONS

Alternate products may be accepted; follow Section 01 2500, Substitution Procedures

PIPING, BURIED WITHIN THE BUILDING ENVELOPE (within 5 feet of building)

***************************************************************************************************

AWWA C151 available pipe size: 3-64 inches.

***************************************************************************************************

Ductile Iron Pipe: AWWA C151.

Fittings: AWWA C110, Ductile-Iron or Gray-Iron, Class 350, or AWWA C153, Ductile Iron Compact Fittings, Class 350.

Joints: AWWA C111, rubber gasket

Jackets: AWWA C105 polyethylene jacket

Copper Tubing: ASTM B88, Type K, hard drawn or annealed.

Fittings: ANSI/ASME B16.22, wrought copper.

Joints: Brazed, AWS A5.8, BCuP silver/phosphorus/copper alloy with melting range 1190 to 1480°F.

PIPING ABOVE GRADE

***************************************************************************************************

Specify Type K when design exceeds pressure and temperature ratings of Type L.

***************************************************************************************************

Copper Tubing: ASTM B88, Type L, hard drawn or annealed.

Fittings: ANSI/ASME B16.22, wrought copper and copper alloy solder-joint.

Joints: ASTM B32, Solder, Alloy Grade Sb5 tin-antimony, or Alloy Grade Sn95 tin and silver, with melting range 430 to 535°F.

CPVC Pipe and Fittings: ASTM D2846, chlorinated polyvinyl chloride (CPVC) material for water service up to 180°F.

Joints: ASTM D2846, solvent weld with ASTM F493 solvent cement.

UNIONS and Flanges

Union for pipe 2 inches and under.

Copper Tubing: ASME B16.22, Class 150, wrought copper, solder joint.

Flanges for pipe over 2 inches.

Copper Tubing: ASME B16.5, Class 150, slip-on bronze flanges.

Gaskets: 1/16 inch thick preformed neoprene.

VALVES

Ball Valves up to 2 inches:

Manufacturer: Nibco, Series 585-70.

MSS SP-110, 600 psi non-shock cold working pressure (CWP), bronze, two piece body, chrome-plated brass ball, full port, teflon seats, blowout proof stem, lever handle, solder or threaded ends to suit piping.

Butterfly Valves over 2 inches:

Manufacturer: Nibco, Series LD 2000.

MSS SP-67, 200 psi non-shock CWP, ductile iron body, aluminum bronze disc, resilient replaceable EPDM seat, lug style, extended neck, lever handle, for use between ANSI Class 125/150 flanges.

Globe Valves up to 2 inches:

Manufacturer: Nibco, Series 211.

MSS SP-80, Class 125, bronze body, bronze trim, hand wheel, bronze disc, solder or threaded ends to suit piping.

Gate Valves up to 2 inches:

Manufacturer: Nibco, Series 111.

MSS SP-80, Class 125 bronze body, bronze trim, rising stem, hand wheel, inside screw, solid wedge disc, solders or threaded ends to suit piping.

Swing Check Valves

Sizes up to 2 inches:

Manufacture: Nibco 433 Series.

MSS SP-80, Class 150, bronze body, horizontal swing, Y pattern, renewable seat and disc. Solder or threaded ends to suit piping.

Sizes over 2 inches:

Manufacture: Nibco F-918-B.

MSS SP-71, Class 125, cast iron body, fluid to 450°F, bolted bonnet, horizontal swing, renewable disc seal and seat, flanged end.

Silent check valve

Size up to 2 inches:

Manufacturer: Nibco 480 Series.

MSS SP-80, Class 125, bronze body, in line lift type, spring-actuated, TFE seat and disc, solder or threaded ends to suit piping.

Sizes over 2 inches:

Manufacturer: Nibco F-910-B.

MSS SP-125, Class 125, cast iron body, fluid to 200°F, renewable seats and disc, spring actuated, flanged.

PRESSURE REDUCING VALVES (PRV)

***************************************************************************************************

Comply with Mechanical Standard Drawings ST-D2020-2 for PRV piping details.

***************************************************************************************************

Manufacturer: CLA-VAL, No. 90-0IAS.

Single seated, hydraulically operated, pilot controlled, diaphragm type valve, 175 psi pressure rating, 180 degree F maximum water temperature and 15 to 75 psi adjustment range.  Pilot control; direct acting, adjustable, spring loaded, and normally open.  Valve construction; globe, ductile iron main valve body and cover, bronze main valve trim, and cast bronze pilot control with stainless steel trim. Repairs must be done without removing valve from line.

Optional Features: Flow clean features and CV flow control (opening speed control).

Capacity/Size:

Flow: [      ] gpm.

Size: [   ] inches with female NPT union ends or ANSI class 150 flanged ends.

pressure reducing valve (prv)

Manufacturer: CLA-VAL, No. 90-OIAB.

Single seated, hydraulically operated, pilot controlled, diaphragm type valve, 175 psi pressure rating, 180 degree F maximum water temperature and 15 to 75 psi adjustment range.  Pilot control; direct acting, adjustable, spring loaded, and normally open.  Valve construction; glove, ductile iron main valve body and cover, bronze main valve trim, and cast bronze pilot control with stainless steel trim. Repairs must be done without removing valve from line.

[Optional Features: Flow clean strainer and shutoff cocks to isolate pilot system.]

Capacity/Size:

Flow: [   ] gpm.

Size: [    ] inches with ANSI class 150 flanged ends.

Pressure Reducing valves (PRV)

Manufacturers:

CLA-VAL, No. 990.

Watts Regulator Company, No. 25AUB or No. U5B.

Balanced single seat with bronze valve body and cover, stainless steel trim, integral strainer, 160°F, maximum water temperature, and approx adjustments range [25-90] psi. Repairs must be done without removing valve from line.

Capacity/Size:

Flow: [   ] gpm.

Size: [    ] inches with NP t with union inlet connection.

CIRCULATOR PUMP, HOT WATER

Manufacturer: Bell and Gossett, Series [100].

Bronze body, brass impeller, steel shaft, suitable for 125 psi working pressure and 225°F water temperature, mechanical seal, direct drive, and oil lubricated drip proof motor, 1750 rpm.

Performance:

Flow: [     ] gpm at [     ] feet head.

Electrical: [     ] hp, [     ] volts, [     ] phase, 60 Hz.

COMMERCIAL GAS WATER HEATER

Manufacturer: Lochinvar, Charger Model [CNR   ].

Performance:

Storage capacity: [     ].gallons.

Input: [    ] Btuh at sea level.

Minimum Recovery Rate: [     ] gph at 100°F rise.

***************************************************************************************************

Specify ASME labeling for heaters larger than 199,000 Btuh.

***************************************************************************************************

Natural gas fired, automatic, vertical storage water heater, glass lined welded steel, [ASME labeled], multiple flue passages, inspection port, magnesium anodes, thermally insulated, encased in corrosion-resistant steel jacket, enamel finish.  Entire heater approved by AGA for operation at 180 °F, 7500 feet altitude installation.  Furnish with ASME rated temperature and pressure relief valve.

*******[OR]*******

***************************************************************************************************

Use the following for units with less than 400,000 Btuh input.

***************************************************************************************************

Controls: AGA certified, automatic water thermostat with adjustable temperature range from 120 to 180°F.  Automatic reset high temperature limiting thermostat factory set at 195°F, gas pressure regulator, multi-ribbon or tubular burner, 100 percent safety shut-off pilot and thermocouple, flue baffle and draft hood, and self-generating controls with no external power source.

***************************************************************************************************

Use the following for units with 400,000 Btuh input or more.

***************************************************************************************************

Controls: AGA certified, automatic direct immersion thermostat with temperature range adjustable minimum 175°F differential.  Automatic reset high temperature limiting thermostat factory set at 195°F.  Gas pressure regulator, multi-ribbon or tubular burner.  One-hundred percent safety shut-off pilot and thermocouple, intermittent electronic ignition monitoring pilot and main flame, trial for re-ignition for momentary loss of flame, shut down of pilot and main burner in 2 to 4 seconds after loss of flame, [automatic flue damper] [and power vent].  Control circuit 120 VAC with 24 VAC transformer.

Strainers

Sizes up to 2 inches:

Manufacturer: Keckley, Style F-150.

Threaded bronze body, 200 psi at 150°F WOG, Y pattern with standard 20 mesh stainless steel screen.

Size over 2 inches:

Manufacturer: Keckley, Style A.

Class 125 flanged iron body, 200 psi at 150°F WOG, Y pattern with standard 1/16 inch stainless steel perforated screen.

HOSE BIB (WALL HYDRANT)

Manufacturer: J.R. Smith Mfg. Co., Model 5609QT.

ANSI/ASME A112.21.3M, non-freeze, integral vacuum breaker, bronze or brass [nickel plated], 3/4 inch exposed hose connection, 1/4 turn, T-handle key.

BACKFLOW PREVENTER, THREADED ENDS

***************************************************************************************************

Comply with Mechanical Standard Drawings ST-D10-30GEN-1 for backflow preventer details.  The LANL Utilities Group water system representative shall approve design and installation of backflow preventers installed outside the building (see Spec 33 1000).

NOTE: BFP series listed below are for cold water service.

***************************************************************************************************

Provide models listed in the latest edition of Approved Backflow Prevention Assemblies by the University of Southern California Foundation for Cross Connection Control and Hydraulic Research.

Suggested Manufactures:

Conbraco, Series 40-200.

Wilkins, Series 975XL.

Watts, Series 909.

Assembly, reduce pressure type, bronze body, with ball type shutoff valves, FNPT ends, test cocks for in line field testing, integral unions between body and  shut-off valves, and air gap drain funnel. Maximum water temperature range 33 to 140°F, maximum rated working pressure 150 psi.

Size: [     ] inch.

BACKFLOW PREVENTER, FLANGED ENDS

Provide models listed in the latest edition of Approved Backflow Prevention Assemblies by the University of Southern California Foundation for Cross Connection Control and Hydraulic Research.

Suggested Manufactures:

Conbraco, Series 40200.

Wilkins, Series 975.

Watts, Series 909.

Assembly, reduced pressure type, cast iron body epoxy coated internal and external, with OS & Y shut-off valves, flanged ends, test cocks for in-line field testing, and an air gap drain funnel.  Maximum water temperature range 33 to 140°F, maximum rated working pressure 175 psi.

Size: [     ] inch.

PRESSURE GAUGE

***************************************************************************************************

Refer to manufacturer’s recommendation for gauge pressure ranges.  Generally, a pressure range of twice the expected normal pressure is recommended, with maximum working pressure not exceeding 75 percent of the range.  If pulsation occurs, working pressure should not exceed 65 percent of the pressure range.  Pressure gauges in the suction side of the pump will be vacuum pressure gauges.

***************************************************************************************************

Manufacturer: Ashcroft, Type 1009

B.	ASME B40.100, Accuracy Grade 1A, maximum plus or minus 1 percent full scale accuracy, minimum 2 1/2 inch dial, stainless steel case, phosphor bronze bourdon tube and 1/4 inch NPT brass bottom connection.  Furnish with brass ball valve.

Range: [     ] psi or [See drawings].

EXECUTION

  - PREPARATION

Ream pipe and tube ends.  Remove burrs.

Remove scale and dirt on inside and outside of pipe before assembly.

Keep open ends of pipe free from scale and dirt. Protect open ends with temporary plugs or caps.

BURIED PIPING

Provide earth cover, bedding, and warning tape per Drawings and Section 31 2000, Earth Moving.

INSTALLATION

Comply with Uniform Plumbing Code (IAMPO), and as applicable with AWWA C600, AWWA M41, and AWWA M23.

Provide non-conducting dielectric connections wherever jointing dissimilar metals.

Route piping in orderly manner and maintain gradient.  Route parallel and perpendicular to walls

Install piping to maintain headroom and neither interfere with use of space nor take more space than necessary.

Group piping whenever practical at common elevations.

Install piping to allow for expansion and contraction without stressing pipe, joints, or connected equipment.

Provide access where valves and other equipment are not exposed.

Install valves with stems upright or horizontal, not inverted.

Pipe relief from safety valves and backflow preventers to nearest floor drain.

Slope water piping and provide drain valves at low points.

Sleeve and caulk pipes penetrating exterior walls or interior bearing walls.  Provide waterproof installation for exterior walls.  Provide UL/FM approved through-penetration firestop system when penetrating fire-rated barriers (e.g., walls, floors, etc.).

Paint exposed piping in occupied spaces to match background color.

Install chrome-plated steel escutcheons where pipes are not insulated in finished areas.

Provide stops on waterlines for plumbing fixtures.

Above Grade Piping: Provide ball valves or gate valves in piping 2 inches and smaller and butterfly valves in piping 2 1/2 inches and larger.  Provide globe valves for throttling application.

Support piping system in accordance with Section 22 0529.

Sleeve pipe penetration and caulk in accordance with Section 22 0548, Vibration and Seismic Control for Plumbing Piping and Equipment.

Disinfect water distribution system in accordance with Section 22 0816.

Pressure test piping system in accordance with Section 22 0813.

Label piping system in accordance with Section 22 0554.

Insulate piping system in accordance with Section 22 0713.

END OF SECTION

************************************************************

Do not delete the following reference information:

************************************************************

FOR LANL USE ONLY

This project specification is based on LANL Master Specification 22 1100 Rev. 3, dated September 15, 2009.