SECTION 22 1413

FACILITY STORM DRAINAGE PIPING

*************************************************************************************************************

LANL MASTER SPECIFICATION

This template must be edited for each project.  In doing so, specifier must add job-specific requirements.  Brackets are used in the text to indicate designer choices or locations where text must be supplied by the designer.  Once the choice is made or text supplied, remove the brackets.  The specifications must also be edited to delete specification requirements for processes, items, or designs that are not included in the project -- and specifier’s notes such as these.  To seek a variance from requirements in the specifications that are applicable, contact the Engineering Standards Manual Mechanical POC. Please contact POC with suggestions for improvement as well.

When assembling a specification package, include applicable specifications from all Divisions, especially Division 1, General requirements.

Specification developed for ML-4 projects.  For ML-1, 2, and 3 applications, additional requirements and independent reviews should be added if increased confidence in procurement or execution is desired; see ESM Chapter 1 Section Z10 Specifications and Quality sections.
*************************************************************************************************************

GENERAL

1.1	SECTION INCLUDES

- Building storm drainage piping, fittings, and accessories within building wall.

1.2	SUBMITTALS

- Submit the following in accordance with Section 01 3300, Submittal Procedures:

- Catalog data on pipe materials, fittings and accessories.

- Installation instructions for accessories.

PRODUCTS

2.1	PRODUCT OPTIONS AND SUBSTITUTIONS

A.	Alternate products may be accepted; follow Section 01 2500, Substitution Procedures.

2.2	STORM DRAINAGE PIPING, ABOVE GROUND

A.	Cast Iron Pipe and Fittings: CISPI 301 hubless, service weight.

1.	Joints:  CISPI 310, neoprene gaskets and stainless steel clamp/shield assemblies.

B.	Cast Iron Pipe and Fittings: ASTM A74, service weight.

1.	Joints:  Bell and spigot, ASTM C564, rubber gaskets.

C.	PVC Pipe and Fittings: ASTM D3034, SDR 35.

      - Joints:  Bell and spigot, ASTM D3212, rubber gaskets.

D.	PVC Pipe and Fittings: ASTM D3034 or ASTM D2665.

      - Joints:  Solvent weld, ASTM D2855, with ASTM D2564 solvent cement.

2.3	ROOF DRAINS

A.	Manufacturer:  J.R. Smith Mfg. Co.

B.	[Select roof drains determined by roof construction, expected rainfall, etc.  Refer to manufacturer’s catalog data for selection criteria.]

2.4	CLEANOUTS

- Manufacturer:  J.R. Smith Mfg. Co.

- [Select cleanouts to suit project.  Refer to manufacturer’s catalog data for selection criteria.]

EXECUTION

3.1	EXAMINATION

A.	Verify excavations are to required grade.  Do not over excavate.

3.2	PREPARATION

A.	Ream pipe ends and remove burrs.

3.3	INSTALLATION

A.	Comply with Uniform Plumbing Code (IAPMO).

B.	Extend cleanouts to finish floor or wall surface.  Lubricate threaded cleanout plugs with non-hardening thread lubricant.  Ensure clearance at cleanout for snaking drainage system.

C.	Install floor cleanouts at elevation to accommodate finished floor.

D.	Route piping in orderly manner and maintain gradient.  Route parallel and perpendicular to walls.

E.	Install piping penetrating roofed areas to maintain integrity of roof assembly.

F.	Install bell and spigot pipe with bell end upstream.

- Sleeve and caulk pipes penetrating exterior walls or interior bearing walls.  Provide waterproof installation for exterior walls.  Provide UL/FM approved through-penetration firestop system when penetrating fire-rated barriers (i.e., walls, floors, etc.).

H.	Test piping system with water in accordance with Section 22 0813, Testing Piping Systems.

    - Label piping in accordance with Section 22 0554, Identification of Plumbing, HVAC and Fire Piping and Equipment.

J.	Support piping in accordance with Section 22 0529, Hangers and Support for Plumbing Piping and Equipment.

K.	Provide splash blocks under downspout nozzle when required to control erosion.

END OF SECTION

************************************************

Do not delete the following information:

************************************************

FOR LANL USE ONLY

This project specification is based on LANL Master Specification 22 1413 Rev. 1, dated June 10, 2008.