SECTION 22 3700

DOMESTIC WATER HEATERS

*************************************************************************************************************

LANL MASTER SPECIFICATION

This template must be edited for each project.   In doing so, specifier must add job-specific requirements.  Brackets are used in the text to indicate designer choices or locations where text must be supplied by the designer.  Once the choice is made or text supplied, remove the brackets.  The specifications must also be edited to delete specification requirements for processes, items, or designs that are not included in the project -- and specifier’s notes such as these.  This specification template must be tailored to meet requirements contained in the LANL Engineering Standards Manual (ESM). To seek a variance from requirements of the ESM that are applicable, contact the Engineering Standards Manual Mechanical POC. Please contact POC with suggestions for improvement as well.

When assembling a specification package, include applicable specifications from all Divisions, especially Division 1, General requirements.

This Specification is developed for ML-4 projects.  For ML-1, 2, and 3 applications, additional requirements and independent reviews should be added if increased confidence in procurement or execution is desired; see ESM Chapter 1 Section Z10 Specifications and Quality sections.

Seismic: In order to edit this section for Project-specific seismic requirements, refer to author notes that say/begin with “Seismic” and the Seismic Specification Guide for Nonstructural Components: Mechanical Components posted with the templates for guidance on properly editing this section.

*************************************************************************************************************

GENERAL

SUMMARY

Section Includes:

Gas-fired water heaters.

Electric water heaters.

Electric, tankless water heaters.

Water heater accessories.

PERFORMANCE REQUIREMENTS

Water Heaters shall perform satisfactorily in the following service conditions:

      - Elevation:  7500 feet above sea level.

      - Maximum ambient temperature:  104 degrees F.

      - Minimum ambient temperature:  Minus 20 degrees F.

          - 24-hour average temperature:  not exceeding 86 degrees F.

********************************************************

Seismic

********************************************************

- [Seismic Protection and Performance:  The seismic protection and performance of Water Heaters shall be in accordance with Section 22 0548.23, Vibration and Seismic Controls for Mechanical Systems.].

ACTION SUBMITTALS

Product Data:  For each type and size of water heater indicated, include rated capacities, operating characteristics, electrical characteristics, and furnished specialties and accessories.  Include documentation indicating that units comply with applicable requirements in ASHRAE/IESNA 90.1, Section 7, Service Water Heating [or Energy Star].

Shop Drawings:  Wiring Diagrams for power, signal, and control wiring.

Certification of welders and qualified welding procedure per Sections [01 4444] [and] [01 4455].

Product Certificates:  For each type of [electric,] [tankless,] [gas-fired] water heater from manufacturer.

Test Reports:  For each type of [electric,] [tankless,] [gas-fired] water heater. [Include factory test reports]

Water Heater Labeling:  Certified and labeled by testing agency acceptable to authorities having jurisdiction. [UL, AGA, ASME, ASHRAE, CSA, NSF]

Energy Efficiency

Indicate EER (Energy Efficiency Rating) or Energy Factor (EF) for equipment provided under work of this Section.

Submit documentation for Energy Star qualifications for equipment provided under work of this Section.

CLOSEOUT SUBMITTALS

Operation and Maintenance Data:  Include emergency, operation, and maintenance manuals.

Warranty: Provide documentation of [One] [Three] [Five] [____] year warranty.

QUALITY ASSURANCE

Electrical Components, Devices, and Accessories:  Listed and labeled as defined in NFPA 70, by a Nationally Recognized Testing Laboratory (NRTL) recognized under 29 CFR 1910.7.

ASHRAE/IESNA Compliance:  Fabricate and label water heaters to comply with ASHRAE/IESNA 90.1-[2013].

ASME Compliance:  Where ASME-code construction is indicated, fabricate and label water heater storage tanks to comply with ASME Boiler and Pressure Vessel Code:  Section VIII, Division 1.

NSF Compliance:  Fabricate and label equipment components that will be in contact with potable water to comply with NSF/ANSI 61-[2016], Drinking Water System Components - Health Effects.

WARRANTY

Special Warranty:  Manufacturer's standard form in which manufacturer agrees to repair or replace components of electric water heaters that fail in materials or workmanship within specified warranty period.

Failures include, but are not limited to, the following:

Structural failures including storage tank and supports.

Faulty operation of controls.

Deterioration of metals, metal finishes, and other materials beyond normal use.

Warranty Periods:  [Three] [Five] [10] years from date of Substantial Completion.

PRODUCTS

GAS-FIRED, WATER HEATERS

Gas-Fired, Storage Water Heaters

Manufacturers:  Subject to compliance with requirements, provide products by one of the following:

American Water Heaters.

Bradford White Corporation.

Lochinvar Corporation.

Rheem Manufacturing Company.

Smith, A. O. Water Products Co.; a Division of A. O. Smith Corporation.

Standard:  ANSI [Z21.10.1, 75 MBH or less] [Z21.10.3, greater than 75 MBH].

Tank Construction:  [ASME-code, above 200 MBH or 120 gallon storage] steel with 150-psig working-pressure rating.

Tappings:  Factory fabricated of materials compatible with tank.  Attach tappings to tank before testing.

              - NPS 2 and Smaller:  Threaded ends according to ASME B1.20.1.

              - NPS 2-1/2 and Larger:  Flanged ends according to ASME B16.5 for steel and stainless-steel flanges, and according to ASME B16.24 for copper and copper-alloy flanges.

Interior Finish:  Comply with NSF/ANSI 61-[2016] barrier materials for potable-water tank linings, including extending finish into and through tank fittings and outlets.

Lining:  [Cement] [Glass] [Nickel plate] [Phenolic coating] [Sheet copper] complying with NSF/ANSI 61-[2016] barrier materials for potable-water tank linings, including extending lining into and through tank fittings and outlets.

Factory-Installed Storage-Tank Appurtenances:

Anode Rod:  Replaceable magnesium.

Dip Tube:  Required unless cold-water inlet is near bottom of tank.

Drain Valve: Corrosion-resistant metal.

Insulation: Comply with ASHRAE/IESNA 90.1. Surround entire storage tank except connections and controls.

Jacket: Steel with enameled finish.

Burner:  For use with atmospheric, gas-fired water heaters and natural-gas fuel.

Automatic Ignition: ANZI Z21.20, electric, automatic, gas-ignition system.

Temperature Control: Adjustable thermostat.

Safety Controls: Automatic, high-temperature-limit and low-water cutoff devices or systems.

Combination Temperature-and-Pressure Relief Valves:  ASME Rated or ANSI Z21.22 certified.  Include one or more relief valves with total relieving capacity at least as great as heat input, and include pressure setting less than the water heater working-pressure rating.  Select one relief valve with sensing element that extends into storage tank.

Special Requirements:  NSF 5 construction.

Capacity and Characteristics:

Minimum Energy Factor (EF) of 0.67 (meets Energy Star criteria) for units less than or equal to 55 gallons [0.77 EF for greater than 55 gallons] with a nominal input of 75,000 BTH/hour or less. Minimum EF of 0.8 for condensing water heaters.

Storage Capacity:  [     ] gallons.

Minimum Recovery Rate:  [     ] gph at 100°F temperature rise.

Temperature Setting:  125 deg F.

Fuel Gas Demand:  [     ] cfh.

Fuel Gas Input:  [       ] Btu/h.

Gas Pressure Regulator:

              - Capacity:  [     ] cfh.

              - Inlet Pressure:  [     ] psig or inches water column.

              - Gas Pressure Required at Burner:  [     ] psig or inches water column.

Electrical Characteristics:

              - Volts:  [120] [240].

              - Phase:  [Single] [Three].

              - Hertz:  60.

i.	Minimum Vent Diameter:  [    ] inches.

ELECTRIC, WATER HEATERS

***********************************************************************************************************

Specify electric water heaters only where natural gas is not available, or where routing a flue pipe is not practical. In this case, consider an Energy Star qualified Heat Pump Water Heater.

************************************************************************************************************

Electric Water Heaters

Manufacturers:  Subject to compliance with requirements, provide products by one of the following:

Bradford White Corporation.

Electric Heater Company (The).

Lochinvar Corporation.

Rheem Manufacturing Company.

Smith, A. O. Water Products Co.; a Division of A. O. Smith Corporation.

Standard:  [UL 1453] [UL 174].

Tank Construction:  [Corrosion-resistant metal] [or] [steel steel with corrosion-resistant coating] [horizontal] [vertical] arrangement.

Tappings:  ASME B1.20.1 pipe thread.

Pressure Rating:  150 psig.

Interior Finish:  Comply with NSF/ANSI 61-[2016] barrier materials for potable-water tank linings, including extending lining material into tappings.

Factory-Installed Tank Appurtenances:

Anode Rod:  Replaceable magnesium.

Dip Tube:  Required unless cold-water inlet is near bottom of tank.

Drain Valve:  Corrosion-resistant metal if tank has drain outlet.  Provide hose-end drain valve in piping for -water heaters without drain outlet.

Insulation:  Comply with ASHRAE/IESNA 90.1-[2013].

Jacket:  Rectangular shaped, with stainless-steel front panel, unless otherwise indicated.

Heat-Trap Fittings:  Inlet type in cold-water inlet and outlet type in hot-water outlet.

Heating Elements:  Electric, screw-in [or bolt-on] immersion type.

Temperature Control:  Adjustable thermostat.

Safety Controls:  High-temperature-limit and low-water cutoff devices or systems.

Relief Valve:  ASME Rated or ANSI Z21.22 certified combination temperature-and-pressure relief valve.  Include relieving capacity at least as great as heat input, and include pressure setting less than the water heater working-pressure rating.  Select relief valve with sensing element that extends into storage tank.

Special Requirements:  NSF 5 construction with legs for floor installation.

Capacity and Characteristics:

Storage Capacity:  [     ] gallons.

Minumum Recovery Rate:  [     ] gph at 100°F temperature rise.

Temperature Setting:  [120 deg F] [140 deg F] [180 deg F].

Power Demand:  [     ] kilowatts.

Heating Elements:

              - Number of Elements:  [One] [Two] [Three].

              - Kilowatts Each Element:  [     ] kilowatts.

              - Number of Stages:  [One] [Two] [Three].

Electrical Characteristics:

              - Volts:  [120] [240] [277] [480].

              - Phases:  [Single] [Three].

              - Hertz:  60.

Electric, Tankless, Water Heaters:

Manufacturers:  Subject to compliance with requirements, provide products by one of the following:

Bosch Water Heating.

Chronomite Laboratories, Inc.

American Hometec, Inc

Eemax, Inc.

E-Tankless Water Heaters Corp.

Keltech, Inc.

Niagara Industries, Inc.

Stiebel Eltron, Inc.

Standard:  UL 499 for electric, tankless, water heater.

Construction:  Copper piping or tubing complying with NSF 61 barrier materials for potable water, without storage capacity.

Connections:  ASME B1.20.1 pipe thread.

Pressure Rating:  150 psig.

Heating Element:  Resistance heating system.

Temperature Control:  [Flow-control fitting] [Thermostat].

Safety Control:  High-temperature-limit cutoff device or system.

Jacket:  Aluminum or steel with enameled finish or plastic.

Support:  Bracket for wall mounting.

Capacity and Characteristics:

Flow Rate:  [     ] gpm.

Maximum Temperature Setting:  [100 deg F] [125 deg F] [140 deg F].

Power Demand:  [    ] kilowatts.

Electrical Characteristics:

              - Volts:  [120] [240] [277] [480].

              - Phases:  [Single] [Three].

              - Hertz:  60.

WATER HEATER ACCESSORIES

*******************************************************************************************

Select one or more of the following subparagraphs appropriate to equipment requirements.

*******************************************************************************************

Drain Pans:  Corrosion-resistant metal with raised edge.  Comply with ANSI LC 3.  Include dimensions not less than base of water heater, and include drain outlet not less than NPS 3/4 with ASME B1.20.1 pipe threads or with ASME B1.20.7 garden-hose threads.

Piping-Type Heat Traps:  Field-fabricated piping arrangement according to ASHRAE/IESNA 90.1.

Heat-Trap Fittings:  ASHRAE 90.1.

Pressure-Reducing Valves:  ASSE 1003-[2009] for water.

Shock Absorbers:  ASSE 1010 or PDI-WH 201, Size A water hammer arrester.

Water Heater Stands:  Manufacturer's factory-fabricated steel stand for floor mounting, capable of supporting the water heater and water content.  Include dimension that will support bottom of water heater a minimum of 18 inches above the floor.

************OR************

Water Heater Mounting Brackets:  Manufacturer's factory-fabricated steel bracket for wall mounting, capable of supporting the water heater and water content.

Gas Shutoff Valves:  ANSI Z21.15, manually operated.  Furnish for installation in piping.

Gas Pressure Regulators: ANSI Z21.18, appliance type. Include [1/2-psig] [2-psig] [5-psig] pressure rating as required to match gas supply.

Automatic Gas Valves:  ANSI Z21.21, appliance, electrically operated, on-off automatic valve.

SOURCE QUALITY CONTROL

Factory Tests:  Test and inspect water heaters specified to be ASME-code construction, according to ASME Boiler and Pressure Vessel Code.

Hydrostatically test water heaters to minimum of one and one-half times pressure rating before shipment.

EXECUTION

INSTALLATION

Water Heater Mounting:  Install water heaters on concrete base.  Comply with requirements for concrete bases specified in Section 03 3001, Reinforced Concrete or Section 03 3053, Miscellaneous Cast-in-Place Concrete.

Exception:  Omit concrete bases for water heaters if installation on stand, bracket, suspended platform, or directly on floor is indicated.

Maintain manufacturer's recommended clearances.

Arrange units so controls and devices that require servicing are accessible.

Install dowel rods to connect concrete base to concrete floor.  Unless otherwise indicated, install dowel rods on 18-inch centers around the full perimeter of concrete base.

For supported equipment, install epoxy-coated anchor bolts that extend through concrete base and anchor into structural concrete floor.

Place and secure anchorage devices.  Use setting drawings, templates, diagrams, instructions, and directions furnished with items to be embedded.

Install anchor bolts to elevations required for proper attachment to supported equipment.

Anchor water heaters to substrate.

Install water heaters level and plumb, according to layout drawings, original design, and referenced standards.  Maintain manufacturer's recommended clearances.  Arrange units so controls and devices needing service are accessible.

Install shutoff valves on water-supply piping to water heaters and on hot water outlet piping.

Electric, Tankless Water Heater Mounting:  Install electric, tankless water heaters at least 18 inches above floor on wall bracket.

Maintain manufacturer's recommended clearances.

Arrange units so controls and devices that require servicing are accessible.

Place and secure anchorage devices.  Use setting drawings, templates, diagrams, instructions, and directions furnished with items to be embedded.

Install anchor bolts to elevations required for proper attachment to supported equipment.

Anchor water heaters to substrate.

Provide pressure and temperature relief valve [when required by UPC, Section 608.3].

Install gas-fired water heaters according to NFPA 54.

          - Install gas shutoff valves on gas supply piping to gas-fired, water heaters.

          - Install gas pressure regulators on gas supplies to gas-fired, water heaters without gas pressure regulators if gas pressure regulators are required to reduce gas pressure at burner.

          - Install automatic gas valves on gas supplies to gas-fired, water heaters if required for operation of safety control.

          - Comply with requirements for gas shutoff valves, gas pressure regulators, and automatic gas valves specified in Section 23 1123, Facility Natural-Gas Piping.

Install combination temperature-and-pressure relief valves in top portion of storage tanks.  Use relief valves with sensing elements that extend into tanks.  Extend commercial-water-heater relief-valve outlet, with drain piping same as water piping in continuous downward pitch, and discharge by positive air gap into closest floor drain.

Install combination temperature-and pressure relief valves in water piping for electric -water heaters without storage.  Extend commercial-water-heater relief-valve outlet, with drain piping same as water piping in continuous downward pitch, and discharge by positive air gap into closest floor drain.

Install water-heater drain piping as indirect waste to spill by positive air gap into open drains or over floor drains.  Install hose-end drain valves at low points in water piping for electric water heaters that do not have tank drains.

Install thermometers on outlet piping of electric water heaters.

Assemble and install inlet and outlet piping manifold kits for multiple electric water heaters.  Fabricate, modify, or arrange manifolds for balanced water flow through each electric water heater.  Include shutoff valve and thermometer in each water heater inlet and outlet, and throttling valve in each electric water heater outlet.

Install pressure-reducing valve with integral bypass relief valve in electric water booster-heater inlet piping and water hammer arrester in booster-heater outlet piping.  Set pressure-reducing valve for outlet pressure of 25 [     ] psig.

Install piping-type heat traps on inlet and outlet piping of electric water heater storage tanks without integral or fitting-type heat traps.

Fill water heaters with water.

CONNECTIONS

Comply with requirements for piping specified in Section 22 1100, Facility Water Distribution.  Drawings indicate general arrangement of piping, fittings, and specialties.

Comply with requirements for gas piping specified in Section 23 1123, Facility Natural-Gas Piping.

Where installing piping adjacent to water heaters, allow space for service and maintenance of water heaters.  Arrange piping for easy removal of water heaters.

IDENTIFICATION

Identify system components.  Comply with requirements for identification specified in Section 22 0554, Identification for Plumbing Piping and Equipment.

FIELD QUALITY CONTROL

Perform tests.

Leak Test:  After installation, charge system and test for leaks.  Repair leaks and retest until no leaks exist. If water heater leaks, do not attempt repair.

Operational Test:  After electrical circuitry has been energized, start units to confirm proper operation.

Test and adjust controls and safeties.  Replace damaged and malfunctioning controls and equipment.

Water heaters will be considered defective if they do not pass tests.

Prepare test reports.

END OF SECTION

****************************************************************

Do not delete the following reference information.

*****************************************************************

THE FOLLOWING STATEMENT IS FOR LANL USE ONLY

This project specification section is based on LANL Master Specification Section 22 3700 Rev. 1, dated March 29, 2018.