SECTION 23 2113

HYDRONIC PIPING

*************************************************************************************************************

LANL MASTER SPECIFICATION

This section is for water from vacuum to 150 psig and temperature from 0–250 deg F, and for steam and condensate from vacuum to 150 psig and 0–366 deg F.

This template must be edited for each project. In doing so, Specifier must add job-specific requirements. Brackets are used in the text to indicate designer choices or locations where text must be supplied by the designer.  Once the choice is made or text supplied, remove the brackets.  The specifications must also be edited to delete specification requirements for processes, items, or designs that are not included in the project -- and specifier’s notes such as these.

To seek a variance from requirements in the specifications that are applicable, contact the Engineering Standards Manual Mechanical POC. Please contact POC with suggestions for improvement as well.

When assembling a specification package, include applicable specifications from all Divisions, especially Division 1, General requirements.

Section developed for ML-4 projects.  For ML-1, 2, and 3 applications, additional requirements might be necessary if increased confidence in procurement or execution is desired, and independent review is necessary.  See ESM Chapter 1 Section Z10 Specifications and Quality sections.
*************************************************************************************************************

GENERAL

SECTION INCLUDES

Site and building pipe materials, fittings, valves, and accessories for process cooling water, chilled water, heating hot water, tower water, blow down piping, equipment drains, and overflow piping.

[For water treatment piping, see Section 23 2500, HVAC Water Treatment.]

[For potable water systems, see Section 22 1100, Facility Water Distribution.]

[For make-up water systems for cooling towers and process water loop see Section 22 1100, Facility Water Distribution.]

RELATED SECTIONS

Section 01 4200, References.

Section 01 2500, Substitution Procedures.

Section 01 4000, Quality Requirements.

Section 01 4444, Offsite Welding & Joining Requirements.

Section 01 4455, Onsite Welding & Joining Requirements.

Section 01 7828, Pressure Safety Closeout Submittals

Section 22 0529, Hangers and Supports for Plumbing Piping and Equipment.

Section 22 0548, Vibration and Seismic Controls for Plumbing, Piping and Equipment.

Section 22 0554, Identification for Plumbing, HVAC, and Fire Piping Equipment.

Section 22 0713, Plumbing and HVAC Insulation.

Section 22 0813, Testing Piping Systems.

Section 23 2500, HVAC Water Treatment.

REFERENCES

The following are the code of record that the design and fabrication must meet.

ASME B31.9 – [YEAR]

*************************************************************************************************************

In the listing below, Designer must eliminate standards that are not applicable to the project. Then, designer must either (1) specify each B31.9-listed materials’ national standard edition for each remaining standard listed or (2) determine latest is equivalent.  Then modify 1.3.B to either (1) keep the first option—and also list the edition year after each standard number (e.g., ASTM F493-04) or (2) keep the second option.

*************************************************************************************************************

[All national standards invoked herein shall be taken to be the edition in effect for the code of record listed above in 1.3.A and shown below, unless noted otherwise]  [All national standards invoked below and herein shall be taken to be the latest edition].

astm International

ASTM A48,Standard Specification for Gray Iron Castings

ASTM A53, Standard Specification for Pipe, Steel, Black and Hot-Dipped, Zinc-Coated, Welded and Seamless

ASTM A105, Standard Specification for Carbon Steel Forgings for Piping Applications

ASTM A108, Standard Specification for Steel Bar, Carbon and Alloy, Cold-Finished

ASTM A126, Standard Specification for Gray Iron Castings for Valves, Flanges, and Pipe Fittings

ASTM A197, Standard Specification for Cupola Malleable Iron

ASTM A234, Standard Specification for Piping Fittings of Wrought Carbon Steel and Alloy Steel for Moderate and High Temperature Service

ASTM A307, Standard Specification for Carbon Steel Bolts, Studs, and Threaded Rod 60000 PSI Tensile Strength

ASTM A536, Standard Specification for Ductile Iron Castings

ASTM A575, Standard Specification for Steel Bars, Carbon, Merchant Quality, M-Grades

ASTM B16, Standard Specification for Free-Cutting Brass Rod, Bar and Shapes for Use in Screw Machines

ASTM B32, Standard Specification for Solder Metal

ASTM B68, Standard Specification for Seamless Copper Tube, Bright Annealed

ASTM B75, Standard Specification for Seamless Copper Tube

ASTM B88, Standard Specification for Seamless Copper Water Tube

ASTM B280, Standard Specification for Seamless Copper Tube for Air Conditioning and Refrigeration Field Service

ASTM B584, Standard Specification for Copper Alloy Sand Castings for General Applications

ASTM D1785, Standard Specification for Poly(Vinyl Chloride) (PVC) Plastic Pipe, Schedules 40, 80, and 120

ASTM D2466, Standard Specification for Poly(Vinyl Chloride) (PVC) Plastic Pipe Fittings, Schedule 40

ASTM D2467, Standard Specification for Poly(Vinyl Chloride) (PVC) Plastic Pipe Fittings, Schedule 80

ASTM D2564, Standard Specification for Solvent Cements for Poly(Vinyl Chloride) (PVC) Plastic Piping Systems

ASTM D2855, Standard Practice for the Two-Step (Primer and Solvent Cement) Method of Joining Poly (Vinyl Chloride) (PVC) or Chlorinated Poly (Vinyl Chloride) (CPVC) Pipe and Piping Components with Tapered Sockets

ASTM F1545, Standard Specification for Plastic-Lined Ferrous Metal Pipe, Fittings, and Flanges

ASTM G62, Standard Test Methods for Holiday Detection in Pipeline Coatings

American Welding Society: AWS A 5.8, Specification for Filler Metals for Brazing and Braze Welding

American Water Works Association

AWWA C110, Ductile-Iron and Gray-Iron Fittings

AWWA C111, Rubber-Gasket Joints for Ductile-Iron Pressure Pipe and Fittings

AWWA C151, Ductile-Iron Pipe, Centrifugally Cast

AWWA C153, Ductile-Iron Compact Fittings

AWWA C606, Grooved and Shouldered Joints

Manufacturers Standardization Society of the Valve and Fittings Industry.

MSS SP-25, Standard Marking System for Valves, Fittings, Flanges, and Unions

MSS SP-67, Butterfly Valves

MSS SP-70, Gray Iron Gate Valves, Flanged and Threaded Ends

MSS SP-71, Gray Iron Swing Check Valves, Flanged and Threaded Ends

MSS SP-72, Ball Valves with Flanged or Butt-Welding Ends for General Service

MSS SP-80, Bronze Gate, Globe, Angle, and Check Valves

MSS SP-85, Gray Iron Globe & Angle Valves, Flanged and Threaded Ends

MSS SP-110, Ball Valves Threaded, Socket-Welding, Solder Joint, Grooved and Flared Ends

MSS SP-125, Gray Iron and Ductile Iron In-Line, Spring-Loaded, Center-Guided Check Valves

UL 207, Standard for Safety Refrigerant-Containing Components and Accessories, Nonelectrical

SUBMITTALS

ACTION submittals.  Submit the following in accordance with submittal procedures prior to work:

Catalog data on pipe materials, fittings, valves, and accessories.

Installation instructions for valves and accessories.

Welding procedures and qualifications.

Certifications of welders and qualified welding procedures.

Examination processes and forms and examiner qualifications for LANL review prior to commencing work.

CLOSEOUT Submittals.

Follow Section 01 4115 Pressure Safety Submittals regarding required documentation.  In addition, provide:

Installation examination evidence documentation required by Article 3.1 of this Section.

QUALITY ASSURANCE

Welders Certification and Qualified Procedure Standards shall be in accordance with Section IX of ASME Boiler and Pressure Vessel Code. Welding per Sections [01 4444 and/or 01 4455].

Valve Identification:  Each valve shall bear markings in accordance with MSS SP-25, including manufacturer’s name or trademark, the material of construction, and symbols to indicate the service conditions for which the manufacturer rates the valve.

Component identification shall follow ESM Chapter 1, 200, Equipment and Numbering & Labeling.  At existing facilities, component labeling conventions are to be continued to be used to avoid confusion.

PRODUCTS

  - PRODUCT OPTIONS AND SUBSTITUTIONS

Alternate products may be accepted; follow Section 01 2500, Substitution Procedures.

*************************************************************************************************************WARNING to DESIGNER on BRAZING:  When specifying brazed joints, consider that brazing reduces the tube rating to the fully annealed condition.

*************************************************************************************************************

*************************************************************************************************************

Direction to Designer on welding:  Drawings shall include welding symbols complying with AWS A2.4 and showing weld size(s)

*************************************************************************************************************

*************************************************************************************************************

Direction to Designer on flanges:  Flange joint design must comply with ASME PCC-1.

*************************************************************************************************************

*************************************************************************************************************

NOTE to designer:  Copper tubing thickness callouts throughout are below based on LANL Alternate Method VAR- 2015-011

*************************************************************************************************************

HEATING WATER PIPING, BURIED (SERVICE UP TO 250 DEG F)

    - Copper Tubing: Alloy [102, 122], temper [drawn H and/or annealed O].  Thickness per UL 207, ASTM B88, B75, B68, or B280.

      - Braze Joints

Fittings: ASME B16.22, wrought copper and copper alloy, solder joint pressure fittings [and/or] ASME B16.18 cast copper alloy solder joint pressure fittings

[Manufacturers and model numbers]

Use AWS A5.8 TB-BCuP-5 silver braze.

Comply with [01 4444, 01 4455].

Solder joint

application is restricted to [compressed air, non-flammable gas, non-toxic gas, non-toxic liquids] less than 4.125 inch OD.

Fittings: ASME B16.22, wrought copper and copper alloy, solder joint pressure fittings [and/or] ASME B16.18 cast copper alloy solder joint pressure fittings

[Manufacturers and model numbers]

Solder in accordance with ASTM B32, Alloy Grade [Sb5, Sn50, other] or UNS [L13950, L55031, other].

Flux [manufacturer, material]

Coating:  See Part 3, Corrosion Control

Pipe: Black steel, ASTM A53, type [E, F, S], grade [A, B], wall thickness [standard wall].  Bolted or mechanical joints for pipe sizes greater than 2 inches.  Threaded joints per ASME B1.20.1 for pipe sizes 2 inches and under.

Threaded Joints:

Fittings: Black steel, ASTM A234, butt-welding type, ASME B16.9, [and/or], ASTM A197, ASME B16.3 malleable threaded type ASME B1.20.1.

[Manufacturer and model numbers]

Bolted Joints:

Flanges and Flanged Fittings: Black steel, ASTM A105, ASME B16.5 class [150, 300, …2500].

Fittings: ASME B16.42 Ductile Iron Pipe Flanges and Flanged Fittings, class [150, 300].

Fittings: Black steel, ASTM A234, Grade WPB, butt-welded type, ASME B16.9, [standard wall].

Fittings: ASME B16.28,  Wrought Steel Butt-welding Short Radius Elbows and Returns

Gaskets conforming to ASME B 16.5 Nonmandatory Appendix B, Limiting Dimensions of Gaskets Other Than Ring Joint Gaskets, Group Ia.  Gaskets used in ASME B16.5 flanges must satisfy the requirements of ASME B16.20a for metallic gaskets and ASME B16.21 for non-metallic flat gaskets.

Bolts and Studs: ASME [B18.2.1, …],[type of bolt], [nominal size], [thread class], [product length], [material], [finish (if required)]

Nuts: ASME B18.2.2, [type: heavy hex, heavy hex jam, hex thick slotted, etc…],[size], [thread class], [material], [finish (if required)]

Washers: ASME B18.21.1 [type: plain, helical, tooth-lock], [material], [hardness], [nominal size], [finish (if required)]

[Manufacturers and model numbers]

Welded Joints:

As shown in Drawings.

Outside Coating and/or Inside Lining: See Part 3, Corrosion Control

HEATING WATER PIPING, ABOVE GROUND (SERVICE UP TO 250 DEG F)

Copper tubing alloy [102, 122] per ASME B31.9 Table I-1. Temper [drawn H and/or annealed O].  Thickness per UL 207, ASTM B88, B75, B68, or B280.

Braze Joints

Fittings: ASME B16.22, wrought copper and copper alloy, solder joint pressure fittings [and/or] ASME B16.18 cast-copper-alloy solder-joint pressure-fittings

[Manufacturers and model numbers]

AWS A5.8 TB-BCuP-5 silver braze.

Comply with [01 4444, 01 4455].

Solder joint

application is restricted to [compressed air, non-flammable gas, non-toxic gas, non-toxic liquids] less than 4.125 inch OD.

Fittings: ASME B16.22, wrought copper and copper alloy, solder joint pressure fittings [and/or] ASME B16.18 cast-copper-alloy solder-joint pressure-fittings.

[Manufacturers and model numbers]

Solder in accordance with ASTM B32, Alloy Grade [Sb5, Sn50, other] or UNS [L13950, L55031, other].

Flux [manufacturer, material]

Pipe: Black steel, ASTM A53, type [E, F, S], grade [A, B], wall thickness [standard wall].  Bolted or mechanical joints for pipe sizes greater than 2 and up to 18 inches.  Threaded joints per ASME B1.20.1 for pipe sizes 2 inches and under.

Threaded Joints:

Fittings: Black steel, ASTM A234, butt welding type, ASME B16.9, [and/or], ASTM A197, ASME B16.3 malleable threaded type ASME B1.20.1.

[Manufacturers and model numbers]

Bolted Joints:

Flanges and Flanged Fittings: Black steel, ASTM A105, ASME B16.5 class [150, 300 … 2500].

Fittings: ASME B16.42 Ductile Iron Pipe Flanges and Flanged Fittings, class [150, 300].

Fittings: Black steel, ASTM A234, Grade WPB, butt-welded type, ASME B16.9, [standard wall].

Fittings: ASME B16.28,  Wrought Steel Butt-welding Short Radius Elbows and Returns

Gaskets: ASME B 16.5 Nonmandatory Appendix B, Limiting Dimensions of Gaskets Other Than Ring Joint Gaskets, Group Ia.  Gaskets used in ASME B16.5 flanges must satisfy the requirements of ASME B16.20a for metallic gaskets and ASME B16.21 for non-metallic flat gaskets.

Bolts and Studs: ASME B18.2.1, …],[type of bolt], [nominal size], [thread class], [product length], [material], [finish (if required)]

Nuts: ASME B18.2.2, [type: heavy hex, heavy hex jam, hex thick slotted, etc…],[size], [thread class], [material], [finish (if required)]

Washers: ASME B18.21.1 [type: plain, helical, tooth-lock], [material], [hardness], [nominal size], [finish (if required)]

[Manufacturer and model numbers]

Mechanical Joints:

Pipe ends per AWWA-C606, Grooved and Shouldered Type Joints, (aka Victaulic 177N) with formed fittings and couplings (Warning:  DO NOT use the reduced wall thickness fittings without express engineering direction).

Fittings AWWA C606 (aka Victaulic 177N), ductile or malleable iron, service rating 86–250 deg F meeting ASTM A 536, grade [60-42-10, 70-50-05].  Grooved and Shouldered Type Joints, (aka Victaulic 177N) with formed fittings and couplings (Warning:  DO NOT use the reduced wall thickness fittings without express engineering direction).

[Manufacturer and model numbers]

Welded Joints:

As shown in Drawings.

PROCESS COOLING WATER, ABOVE GRADE

Copper tubing alloy [102, 122] per ASME B31.9 Table I-1. Temper shall be [drawn H and/or annealed O].

Braze Joints

Fittings: ASME B16.22, wrought copper and copper alloy, solder joint pressure fittings [and/or] ASME B16.18 cast copper alloy solder joint pressure fittings

[Manufacturers And Model Numbers

Use AWS A5.8 TB-BCuP-5 silver braze.  (Note:  brazing reduces the tube rating to the fully annealed condition).

Comply with [01 4444, 01 44555].

Solder joint

Application is restricted to [compressed air, non-flammable gas, non-toxic gas, non-toxic liquids] less than 4.125 inch OD.

Fittings: ASME B16.22, wrought copper and copper alloy, solder joint pressure fittings [and/or] ASME B16.18 cast copper alloy solder joint pressure fittings

[Manufacturers and Model Numbers]

Solder in accordance with ASTM B32 [year or state latest], Alloy Grade [Sb5, Sn50, other] or UNS [L13950, L55031, other].

Flux [manufacturer, material]

Pipe Up to 2”: black steel ASTM A53, type [E, F, S] grade [A or B], wall thickness [schedule 80]. Threaded joints per ASME B1.20.1 for pipe sizes 2 inches and under.

Threaded Joints:

Fittings: Black steel, ASTM A234, butt welding type, ASME B16.9, [and/or], ASTM A197, ASME B16.3 malleable threaded type ASME B1.20.1.

[Manufacturer and model numbers]

Greater than 2 inches black steel ASTM A53, type [E, F, S] grade [A or B], wall thickness [standard wall] [welded or bolted or mechanical joints]

Bolted Joints:

Flanges and Flanged Fittings: Black steel, ASTM A105, ASME B16.5 class [150, 300, …2500].

Fittings: ASME B16.42 Ductile Iron Pipe Flanges and Flanged Fittings, class [150, 300].

Fittings: Black steel, ASTM A234, Grade WPB, butt-welded type, ASME B16.9, [standard wall].

Fittings: ASME B16.28,  Wrought Steel Butt-welding Short Radius Elbows and Returns

Gaskets: ASME B16.5 Nonmandatory Appendix B, Limiting Dimensions of Gaskets Other Than Ring Joint Gaskets, Group Ia.  Gaskets used in ASME B16.5 flanges must satisfy the requirements of ASME B16.20a for metallic gaskets and ASME B16.21 for non-metallic flat gaskets.

Bolts and Studs shall be ASME B18.2.1, …],[type of bolt], [nominal size], [thread class], [product length], [material], [finish (if required)]

Nuts shall be ASME B18.2.2, [type: heavy hex, heavy hex jam, hex thick slotted, etc…],[size], [thread class], [material], [finish (if required)]

Washers shall be ASME B18.21.1 [type: plain, helical, tooth-lock], [material], [hardness], [nominal size], [finish (if required)]

[Manufacturer and model numbers]

Mechanical Joints:

Pipe ends per AWWA-C606, Grooved and Shouldered Type Joints, (aka Victaulic 177N) with formed fittings and couplings (Warning:  DO NOT use the reduced wall thickness fittings without express engineering direction).

Fittings AWWA C606, (aka Victaulic 177N), ductile or malleable iron, service rating 86–250 deg F meeting ASTM A 536, grade [60-42-10, 70-50-05].  Grooved and Shouldered Type Joints, (aka Victaulic 177N) with formed fittings and couplings (Warning:  DO NOT use the reduced wall thickness fittings without express engineering direction).

[Manufacturer and model numbers]

Welded joints

As shown in Drawings.

CHILLED WATER PIPING, BURIED

Copper Tubing: Alloy [102, 122], temper shall be [drawn H and/or annealed O].  Thickness per UL 207, ASTM B88, B75, B68, or B280.

Braze Joints

Fittings: ASME B16.22, wrought copper and copper alloy, solder joint pressure fittings [and/or] ASME B16.18 cast copper alloy solder joint pressure fittings

[Manufacturers and model numbers

AWS A5.8 TB-BCuP-5 silver braze.

Comply with [01 4444, 01 4455].

Solder joint

application is restricted to [compressed air, non-flammable gas, non-toxic gas, non-toxic liquids] less than 4.125 inch OD.

Fittings: ASME B16.22, wrought copper and copper alloy, solder joint pressure fittings [and/or] ASME B16.18 cast copper alloy solder joint pressure fittings

[Manufacturer and model numbers]

Solder in accordance with ASTM B32, Alloy Grade [Sb5, Sn50, other] or UNS [L13950, L55031, other].

Flux [manufacturer, material]

Coating: See Part 3, Corrosion Control.

Ductile Iron Pipe:

AWWA C151 for [3 inch, …48 inch] inch pipe size, Rated Water Working Pressure per Table 6 [150, 200, 250, 300, 350], suitable for trench Type [1, 2, 3, 4, 5].

Outside Coating and/or Inside Lining: See Part 3, Corrosion Control

[Manufacturer and model numbers]

AWWA C110 Fittings:

350 psig pressure rating for [3 inch, … 24 inch], ductile-iron push-on-joint fittings or flange-joint fittings

250 psig pressure rating for [24 inch, … 48 inch] [ductile-iron, grey-iron]

150 psig pressure rating for [24 inch, … 48 inch] grey-iron

AWWA C153 Ductile-Iron Compact Fittings, Class 350.

Synthetic rubber gaskets meeting AWWA C111 [ring and/or full-face] conforming to AWWA C110 Table A.1.

Outside Coating and/or Inside Lining:  See part 3, Corrosion Control

[Manufacturer and model numbers]

Flanged Joint

Flange joint [bolts smaller than ¾ inch may have either standard square or heavy hex heads used with heavy hex nuts.  Bolts ¾ in and larger have either square or hex heads and either hex or heavy hex nuts.  Bolts and nuts threaded in accordance with ASME B1.1 Unified Inch Screw Threads (UN and UNR Thread Form) class 2A external and class 2B internal.  Bolts and nuts low-carbon steel and conform to the chemical and mechanical requirements of ASTM A307, 60 ksi tensile strength, grade B.  The carbon-steel bolts should be used where gray-iron flanges are installed with flat ring gaskets that extend only to the bolts.  Higher-strength bolts may properly be used where gray-iron flanges are installed with full-face gaskets.  Higher-strength bolts may be used where ductile flanges are installed with either ring or full-faced gaskets.]

Bolts and Studs: ASME B18.2.1 ,[type of bolt], [nominal size], [thread class], [product length], [material], [finish (if required)]

Nuts: ASME B18.2.2, [type: heavy hex, heavy hex jam, hex thick slotted, etc…],[size], [thread class], [material], [finish (if required)]

Washers: ASME B18.21.1 [type: plain, helical, tooth-lock], [material], [hardness], [nominal size], [finish (if required)]

[Manufacturer and model numbers]

Mechanical Joints

Mechanical joint bell, socket, plain ends, and accessories: AWWA C111 using [ductile-iron, grey-iron]

[Manufacturers and model numbers]

Welded Joints:

As shown in Drawings.

PVC Pipe: ASTM D1785, schedule [40][80].

Fittings: PVC, schedule [40 ASTM D2466] [80 ASTM D2467].

Pipe [Manufacturers and model numbers]

Fittings [Manufacturers and model numbers]

Primer [Manufacturers and model numbers]

Solvent [Manufacturers and model numbers]

CHILLED WATER PIPING, ABOVE GRADE

Copper tubing alloy [102, 122] per ASME B31.9 Table I-1. Temper shall be [drawn H and/or annealed O].

Braze Joints

Fittings: ASME B16.22, wrought copper and copper alloy, solder joint pressure fittings [and/or] ASME B16.18 cast copper alloy solder joint pressure fittings

[Manufacturers and Model Numbers

Use AWS A5.8 TB-BCuP-5 silver braze.

Comply with [01 4444, 01 44555].

Solder joint

Application is restricted to [compressed air, non-flammable gas, non-toxic gas, non-toxic liquids] less than 4.125 inch OD.

Fittings: ASME B16.22, wrought copper and copper alloy, solder joint pressure fittings [and/or] ASME B16.18 cast copper alloy solder joint pressure fittings

[Manufacturers and Model Numbers]

Solder in accordance with ASTM B32 [year or state latest], Alloy Grade [Sb5, Sn50, other] or UNS [L13950, L55031, other].

Flux [manufacturer, material]

Pipe Up to 2”: black steel ASTM A53, type [E, F, S] grade [A or B], wall thickness [schedule 80]. Threaded joints per ASME B1.20.1 for pipe sizes 2 inches and under.

Threaded Joints:

Fittings: Black steel, ASTM A234, butt welding type, ASME B16.9, [and/or], ASTM A197, ASME B16.3 malleable threaded type ASME B1.20.1.

[Manufacturers and model numbers]

Greater than 2 inches black steel ASTM A53, type [E, F, S] grade [A or B], wall thickness [standard wall] [welded or bolted or mechanical joints].

Bolted Joints:

Flanges and Flanged Fittings: Black steel, ASTM A105, ASME B16.5 class [150, 300,…2500].

Fittings: ASME B16.42 Ductile Iron Pipe Flanges and Flanged Fittings, class [150, 300].

Fittings: Black steel, ASTM A234, Grade WPB, butt-welded type, ASME B16.9, [standard wall].

Fittings: ASME B16.28,  Wrought Steel Butt-welding Short Radius Elbows and Returns

Gaskets: ASME B 16.5 Nonmandatory Appendix B, Limiting Dimensions of Gaskets Other Than Ring Joint Gaskets, Group Ia.  Gaskets used in ASME B16.5 flanges must satisfy the requirements of ASME B16.20a for metallic gaskets and ASME B16.21 for non-metallic flat gaskets.

Bolts and Studs: ASME B18.2.1, …],[type of bolt], [nominal size], [thread class], [product length], [material], [finish (if required)]

Nuts: ASME B18.2.2, [type: heavy hex, heavy hex jam, hex thick slotted, etc…],[size], [thread class], [material], [finish (if required)]

Washers: ASME B18.21.1 [type: plain, helical, tooth-lock], [material], [hardness], [nominal size], [finish (if required)]

[Manufacturers and model numbers]

Mechanical Joints:

Pipe ends per AWWA-C606, Grooved and Shouldered Type Joints, (aka Victaulic 177N) with formed fittings and couplings (Warning:  DO NOT use the reduced wall thickness fittings without express engineering direction).

Fittings AWWA C606, (aka Victaulic 177N), ductile or malleable iron, service rating 86– 250 deg F meeting ASTM A 536, grade [60-42-10, 70-50-05].  Grooved and Shouldered Type Joints, (aka Victaulic 177N) with formed fittings and couplings (Warning:  DO NOT use the reduced wall thickness fittings without express engineering direction).

[Manufacturers and model numbers]

Factory reference: Installation Instructions I-177N QuickVic 7814 Rev B, Updated 01.2015 Z000177N00

Welded Joints:

As shown in Drawings.

TOWER WATER PIPING BURIED

Copper Tubing: Alloy [102, 122], temper [drawn H and/or annealed O]. Thickness per UL 207, ASTM B88, B75, B68, or B280.

Braze Joints

Fittings: ASME B16.22, wrought copper and copper alloy, solder joint pressure fittings [and/or] ASME B16.18 cast copper alloy solder joint pressure fittings

[Manufacturers and model numbers

AWS A5.8 TB-BCuP-5 silver braze.

Comply with [01 4444, 01 44555].

Solder joint

application is restricted to [compressed air, non-flammable gas, non-toxic gas, non-toxic liquids] less than 4.125 inch OD.

Fittings: ASME B16.22, wrought copper and copper alloy, solder joint pressure fittings [and/or] ASME B16.18 cast copper alloy solder joint pressure fittings

[Manufacturers and model numbers]

Solder in accordance with ASTM B32, Alloy Grade [Sb5, Sn50, other] or UNS [L13950, L55031, other].

Flux [manufacturer, material]

Ductile Iron Pipe:

AWWA C151 for [3 inch, …48 inch] inch pipe size, Rated Water Working Pressure per Table 6 [150, 200, 250, 300, 350], suitable with trench type [1, 2, 3, 4, 5]

Outside Coating and/or Inside Lining: See Part 3, Corrosion Control

[Manufacturer and model numbers]

AWWA C110 Fittings:

350 psig pressure rating for [3 inch, … 24 inch], ductile-iron push-on-joint fittings or flange-joint fittings

250 psig pressure rating for [24 inch, … 48 inch] [ductile-iron, grey-iron]

150 psig pressure rating for [24 inch, … 48 inch] grey-iron

AWWA C153, Ductile-Iron Compact Fittings, Class 350.

Synthetic rubber gaskets meeting AWWA C111 [ring and/or full-face] conforming to AWWA C110 Table A.1.

Outside Coating and/or Inside Lining: See Part 3, Corrosion Control

[Manufacturers and model numbers]

Flanged Joint

Flange joint [bolts smaller than ¾ inch may have either standard square or heavy hex heads used with heavy hex nuts.  Bolts ¾ in and larger have either square or hex heads and either hex or heavy hex nuts.  Bolts and nuts are threaded in accordance with ASME B1.1 Unified Inch Screw Threads (UN and UNR Thread Form) class 2A external and class 2B internal.  Bolts and nuts are low-carbon steel and conform to the chemical and mechanical requirements of ASTM A307, 60 ksi tensile strength, grade B.  The carbon-steel bolts should be used where gray-iron flanges are installed with flat ring gaskets that extend only to the bolts.  Higher-strength bolts may properly be used where gray-iron flanges are installed with full-face gaskets.  Higher-strength bolts may be used where ductile flanges are installed with either ring or full-faced gaskets.]

Bolts and Studs: ASME B18.2.1 ,[type of bolt], [nominal size], [thread class], [product length], [material], [finish (if required)]

Nuts: ASME B18.2.2, [type: heavy hex, heavy hex jam, hex thick slotted, etc…],[size], [thread class], [material], [finish (if required)]

Washers: ASME B18.21.1 [type: plain, helical, tooth-lock], [material], [hardness], [nominal size], [finish (if required)]

[Manufacturers and model numbers]

[Torque bolts for flanges of size 6 inch to 69 ft-lb; 4 inch to 49 ft-lb; and 3 inch to 73 ft-lb respectively – per Garlock requirements for full-face homogenous rubber gaskets of B16.5 and 16.47 Series A less than 70 durometer, 150# flat face flanges and ASTM A193 B7 and B7M bolts.]

Mechanical Joints

Mechanical joint bell, socket, plain ends, and accessories: AWWA C111 using [ductile-iron, grey-iron]

[Manufacturers and model numbers]

Welded Joints:

As shown in Drawings.

PVC Pipe: ASTM D1785, schedule [40][80].

Fittings: PVC, schedule [40 ASTM D2466 or 80 ASTM D2467].

Joints: Assembly per ASTM D285 solvent weld with ASTM D2564 solvent cement for PVC D2564 or CPVC D2846.

Solvent welding or thermal bonding shall comply with Section 01 4444, Offsite Welding and Joining Requirements and Section 01 4455, Onsite Welding and Joining Requirements.

Pipe [Manufacturers and model numbers]

Fittings [Manufacturers and model numbers]

Primer [Manufacturers and model numbers]

Solvent [Manufacturers and model numbers]

Pipe up to 18 in: Black steel, ASTM A53, type [e, f, s], grade [a, b], wall thickness [standard wall].  Bolted or mechanical joints for pipe sizes greater than 2 and up to 18 inches.  Threaded joints per ASME B1.20.1 for pipe sizes 2 inches and under.

Threaded Joints

Fittings: Black steel, ASTM A234, butt welding type, ASME B16.9, [and/or], ASTM A197, ASME B16.3 malleable threaded type ASME B1.20.1.

[Manufacturers and model numbers]

Bolted Joints

Flanges and Flanged Fittings: Black steel, ASTM A105, ASME B16.5 class [150, 300,…2500].

Fittings: ASME B16.42 Ductile Iron Pipe Flanges and Flanged Fittings, class [150, 300].

Fittings: Black steel, ASTM A234, Grade WPB, butt-welded type, ASME B16.9, [standard wall].

Fittings: ASME B16.28,  Wrought Steel Butt-welding Short Radius Elbows and Returns

Gaskets: ASME B16.5 Nonmandatory Appendix B, Limiting Dimensions of Gaskets Other Than Ring Joint Gaskets, Group Ia.  Gaskets used in ASME B16.5 flanges must satisfy the requirements of ASME B16.20a for metallic gaskets and ASME B16.21 for non-metallic flat gaskets.

Bolts and Studs: ASME B18.2.1, …],[type of bolt], [nominal size], [thread class], [product length], [material], [finish (if required)]

Nuts: ASME B18.2.2, [type: heavy hex, heavy hex jam, hex thick slotted, etc…],[size], [thread class], [material], [finish (if required)]

Washers: ASME B18.21.1 [type: plain, helical, tooth-lock], [material], [hardness], [nominal size], [finish (if required)]

[Manufacturers and model numbers]

Mechanical Joints

Pipe ends per AWWA-C606, Grooved and Shouldered Type Joints, (aka Victaulic 177N) with formed fittings and couplings (Warning:  DO NOT use the reduced wall thickness fittings without express engineering direction).

Fittings AWWA C606 (aka Victaulic 177N), ductile or malleable iron, service rating 86–250 deg F meeting ASTM A 536, grade [60-42-10, 70-50-05].  Grooved and Shouldered Type Joints, (aka Victaulic 177N) with formed fittings and couplings (Warning:  DO NOT use the reduced wall thickness fittings without express engineering direction).

[Manufacturers and model numbers]

Welded Joints

As shown in Drawings.

Outside Coating: See Part 3, Corrosion Control

[Manufacturers and Model Numbers]

Inside Lining: See Part 3, Corrosion Control

[Manufacturers and Model Numbers]

Pipe 18” through 24”: Black steel, wall thickness [standard or schedule 40], API 5L-[year or state latest], Grade [A and/or B and/or X42], condition [as-rolled, normalizing rolled, normalized or normalizing formed].

Bolted Joints:

Flanges and Flanged Fittings: Black steel, ASTM A105, ASME B16.5 class [150, 300, …2500].

Fittings: ASME B16.42 Ductile Iron Pipe Flanges and Flanged Fittings, class [150, 300].

Fittings: Black steel, ASTM A234, Grade WPB, butt-welded type, ASME B16.9, [standard wall].

Fittings: ASME B16.28,  Wrought Steel Butt-welding Short Radius Elbows and Returns

Gaskets: ASME B 16.5 Nonmandatory Appendix B, Limiting Dimensions of Gaskets Other Than Ring Joint Gaskets, Group Ia.  Gaskets used in ASME B16.5 flanges must satisfy the requirements of ASME B16.20a for metallic gaskets and ASME B16.21 for non-metallic flat gaskets.

Bolts and Studs: ASME B18.2.1, …],[type of bolt], [nominal size], [thread class], [product length], [material], [finish (if required)]

Nuts: ASME B18.2.2, [type: heavy hex, heavy hex jam, hex thick slotted, etc…],[size], [thread class], [material], [finish (if required)]

Washers: ASME B18.21.1 [type: plain, helical, tooth-lock], [material], [hardness], [nominal size], [finish (if required)]

[Manufacturers and model numbers]

Welded Joints:

As shown in Drawings.

Outside Coating and/or Inside Lining:

[Manufacturers and model numbers]

TOWER WATER PIPING, ABOVE GRADE

Copper Tubing: Alloy [102, 122], temper [drawn H and/or annealed O].  Thickness per UL 207, ASTM B88, B75, B68, or B280.

Braze Joints

Fittings: ASME B16.22, wrought copper and copper alloy, solder joint pressure fittings [and/or] ASME B16.18 cast copper alloy solder joint pressure fittings

[Manufacturers and model numbers

Use AWS A5.8 TB-BCuP-5 silver braze.

Solder joint

application is restricted to [compressed air, non-flammable gas, non-toxic gas, non-toxic liquids] less than 4.125 inch OD.

Fittings: ASME B16.22, wrought copper and copper alloy, solder joint pressure fittings [and/or] ASME B16.18 cast copper alloy solder joint pressure fittings

- [Manufacturers and model numbers]

Solder in accordance with ASTM B32, Alloy Grade [Sb5, Sn50, other] or UNS [L13950, L55031, other].

- [Manufacturer, model number]

Flux [manufacturer, model number]

Pipe up to 18”: Black steel, ASTM A53, type [E, F, S], grade [A, B], wall thickness [standard wall].  Bolted or mechanical joints for pipe sizes greater than 2 inches.  Threaded joints per ASME B1.20.1 for pipe sizes 2 inches and under.

Threaded Joints:

Fittings: Black steel, ASTM A234, butt welding type, ASME B16.9, [and/or], ASTM A197, ASME B16.3 malleable threaded type ASME B1.20.1.

[Manufacturers and model numbers]

Bolted Joints:

Flanges and Flanged Fittings: Black steel, ASTM A105, ASME B16.5 class [150, 300,…2500].

Fittings: ASME B16.42 Ductile Iron Pipe Flanges and Flanged Fittings, class [150, 300].

Fittings: Black steel, ASTM A234, Grade WPB, butt-welded type, ASME B16.9, [standard wall].

Fittings: ASME B16.28,  Wrought Steel Butt-welding Short Radius Elbows and Returns

Gaskets: ASME B 16.5 Nonmandatory Appendix B, Limiting Dimensions of Gaskets Other Than Ring Joint Gaskets, Group Ia.  Gaskets used in ASME B16.5 flanges must satisfy the requirements of ASME B16.20a for metallic gaskets and ASME B16.21 for non-metallic flat gaskets.

Bolts and Studs: ASME B18.2.1, …],[type of bolt], [nominal size], [thread class], [product length], [material], [finish (if required)]

Nuts: ASME B18.2.2, [type: heavy hex, heavy hex jam, hex thick slotted, etc…],[size], [thread class], [material], [finish (if required)]

Washers: ASME B18.21.1 [type: plain, helical, tooth-lock], [material], [hardness], [nominal size], [finish (if required)]

[Manufacturers and model numbers]

Mechanical Joints:

Pipe ends per AWWA-C606, Grooved and Shouldered Type Joints, (aka Victaulic 177N) with formed fittings and couplings (Warning:  DO NOT use the reduced wall thickness fittings without express engineering direction).

Fittings AWWA C606, (aka Victaulic 177N), ductile or malleable iron, service rating 86–250 deg F meeting ASTM A 536, grade [60-42-10, 70-50-05].  Grooved and Shouldered Type Joints, (aka Victaulic 177N) with formed fittings and couplings (Warning:  DO NOT use the reduced wall thickness fittings without express engineering direction).

[Manufacturers and model numbers]

Welded Joints:

As shown in Drawings.

Pipe 18” through 24”: Black steel, wall thickness [standard or schedule 40], API 5L-[year or state latest], Grade [A and/or B and/or X42], condition [as-rolled, normalizing rolled, normalized or normalizing formed].

Bolted Joints:

Flanges and Flanged Fittings: Black steel, ASTM A105, ASME B16.5 class [150, 300,…2500].

Fittings: ASME B16.42 Ductile Iron Pipe Flanges and Flanged Fittings, class [150, 300].

Fittings: Black steel, ASTM A234, Grade WPB, butt-welded type, ASME B16.9, [standard wall].

Fittings: ASME B16.28,  Wrought Steel Buttwelding Short Radius Elbows and Returns

Gaskets: ASME B 16.5 Nonmandatory Appendix B, Limiting Dimensions of Gaskets Other Than Ring Joint Gaskets, Group Ia.  Gaskets used in ASME B16.5 flanges must satisfy the requirements of ASME B16.20a for metallic gaskets and ASME B16.21 for non-metallic flat gaskets.

Bolts and Studs: ASME B18.2.1, …],[type of bolt], [nominal size], [thread class], [product length], [material], [finish (if required)]

Nuts: ASME B18.2.2, [type: heavy hex, heavy hex jam, hex thick slotted, etc…],[size], [thread class], [material], [finish (if required)]

Washers: ASME B18.21.1 [type: plain, helical, tooth-lock], [material], [hardness], [nominal size], [finish (if required)]

[Manufacturers and model numbers]

Welded Joints:

As shown in Drawings.

BLOW DOWN PIPING, ABOVE GRADE

Copper tubing alloy [102, 122] per ASME B31.9 Table I-1. Temper shall be [drawn H and/or annealed O].

Braze Joints

Fittings: ASME B16.22, wrought copper and copper alloy, solder joint pressure fittings [and/or] ASME B16.18 cast copper alloy solder joint pressure fittings

[Manufacturers and Model Numbers

Use AWS A5.8 TB-BCuP-5 silver braze.

Comply with [01 4444, 01 44555].

Solder joint

Application is restricted to [compressed air, non-flammable gas, non-toxic gas, non-toxic liquids] less than 4.125 inch OD.

Fittings: ASME B16.22, wrought copper and copper alloy, solder joint pressure fittings [and/or] ASME B16.18 cast copper alloy solder joint pressure fittings

[Manufacturers and Model Numbers]

Solder in accordance with ASTM B32 [year or state latest], Alloy Grade [Sb5, Sn50, other] or UNS [L13950, L55031, other].

Flux [manufacturer, material]

Pipe: Black steel, ASTM A53, type [E, F, S], grade [A, B], wall thickness [schedule 80].  Bolted or mechanical joints for pipe sizes greater than 2 and up to 18 inches.  Threaded joints per ASME B1.20.1 for pipe sizes 2 inches and under.

Threaded Joints:

Fittings: Black steel, ASTM A234, butt welding type, ASME B16.9, [and/or], ASTM A197, ASME B16.3 malleable threaded type ASME B1.20.1.

[Manufacturers and model numbers]

Greater than 2 inches black steel ASTM A53 type [E, F, S] grade [A or B], wall thickness [standard wall] [welded or bolted or mechanical joints].

Bolted Joints:

Flanges and Flanged Fittings: Black steel, ASTM A105, ASME B16.5 class [150, 300,…2500].

Fittings: ASME B16.42 Ductile Iron Pipe Flanges and Flanged Fittings, class [150, 300].

Fittings: Black steel, ASTM A234, Grade WPB, butt-welded type, ASME B16.9, [standard wall].

Fittings: ASME B16.28,  Wrought Steel Butt-welding Short Radius Elbows and Returns

Gaskets: ASME B 16.5 Nonmandatory Appendix B, Limiting Dimensions of Gaskets Other Than Ring Joint Gaskets, Group Ia.  Gaskets used in ASME B16.5 flanges must satisfy the requirements of ASME B16.20a for metallic gaskets and ASME B16.21 for non-metallic flat gaskets.

Bolts and Studs: ASME B18.2.1, …],[type of bolt], [nominal size], [thread class], [product length], [material], [finish (if required)]

Nuts: ASME B18.2.2, [type: heavy hex, heavy hex jam, hex thick slotted, etc…],[size], [thread class], [material], [finish (if required)]

Washers: ASME B18.21.1 [type: plain, helical, tooth-lock], [material], [hardness], [nominal size], [finish (if required)]

[Manufacturers and model numbers]

[Torque bolts for flanges of size 6 inch to 69 ft-lb; 4 inch to 49 ft-lb; and 3 inch to 73 ft-lb respectively – per Garlock requirements for full face homogenous rubber gaskets of B16.5 and 16.47 series A less than 70 durometer, #150 flat face flanges and ASTM A193 B7 and B7M bolts.]

Mechanical Joints:

Pipe ends per AWWA-C606, Grooved and Shouldered Type Joints, (aka Victaulic 177N) with formed fittings and couplings (Warning:  DO NOT use the reduced wall thickness fittings without express engineering direction).

Fittings AWWA C606, (aka Victaulic 177N), ductile or malleable iron, service rating 86–250 deg F meeting ASTM A 536, grade [60-42-10, 70-50-05].  Grooved and Shouldered Type Joints, (aka Victaulic 177N) with formed fittings and couplings (Warning:  DO NOT use the reduced wall thickness fittings without express engineering direction).

[Manufacturers and model numbers]

Factory reference: Installation Instructions I-177N QuickVic 7814 Rev B, Updated 01.2015 Z000177N00

Welded Joints:

As shown in Drawings.

BLOW DOWN PIPING BURIED

Pipe: Black steel, ASTM A53, type [E, F, S], grade [A, B], wall thickness [schedule 80].  Bolted or mechanical joints for pipe sizes greater than 2 and up to 18 inches.  Threaded joints per ASME B1.20.1 for pipe sizes 2 inches and under.

Threaded Joints:

Fittings: Black steel, ASTM A234, butt welding type, ASME B16.9, [and/or], ASTM A197, ASME B16.3 malleable threaded type ASME B1.20.1.

[Manufacturers and model numbers]

Greater than 2 inches black steel ASTM A53 type [E, F, S] grade [A or B], wall thickness [standard wall] [welded or bolted or mechanical joints].

Bolted Joints:

Flanges and Flanged Fittings: Black steel, ASTM A105, ASME B16.5 class [150, 300,…2500].

Fittings: ASME B16.42 Ductile Iron Pipe Flanges and Flanged Fittings, class [150, 300].

Fittings: Black steel, ASTM A234, Grade WPB, butt-welded type, ASME B16.9, [standard wall].

Fittings: ASME B16.28,  Wrought Steel Butt-welding Short Radius Elbows and Returns

Gaskets: ASME B 16.5 Nonmandatory Appendix B, Limiting Dimensions of Gaskets Other Than Ring Joint Gaskets, Group Ia.  Gaskets used in ASME B16.5 flanges must satisfy the requirements of ASME B16.20a for metallic gaskets and ASME B16.21 for non-metallic flat gaskets.

Bolts and Studs: ASME B18.2.1, …],[type of bolt], [nominal size], [thread class], [product length], [material], [finish (if required)]

Nuts: ASME B18.2.2, [type: heavy hex, heavy hex jam, hex thick slotted, etc…],[size], [thread class], [material], [finish (if required)]

Washers: ASME B18.21.1 [type: plain, helical, tooth-lock], [material], [hardness], [nominal size], [finish (if required)]

[Manufacturers and model numbers]

[Torque bolts for flanges of size 6 inch to 69 ft-lb; 4 inch to 49 ft-lb; and 3 inch to 73 ft-lb respectively – per Garlock requirements for full face homogenous rubber gaskets of B16.5 and 16.47 series A less than 70 durometer, #150 flat face flanges and ASTM A193 B7 and B7M bolts.]

Welded Joints:

As shown in Drawings.

Coating: See Part 3, Corrosion Control.

EQUIPMENT DRAINS AND OVERFLOWS (ALL EQUIPMENT)

Pipe: Galvanized steel, ASTM A53, type [E, F, S], grade [A, B], wall thickness [schedule 80].  Bolted or mechanical joints for pipe sizes greater than 2 to 18 inches.  Threaded joints per ASME B1.20.1 for pipe sizes 2 inches and under.

Threaded joints

Fittings:  [Galvanized grey iron per ASME B16.12 and/or malleable iron ASTM A197, per ASME B16.3] Malleable iron threaded pipe unions per, B16.39].

[Manufacturers and model numbers]

Greater than 2 inches black steel ASTM A53, type [E, F, S] grade [A or B], wall thickness [standard wall] [welded or bolted or mechanical joints]

Bolted Joints:

Flanges and Flanged Fittings: Black steel, ASTM A105, ASME B16.5 class [150, 300, 2500].

Fittings: ASME B16.42 Ductile Iron Pipe Flanges and Flanged Fittings, class [150, 300].

Fittings: Black steel, ASTM A234, Grade WPB, butt-welded type, ASME B16.9, [standard wall].

Fittings: ASME B16.28,  Wrought Steel Butt-welding Short Radius Elbows and Returns

Gaskets: ASME B 16.5 Nonmandatory Appendix B, Limiting Dimensions of Gaskets Other Than Ring Joint Gaskets, Group Ia.  Gaskets used in ASME B16.5 flanges must satisfy the requirements of ASME B16.20a for metallic gaskets and ASME B16.21 for non-metallic flat gaskets.

Bolts and Studs: ASME B18.2.1, [type of bolt], [nominal size], [thread class], [product length], [material], [finish (if required)]

Nuts: ASME B18.2.2, [type: heavy hex, heavy hex jam, hex thick slotted, etc.…],[size], [thread class], [material], [finish (if required)]

Washers: ASME B18.21.1 [type: plain, helical, tooth-lock], [material], [hardness], [nominal size], [finish (if required)]

[Manufacturers and model numbers]

[Torque bolts for flanges of size 6 inch to 69 ft-lb; 4 inch to 49 ft-lb; and 3 inch to 73 ft-lb respectively – per Garlock requirements for full face homogenous rubber gaskets of B16.5 and 16.47 series A less than 70 durometer, #150 flat face flanges and ASTM A193 B7 and B7M bolts.]

Mechanical Joints:

Pipe ends per AWWA-C606, Grooved and Shouldered Type Joints, (aka Victaulic 177N) with formed fittings and couplings (Warning:  DO NOT use the reduced wall thickness fittings without express engineering direction).

Fittings AWWA C606, (aka Victaulic 177N), ductile or malleable iron, service rating 86–250 deg F meeting ASTM A 536, grade [60-42-10, 70-50-05].  Grooved and Shouldered Type Joints, (aka Victaulic 177N) with formed fittings and couplings (Warning:  DO NOT use the reduced wall thickness fittings without express engineering direction).

[Manufacturers and model numbers]

Factory reference: Installation Instructions I-177N QuickVic 7814 Rev B, Updated 01.2015 Z000177N00

Welded Joints:

As shown in Drawings.

UNIONS, FLANGES, AND COUPLINGS (TOWER AND CHILLED WATER)

Mechanical Couplings.

Mechanical and Proprietary Joints, ductile or malleable, service rating 35–230 deg F at 300 psig, flexible type meeting AWWA-606.

[Manufacturers and model numbers]

Factory reference: Installation Instructions I-177N QuickVic 7814 Rev B, Updated 01.2015 Z000177N00

Dielectric Connections.

Union with galvanized or plated steel threaded-end, copper solder-end, and water-impervious isolation barrier.

Dielectric ASME B3.1 threaded fittings per ASME B16.9, 250 psi rating

Dielectric flanged fittings, conforming to [ASME B16.42 (iron), ASME B16.24 (bronze)], with mandatory polysulfone bolt insulators.

Materials of construction [grey iron ASTM A48, malleable iron ASTM A197, steel ASTM A108, brass ASTM B16, bronze ASTM B584]

Gasket [Buna-N (180F at 250 psi), EPDM (300 F, 50psi)]

Watts series 3000 dielectric

Ferrous metal, plastic-lined: ASTM F1545, carbon steel per ASTM A575.

Manufacturer:  Victaulic, Style 47

VALVES

Gates Valves up to 2 inches.

Manufacturer: Nibco, Series 111.

MSS SP-80 Class [125, 150 for threaded, or solder] ends, valve type [1A, 1B, 2, 3, or 4] bronze body, bronze trim.

Gate Valves over 2 to 12 inches.

Manufacturer: Nibco, Series F-617-0

MSS SP-70, Class [125, 250], valve type [I, II, III, IV], construction [NF: non-rising stem, OF: outside screw and yolk], iron body, bronze trim flanged ends.

Globe Valves up to 2 inches.

Manufacturer: Nibco, Series 211.

MSS SP-80, Class [125, 150 for threaded, or solder] ends, valve type [1, 2, or 3] bronze body, bronze trim, rising stem, hand wheel, inside screw.

Globe Valves over 2 to 10 inches

Manufacturer: Nibco F-718-B.

MSS SP-85, Class 150 flanged ends, iron body, bronze trim, hand wheel, type [1, 2, or 3] removable bronze disc.

Ball Valves up to 2 inches.

Manufacturer: Nibco, Series 585-70.

MSS SP 110, 150 psi non-shock cold working pressure (CWP) minimum pressure rating

Bronze, two-piece body, chrome-plated brass ball, full port, Teflon seats and stuffing box ring, blowout proof stem, lever handle, solder or threaded ends.

Ball Valves over 2 to 12 inches.

Manufacturer: Nibco, Series F-510-CS-R-66-FS

MSS SP-72, one piece body, full port ball, flange class 150, 150 psig non-shock cold working pressure (CWP) minimum,

Butterfly Valves 2 inches to 12 inches

Manufacturer:  Nibco, Series GD-4775

Standard: Design to comply with MSS SP-67, Type I (tight shut-off), AWWA C606 end connections, non-shock cold working pressure (CWP) minimum pressure rating

Butterfly Flanged Valves 2 inches to 12 inches

Manufacturer:  Nibco, Series FD-57[6=EPDM, 7=BUNA]

Standard: Design to comply with MSS SP-67, Type I (tight shut-off), flanged end connections class 150, minimum, non-shock cold working pressure (CWP) minimum pressure rating.

Butterfly Wafer Valves over 2 inches to 12 inches

Manufacturer: Nibco, Series WD 2000/ LD 2000

Design to comply with MSS SP-67, Type I (tight shut-off). Bolting compatible with class 150 flange, 150 psig non-shock cold working pressure (CWP) minimum pressure rating.

Lift Check Valves sizes up to 2 inches.

Manufacturer: Nibco 473 Series.

MSS SP-80, Type [1, 2] bronze, horizontal swing, Y-pattern, renewable seat and disc, non-shock cold working pressure (CWP) minimum pressure rating. Solder or threaded ends.

Lift Check Valves sizes over 2 inches to 12 inches.

Manufacturer: Nibco F-918-B.

MSS SP-71, grey iron, type I [II, III, IV] class 125, flanged end connections, 150 psig minimum pressure rating.

Spring Check Valves up to 2 inches.

Manufacturer: Nibco 480 Series.

MSS SP-80, Type [1, 2] bronze, horizontal swing, Y-pattern, renewable seat and disc, non-shock cold working pressure (CWP) minimum pressure rating. Solder or threaded ends.

Spring Check Valves over 2 inches to 36 inches.

Manufacturer: Nibco F-910-B.

MSS-SP-125, Class 125, cast iron body, fluid to 200 degrees F, renewable seats and disc, spring actuated, flanged.

Balancing Valves

Manufacturer. Griswold Controls class 150 wafer

Size 3 inch to 14 inches ASTM A536 GR60-40-18, 16 inches to 24 inches Gray Iron ASTM A126-61T, Class 20, cartridge ANSI type 304 stainless steel, AISI Type 17-7 PH stainless steel spring. Compatible with ASME B16.5 class 150 steel flanges.

Size less than 3 inches:

Manufacturer:  Bell and Gossett

Model Number:  Circuit Setters cb [ ½, ¾, 1, 1 ½, 2, 2 ½][S]

*************************************************************************************************************Pressure and Vacuum Gauges: Overpressure relief protection must be provided on Bourdon-tube, dial-indicating pressure gauges that operate at pressures greater than 15 psig by one of the following means:

Pressure gauges approved by Underwriters Laboratories (UL) in accordance with UL-404, “Standard for Gauges, Indicating Pressure, for Compressed Gas Service” Standard for Safety.

Tempered safety glass or plastic face or shield and a blowout back or plug for pressure relief.

Pressure gauges that serve primarily a pressure indication for overpressure protection (i.e., not used for process data collection) must have a range of at least 1.25 times, but no more than twice the set pressure of the relief device as recommended in ASME Section VIII, Div. 1, Appendix M, Para. M-14.

Refer to manufacturer’s recommendation for gauge pressure range.  Generally, a pressure range of twice the expected normal pressure is recommended with maximum working pressure not exceeding 75 percent of the range.  If pulsation occurs, working pressure should not exceed 65 percent of the pressure range.  Pressure gauges in the suction side of the pump will be vacuum pressure gauges.
*************************************************************************************************************

PRESSURE GAUGES

Manufacturer: Ashcroft, Type 1279 or 1009 (stainless steel)

ASME B40.100, Accuracy Grade 1A, maximum plus or minus 1 percent full scale accuracy, minimum 4 1/2 inches dial, glycerin filled, phosphor bronze bourdon tube, 1/4 inch NPT brass bottom connection, phenolic case. Tempered safety glass or plastic face or shield meeting the requirements of ANSI Z97.1, and a blowout back or plug for pressure relief.

[Range:  [0-160] psi.]

[Maximum temperature: [200 degrees F]]

[Range and temperature are specified on Drawings]

[Manufacturer and model numbers]

THERMOMETER

Manufacturer: Reotemp, Model MM

ASME B40.200, Grade A, maximum plus or minus 1 percent full scale accuracy,  bimetal thermometer, mercury free, minimum 4 inches dial, stainless steel case, all angle direct mount, with standard connection.

Range:  [ ] degrees F.

Model:  [    ]

THERMOWELL

Thermowell design meeting ASME PTC 19.3 TW

Manufacturer:  Daily Thermetrics, ½, ¾, or 1 inch NPT

Materia: [316 stainless steel rated at 7000 psig at 70 F, brass rated at 5000 psig at 70 F]

Dielectric Union

Dielectric Connections.

Union with galvanized or plated-steel threaded-end, copper solder-end, and water-impervious isolation barrier.

Dielectric ASME B3.1 threaded fittings per ASME B16.9, 250 psi rating

Dielectric flanged fittings, conforming to [ASME B16.42 (iron), ASME B16.24 (bronze)], with mandatory polysulfone bolt insulators.

Materials of construction [grey iron ASTM A48, malleable iron ASTM A197, steel ASTM A108, brass ASTM B16, bronze ASTM B584]

Gasket [Buna-N (180F at 250 psi), EPDM (300 F, 50psi)]

Watts series 3000 dielectric

Ferrous metal, plastic-lined: ASTM F1545, carbon steel ASTM A575.

Manufacturer:  Victaulic, Style 47

Pressure Temperature Test Port

Manufacturer:  Pete’s Plug

316 stainless steel, ¼ inch, suitable for use in 150 psig systems.  Provide extra-long (XL) plug when pipe insulation exceeds 1 in. thickness.

AUTOMATIC AIR VENTS

Manufacturer:  Spirax Sarco Automatic Air Vents, Model 13WS

ASTM A126 Class B cast iron body, ASME B16.1 class 150 flanges

Manufacturer: Bell & Gossett Automatic Air Vents, Model No. 87

Brass body with non-ferrous internals

Rated for 150 psi and 250°F

STRAINERS

Basket strainer NPS size [2,… 36 inch]

ASME B16.34, pressure [150…1500 psig], flange end ASME [B16.5 or B16.47].

Materials [WCB, LCB, WC6, WC9, C12, C5, CF8, CF3, CF3M, CF8M].

Manufacturer:  Landee Valves M/N ASME B16.34 Basket Strainer, [WC6, WC9]

Manufacturer: Eaton Model 510, 9 to 24 inches

ASTM A126, class B compliant

Bronze body, Y-type screwed end, 20 mesh stainless steel screen, for water service-WOG (non-shock) 400 psi at 210 degrees F.

Eaton Model 72, 2 to 6 inches.

Body: cast iron ASTM A126 Class B

Screen: Stainless Steel, 1/8” perforations, ASME B16.1 class 150 flanges

RELIEF VALVE

Manufacturer:  [Kunkle Model 912.]

Bronze body, brass trim, ASME Section VIII (UV) rated for liquid service, maximum pressure and temperature rating 300 psig and 406 degree F.

Connection Sizes:  [1/2 inch inlet, 3/4 inch outlet] [as shown on drawings].

Set Pressure:  [       ] psi.

Orifice:  [       ] dia.

Capacity:  [                ] gpm.

VIBRATION ELIMINATION

Manufacturer:  Anaconda, Universal Metal Hose

Industrial Metal Hose, Refrigeration Products, Armored and Specialty Flexible Hose Components Anaconda Vibration Eliminators, Bronze or Stainless Steel Vibration Eliminators, copper conforms to UL SA 2528, ends per ASME B16.18 and B16.22;

Diameter [   ] inch

Length [   ] inch

Part Number [   ]

EXPANSION TANK

An air expansion tank is required on hot water heating and chilled water closed piping systems. An ASME coded tank is required on systems designed to operate at or above 15 psig.

Size:  [   ] gal

Manufacture:  [   ]

Model Number:  [   ]

ASME code stamp for Section VIII of the ASME Boiler and Pressure Vessel Code Section VIII, Division 1. Provide NBIC numbering and registration.

CHEMICAL POT FEEDER WITH FILTER

Manufacturer: [Griswold Water Systems]

Series: [Professional DB-GE]

Model: [DB-12-GE-CS-A.]

ASME code stamp for Section VIII of the ASME Boiler and Pressure Vessel Code Section VIII, Division 1. Provide NBIC numbering and registration.

Accessories:

Capacity [12] gallon

Connections [3/4” FPT] inlet and outlet

Full Bottom Drain

Carbon steel construction

Bolt on holes with anchor bolt holes.

Stainless Steel basket

[Filter bag kit with (4) 25 Micron Filter bags rated for 170°F]

[Funnel kit]

[Victaulic Cap Enclosure rated at 600 psi at 230°F]

PUMP EXPANSION FITTING

Manufacturer: Hyspan

Model: 5501R

Type: Laminated bellows with tie rods.

Flange: ASME B16.5, Class 150

ASME BPV Section 8 Div 1 stamped.  Provide NBIC numbering and registration.

CONTROL VALVES AND CONTROL VALVE ACTUATORS

Manufacturer: Belimo

Models: B2 2-way and B3 3-way

Type: Stainless steel ball valve and stem, PTFE seat, Tefzel disc, EPDM O-rings

Sizes from ½ inch to 2 inch.

Maximum Temperature 250 F

Flange: FNPT connections per ASME B1.20.1

[Actuator:  LF24-MFT-S US 2-10 VDC]

PRESSURE REDUCING VALVE [Note:  There is no listed item, and no approved alternative at this time).

[Manufacturer: Bell and Gossett, Model FB-38TU]

[Brass body, factory setting 12 psig, adjustable range 10-25 psig, removable strainer, low inlet pressure check valve, ½” NPT union and ½” sweat connections]

EXECUTION

  - INSPECTION/EXAMINATION

Inspection and Examination shall conform to Section 936 of ASME 31.9; see Appendix B.

Examination activities to verify the quality of the work must be performed by persons other than those who performed the activity being examined. Such persons must not report directly to the immediate supervisors responsible for work being examined.

The fabrication documentation must have evidence of the examination, the evidence must be maintained in the pressure system documentation package submitted to the pressure safety officer.

Do not install underground piping when bedding is wet or frozen.

Verify that excavations are to required grade.

PREPARATION

Ream pipe and tube ends.  Remove burrs.

Remove scale and dirt on inside and outside before assembly.

Prepare piping connections to equipment with flanges or unions.

[specify any special cleaning requirement]

BURIED PIPING

*************************************************************************************************************

Tracer wire and test station(s): are required when specifying cast iron, ductile iron, and non-metallic piping.

Comply with Civil Standard Drawings ST-G30GEN-3 for tracer wire/test station details and Civil Standard Drawings ST-G30-GEN-4 for trenching detail.

*************************************************************************************************************

Tracer wire and test station(s).

Provide earth cover, bedding, warning tape, tracing wire and test stations. Refer to Section 31 2000, Earth Moving.

INSTALLATION

General

Install process cooling water, chilled water, heating hot water, and condenser water (tower water), equipment drains, and overflow piping in conformance with ASME B31.9.

Route piping in orderly manner and maintain gradient. Route parallel and perpendicular to walls.

For multiple openings in piping mains, the distance between their centers shall be at least the sum of their inside diameters

Branch connections shall utilize fittings (tee, lateral, or cross) in accordance with listed codes.

Provide non-conducting dielectric connections wherever jointing dissimilar metals.  Matching of bronze with steel or copper does not require dielectrics.

Install piping to maintain headroom and neither interfere with use of space nor take more space than necessary.

Group piping whenever practical at common elevations.

Install piping to allow for expansion and contraction without stressing pipe, joints, or connected equipment.

Provide access where valves and other equipment are not exposed.

All valves shall be installed in accordance with the manufacturer's instructions and with sufficient clearance and access for ease of operation and maintenance. Install valves with stems upright or horizontal, not inverted.

Sleeve and caulk pipes penetrating exterior walls or interior bearing walls.  Provide waterproof installation for exterior walls.  Provide UL/FM approved through-penetration firestop system when penetrating fire rated barriers (e.g., walls, floors, etc.).

Slope water piping and provide drain valves at low points

Pipe relief devices to nearest floor drain.  Install a union in the piping to allow the valve to be removed for service.

Flush and chemically treat HVAC water piping systems in accordance with Section 23 2500, HVAC Water Treatment.

Pressure test piping system in accordance with Section 22 0813, Testing Piping Systems.

Label piping system in accordance with Section 22 0554, Identification for Plumbing, HVAC and Fire Piping and Equipment.

Insulate piping system in accordance with Section 22 0713, Piping and HVAC Insulation.

Support piping system in accordance with Section 22 0529, Hangers and Supports for Plumbing Piping and Equipment.  Do not anchor the pipe.  Allow piping to slide and expand or contract with temperature.

Provide automatic air vents in hydronic closed piping systems at high point.  Provide isolation ball valve at inlet connection.

Install chrome-plated steel escutcheons for insulated pipes at finished surfaces.

Above grade piping: unless otherwise noted, provide ball valves in piping 2 inches and smaller, butterfly valves in piping 2 1/2 inches and larger, and gate valves with standard male capped hose connection, for equipment and drain valves. Provide globe valves for throttling applications.  Provide strainers with full port drain ball valves.  Valves are in accordance with Article 2.13.

Instrument taps: isolated from the main process by a root valve. Instrumentation gauges and instruments that are calibrated provided with a calibration port, normally the same size as the instrument impulse line.

Assemble bolts, nuts, and studs; torque using calibrated wrenches.

Soldering

Follow ASTM B828, “Standard Practice for Making Capillary Joints by Soldering.”

Brazing

Assemble brazed and soldered joints as follows:

No visible unfilled joint space.

Penetration of filler metal inside the pipe not to exceed 100% of the wall thickness.

No visible evidence of overheating.

Welding

Welding (including solvent welding and thermal bonding) and brazing: per Section 01 4444, Offsite Welding and Joining Requirements and Section 01 4455, Onsite Welding and Joining Requirements.

PVC Joints: Assembly per ASTM D2855 solvent weld with ASTM D2564 solvent cement for PVC D2564 or CPVC D2846.

Threaded

Assemble ASME B1.20.1 threaded pipe joints as follows

No more than six and no less than two threads visible after makeup of the joint.

No severe chipping or tearing of visible threads.

Bolted

[Torque bolts for flanges of size 6 inch to 69 ft-lb; 4 inch to 49 ft-lb; and 3 inch to 73 ft-lb respectively – per Garlock requirements for full face homogenous rubber gaskets of B16.5 and 16.47 series a less than 70 durometer, #150 flat face flanges and ASTM A193 B7 and B7M bolts.]

[Flange torque process and values are shown in the Drawings.] [Example: Torque bolts for flanges of size 6 inch to 69 ft-lb; 4 inch to 49 ft-lb; and 3 inch to 73 ft-lb respectively – per Garlock requirements for full face homogenous rubber gaskets of B16.5 and 16.47 series a less than 70 durometer, #150 flat face flanges and ASTM A193 B7 and B7M bolts.]

Before assembly, the flange faces shall be parallel within 1 deg, and the force required to align pipe axes not to exceed 10 ft-lb/in. (14 n·m/25 mm) of nominal pipe diameter.

Bolts and nuts fully engaged.

Mechanical

Mechanical joints per AWWA 606.

Example Installation Instructions: [Factory reference: Installation Instructions I-177N QuickVic 7814 Rev B, Updated 01.2015 Z000177N00]

[Tighten the nuts evenly by alternating sides until metal-to-metal contact occurs at the bolt pads.  Make sure the housing keys engage the grooves completely during tightening.]

[Visually inspect the bolt pads at each joint to ensure metal-to-metal contact is achieved across the entire bolt pad section.]

Examination, Inspection, and Testing

Pressure test piping system in accordance with Section 22 0813, Testing Piping Systems.

All soldering, brazing, and welding: Inspected, examined, and tested in accordance with ASME B31.9; ASME B&PV Code; and LANL ESM STD-342-100, Chapter 13, “Welding, Joining, and NDE.”

Contact the Owners’ Inspector to determine the initial inspection points (minimum hold points).

Holiday test buried piping with coating per ASTM G62 and Section 22 0813.

CORROSION CONTROL

Contact LANL’s Utilities Engineering Corrosion Specialist at 606-0335 for cathodic protection requirements when using black steel pipe below grade.  NOTE: Factory pre-insulated piping systems (e.g., Perma Pipe, Multi Therm 500, (303) 751- 4100 or Rovanco Corp, (505) 344-7100, may be used as a replacement for corrosion control and/or field insulation.

Pipe Coating (black steel pipe below grade). Field-wrap pipe coating such as Polyken or a factory coating suitable for the operating temperature of the piping system. Field-wrap joints and fittings.

Piping Corrosion Tape for Joints and Fittings: Polyken #934-35 35-mil polyethylene tape or LANL-approved equal. Provide manufacturer-recommended primer (Polyken 1027). Maximum Operating Temperature [XXX]. Pre-clean pipe per tape manufacturer’s requirements. All joints and fittings field-wrapped with a minimum of two layers of 30-mil corrosion tape.

Field-Applied Corrosion Coating: Polyken #1600-30HT or LANL-approved equal. Provide manufacturer-recommended primer (Polyken 955 or 954).  Total thickness 30 mils. Maximum Operating Temperature 180°F.  All joints and fittings field-wrapped with a minimum of two layers of 35-mil corrosion tape.  Pre-clean pipe per tape manufacturer’s requirements. Field Applied Corrosion Coating System shall be a two layer system:

          - Layer One: A liquid adhesive (primer) layer consisting of thermally-activated material formulated for elevated temperature stability.

          - Layer Two: A coating layer consisting of a cross-linked polyethylene backing and a cross-linked elastomeric adhesive capable of maintaining long-term protection at the temperature up to 180°F.

Factory Applied Corrosion Control Coating: Factory applied fused system consisting of: an adhesive primer layer, with minimum 10-mil thermoplastic elastomer layer and minimum 40-mil polyolefin top layer containing UV protection; or alternate of an epoxy primer layer with minimum 50-mil high-density polyethylene top layer or an approved equal. Product marking shall be transferred to and stenciled to the outside of the pipe coating. Minimum transferred information shall include: pipe specifications, grade, size, type, and heat number in accordance with the certified material test report and the product marking. All joints and fittings shall be field wrapped with a minimum of two layers of 35-mil corrosion tape.

Factory Applied Corrosion Control manufacturers:

          - Tyco Adhesives, Synergy Plant Coating System.

          - Tyco Adhesives, VANGUARD Plant Coating System.

          - LANL-approved equal.

Test coated underground steel piping for holidays per Section 22 0813, Testing Piping Systems (ref Article 3.3) per ASTM G62.

[Specify a field wrap pipe coating such as Polyken or a factory coating suitable for the operating temperature of the piping system.]  Field-wrap joints and fittings.

Outside Coating: [cement mortar-lined with seal coated with asphaltic materials outside coating.] [asphaltic outside coating] [fusion bonded epoxy spray coating] [corrosion control thin-film coatings from 0.0254 to 0.254 mm (1 to 10 mils) per Article 3.6]

[Manufacturer and model numbers]

Inside Lining: [cement mortar-lined] [asphaltic lining] [corrosion control thin-film coatings from 0.0254 to 0.254 mm (1 to 10 mils) per Article 3.6]

[Manufacturer and model numbers]

Solid Pour-in-Place Insulation

[DRI-THERM, model number]

[Manufacturer and model numbers]

END OF SECTION

********************************************************************************

Do not delete the following reference information:

********************************************************************************

THE FOLLOWING REFERENCE is FOR LANL USE ONLY

This project specification is based on LANL Master Specification 23 2113, Rev. 5, dated March 2, 2017.