SECTION 23 2300

REFRIGERANT PIPING

************************************************************************************************************

LANL MASTER SPECIFICATION

Word file at http://engstandards.lanl.gov

This template must be edited for each project.  In doing so, specifier must add job-specific requirements.  Brackets are used in the text to indicate designer choices or locations where text must be supplied by the designer.  Once the choice is made or text supplied, remove the brackets.  The specifications must also be edited to delete specification requirements for processes, items, or designs that are not included in the project -- and specifier’s notes such as these.  To seek a variance from requirements in the specifications that are applicable, contact the Engineering Standards Manual Mechanical POC. Please contact POC with suggestions for improvement as well.

When assembling a specification package, include applicable specifications from all Divisions, especially Division 1, General requirements.

Specification developed for ML-4 projects.  For ML-1, 2, and 3 applications, additional requirements and independent reviews should be added if increased confidence in procurement or execution is desired; see ESM Chapter 1 Section Z10 Specifications and Quality sections. ************************************************************************************************************

GENERAL

SECTION INCLUDES

Site and building refrigerant piping, fittings, and refrigeration specialties.

SUBMITTALS

Submit the following in accordance with Project submittal procedures:

Catalog Data:

Data on pipe materials, fittings, and accessories.

Refrigerant Specialties: Manufacturers catalog information including capacity, component sizes, rough-in requirements, pressure drop, etc.

Manufacturer's Installation Instructions: Submit hanging and support methods, joining procedures and isolation.

Operation and Maintenance Manual:  Submit operation and maintenance instructions for refrigerant specialties.

Certification of welders.

QUALITY ASSURANCE

Welders Certifications and Qualified Procedure Standards per Section [01 4444] [and] [01 4455].

Comply with ASME B31.5, Refrigeration Piping; ASHRAE 15, Safety Standard for Refrigeration Piping; and ASHRAE 34, Designation and Safety Classification of Refrigerants.

PRODUCTS

  - PRODUCT OPTIONS AND SUBSTITUTIONS

Alternate products may be accepted; follow Section 01 2500, Substitution Procedures.

REFRIGERANT PIPING

Copper Tubing: ASTM B280, Type ACR hard drawn [or annealed].

Fittings: ASME B16.22 wrought copper.

Joints: Braze, AWS A5.8 BCuP silver/phosphorus/copper alloy with melting range 1190 to 1480°F.

UNIONS, FLANGES, AND COUPLINGS

2 inches and Smaller:

Copper Pipe: Bronze, soldered joints.

2-1/2 inches and Larger:

Copper Piping: Bronze, flanged joints.

Gaskets: 1/16 inch thick preformed neoprene.

Dielectric Connections: Union with galvanized or plated steel threaded end, copper solder end, water impervious isolation barrier.

REFRIGERANT SPECIALTIES

************************************************************************************************************

Specify required refrigeration specialties such as filter-dryers, solenoid valves, expansion valves, moisture and liquid indicators, strainers, pressure regulators, etc., to suit project.

************************************************************************************************************

EXECUTION

  - PREPARATION

Ream pipe and tube ends. Remove burrs.

Remove scale and dirt on inside and outside before assembly.

Keep open ends of pipe free from scale and dirt. Protect open ends with temporary plugs or caps.

BURIED PIPING

Provide earth cover, bedding, and warning tape per Drawings and Section          31 2000, Earth Moving.

INSTALLATION – Above ground piping system

Install refrigerant piping in accordance with ASME B31.5, Refrigeration Piping.

Where more than one piping system material is specified, provide compatible system components and joints.  Use non-conducting dielectric connections when joining dissimilar metals in systems.

Provide flanges, unions, or couplings at locations requiring servicing. Use unions, flanges, or couplings downstream of valves and at equipment connections.  Do not use direct welded or threaded connections to valves or equipment.

Provide flexible connectors at or near equipment where piping configuration does not absorb vibration.

Install flexible connectors at right angles to axial movement of compressor, parallel to crankshaft.

Route piping parallel to building structure and maintain gradient.

Install piping to conserve building space, and not interfere with use of space.

Group piping whenever practical at common elevations.

Sleeve pipe passing through partitions, walls and floors.  Provide UL/FM approved through penetration fire stop system when penetrating a fire rated barrier (i.e., wall, floors, etc.).

Install piping to allow for expansion and contraction without stressing pipe, joints, or connected equipment.

Provide access where valves and fittings are not exposed.

Arrange refrigerant piping to return oil to compressor.  Provide traps and loops in piping, and provide double risers as required. Slope horizontal piping 1/2 inch in 10 feet in direction of flow.

Flood refrigerant piping system with nitrogen when brazing.

Install valves with stems upright or horizontal, not inverted.

Provide external equalizer piping on expansion valves with refrigerant distributor connected to evaporator.

Fully charge completed system with refrigerant after testing.

Comply with ASHRAE 15 procedures for charging and purging of systems and for disposal of refrigerant.

Support piping in accordance with Section 22 0529, Hangers and Supports for Plumbing Piping and Equipment.

Sleeve pipe penetration and caulk in accordance with Section 22 0548, Vibration and Seismic Control for Plumbing Piping and Equipment.

Pressure test piping in accordance with Section 22 0813, Testing Piping Systems.

Insulate piping in accordance with Section 22 0713, Plumbing and HVAC Insulation.

Label piping in accordance with Section 22 0554, Identification for Plumbing, HVAC, and Fire Piping and Equipment.

INSTALLATION - REFRIGERANT SPECIALTIES

***********************************************************************************************************

Edit the following descriptive specifications in accordance with project requirements.

***********************************************************************************************************

Install moisture/liquid indicators in liquid line at the inlet of the thermostatic expansion valve or at the inlet of the evaporator coil capillary tube.

Install refrigerant service valves in suction and discharge lines of compressor.

Install a check valve at the compressor discharge and a liquid accumulator at the compressor suction connection.

Install refrigerant charging valve in liquid line between receiver shut-off valve and expansion valve.

Install solenoid valves upstream from each expansion valve.  Install solenoid valves in horizontal lines with coil at top and provide electrical connection to solenoid valves.

Install thermostatic expansion valves as close as possible to distributors on evaporators and locate expansion valve sensing bulb immediately downstream of evaporator on suction line.

Install pressure relief valves on ASME receivers. Install relief valve discharge piping to terminate outdoors.

Install strainer upstream of each automatic valve and install shut-off valves on each side of strainer.

Install filter dryers in liquid line between compressor and thermostatic expansion valve or in the suction line of the compressor.

END OF SECTION

*********************************************************

Do not delete the following reference information:

*********************************************************

FOR LANL USE ONLY

This project specification is based on LANL Master Specification 23 2300 Rev. 2, dated September 15, 2009.