section 23 4133.16

HEPA FILTERS – ASME AG-1, SECTION FK, special

************************************************************************************************************************

LANL MASTER SPECIFICATION SECTION

This section covers ASME AG-1, Section FK, Special HEPA filters that include radial-flow filters, axial-flow circular filters, and axial-flow rectangular filters that are not included in Section FC.  Two other types of HEPA filter are covered in two other sections:

- Section 23 4133.13 HEPA Filters - ASME AG-1 Section FC that includes common sizes of square filters with flow rates of up to 2000 scfm.

- Section 23 4133.19 HEPA Filters - Auxiliary Nuclear Grade includes encapsulated filters with one or two end connections and other filter configurations not included in ASME AG-1, Sections FC or FK.

Higher pressure, high efficiency filters for process piping (e.g., Swagelok) are addressed in Section 43 3113.37.

Edit this document so that it only includes the information pertaining to the type of HEPA filter being specified.  To seek a variance from applicable requirements, contact the ESM Mechanical POC.

When editing to suit a specific project, author shall add job-specific requirements and delete only those portions that in no way apply to the activity (e.g., a component that does not apply).  Edit this document so that it only includes the information pertaining to the type of HEPA filter being specified.    To seek a variance from applicable requirements, contact the ESM Mechanical POC.

When assembling a specification package, include applicable sections from all Divisions, especially Division 01, General Requirements.

Information within “stars” is provided as guidance to the author responsible for revising this document.  Delete information within “stars” during editing.  Information within [ ] needs to be edited for the specific project.  Some of this information starting and ending in “stars” is also guidance that needs to be removed during editing

This template was prepared by an organization operating under a quality assurance program that meets the requirements of 10 CFR 830 (suitable for ML-1 through ML-4 projects).  Implementation of this document requires modification to meet project-specific requirements; responsibility for this lies with the author.  The author shall apply a graded approach to quality assurance based on the management level designation of the project.  When this document is used with nuclear facilities subject to 10 CFR 830, modification to it must be performed by an individual or organization operating under a quality assurance program that meets the requirements of that CFR.

The filters listed in the Specifier’s Reference webposted under 23 4133.13 in Div 23 are all HEPA filters that have been qualified to Article 5000 of ASME AG-1, Section FC.  These filters can be used as the basis for determining if a Type 2 or Type 4 Section FK filter is eligible to be considered qualified.

************************************************************************************************************************

general

Summary

Section Includes

ASME AG-1, Section FK Special HEPA Filters

Related Sections

[Section 23 3225 Bag-in Bag-out Housings]

[Section 23 4133.13 HEPA Filters - ASME AG-1, Section FC]

[Section 23 4133.19 HEPA Filters - Auxiliary Nuclear Grade]

Applicability

Filters to be installed in confinement ventilation systems for containing radioactive particles; their safety function and primary critical characteristic is particle removal efficiency of at least 99.97 percent for 0.3 micrometer particles of an approved aerosol test.

Procurement and installation of HEPA filters for Department of Energy (DOE) facilities at Los Alamos National Laboratory.

Filters for use in air and gas streams with a 250 degrees F maximum continuous temperature.

References

Except for NQA-1, follow latest edition of all documents invoked herein (editions below reflect those used in the development of this template).

American Society of Mechanical Engineers (ASME)

ASME AG-1-2017, Code on Nuclear Air and Gas Treatment, Section FC, HEPA Filters

ASME AG-1-2017, Section FK, Special HEPA Filters

ASME NQA-1, Quality Assurance Program Requirements for Nuclear Facilities, 2008 with 2009 addenda

Department of Energy (DOE)

DOE-STD-3020-2015, Specification for HEPA Filters Used by DOE Contractors

DOE-HDBK-1169-2003, Nuclear Air Cleaning Handbook, Appendix A

Underwriter Laboratories

UL-586, Standard for High Efficiency Particulate Air Filter Units

Code of Federal Register

10 CFR 830.122 Quality Assurance Criteria

40 CFR 261, Identification and Listing of Hazardous Waste

*************************************************************************************************************

The edition of QPA-RIT-WI-002 needs to be verified as latest; if it is revised, then the following reference AND Appendix A will need revision by specifier (and notify template owner).  https://caosp.lanl.gov/dc/default.aspx

*************************************************************************************************************

Los Alamos National Laboratory

QPA-RIT-WI-002.007, Work Instruction for Receipt Inspection of ML-1, ML-2, and ML-3 HEPA Filters Used in Ventilation Systems

Definitions, acronyms and abbreviations

Acceptance Test: Inspection and testing of a filter to verify certain characteristics or properties, which determine the acceptance or rejection of that filter.

Air Flow:  The volume of air through a system per unit of time, expressed as standard cubic feet per minute (scfm) or actual cubic feet per minute (acfm).

Approved Test Aerosol: Particle-generating materials approved by DOE and used as test aerosols for performing testing of HEPA filters.

ASME AG-1, Section FC HEPA Filters: Axial flow square open faced, fire resistant, HEPA filters used in nuclear air cleaning systems.

ASME AG-1, Section FK Special HEPA Filters:  Radial flow, Axial flow circular open face, and Axial flow rectangular open face (not covered by Section FC), fire resistant, HEPA filters used in nuclear air cleaning systems.

C of C: Certificate of Conformance: A document signed or otherwise authenticated by an authorized individual certifying the degree to which items or services meet specified requirements.

DOE:  Department of Energy

EPA: Environmental Protection Agency

Filter Test Facility (FTF): A facility established by the DOE specifically to conduct performance tests and quality assurance inspections of HEPA filters.

High Efficiency Particulate Air (HEPA) Filter:  A throwaway, extended-medium dry-type filter with a rigid casing enclosing the full depth of the pleats.  The filter shall exhibit a minimum efficiency of 99.97% when tested with an aerosol of 0.3 µm diameter.

In-Place Leakage Test:  A test conducted after HEPA filters have been installed where the downstream test aerosol concentration (in µg/liter) is compared to the upstream test aerosol concentration (in µg/liter) and is reported as a percentage. This test uses a polydispersed aerosol having a light-scattering number mean diameter of 0.7 µm and a size range of 0.1 to 3.0 µm.

LANL: Los Alamos National Laboratory

Nominal Air Flow Rating: The flow rate which HEPA filters are identified by the manufacturer and confirmed at the FTF.

Nuclear Facility: A DOE facility in which radioactive materials are produced or handled to the degree that environmental protection is required.

Penetration: The downstream test aerosol concentration, expressed as a percentage of the upstream test aerosol concentration where a monodispersed aerosol with a light-scattering number mean diameter of 0.3 µm is used.

QA: Quality Assurance

Qualification Test: A test, often destructive, of a prototype or randomly selected production filter to establish its capability to meet certain functional and specification requirements.  The results of the test are considered to be typical of individual items or model number, which are of the same design and are manufactured by the same process.

SST: Stainless steel

wg:  water gage

LANL-PERFORMED WORK

LANL will perform receipt inspection on filters ordered by LANL organizations in accordance with Article 3.1 of this Section.

LANL will do in-place leakage testing of HEPA filter(s) after successful installation in systems required to be tested.

DESIGN REQUIREMENTS

Materials for the components below are specified in Article 2.3, Materials of Construction.

*************************************************************************************************************

Edit Design Requirements as necessary for specific application.

Type 1:  As of the date of this document, no Section FK Type 1 HEPA filters have been qualified by any of the three manufacturers from which LANL usually buys filters.  Therefore, the use of Type 1 filters is discouraged at this time.

Types 2 and 4: Both Type 2 and Type 4 filters may be deemed qualified based on the qualification of a filter size listed in ASME AG-1, Section FC, Table FC-4110-1.  The filters listed in the Specifier’s Reference webposted under 23 4133.13 in Div 23 have been qualified to Article 5000 of ASME AG-1, Section FC.  These filters can be used as the basis for determining if a Type 2 or Type 4 Section FK filter is eligible to be considered qualified.  See ASME AG-1, Section FK, Articles FK-5200 and FK-5400; and DOE-STD-3020-2015 (Section 6.1.2) for guidance on determining how to use the information contained in the Specifier’s Reference.

Types of HEPA Filter as defined in ASME AG-1, Section FK

- Type 1 – Radial flow filters

- Type 2 – Axial flow circular filters

- Type 4 – Axial flow rectangular filters that are size variation of those addressed in ASME AG-1, Section FC

Types of Filter Pack are defined in ASME AG-1, Section FK

- Type A – Folded filter media with corrugated separator/supports

- Type B – Mini-pleat medium with glass fiber or noncombustible thread separators

- Type C – Continuous corrugated filter media folded without separators

##### Type D – Folded filter media with glass fiber ribbon separators of glass fiber media or noncombustible threads glued to filter media

*************************************************************************************************************

Design in accordance to ASME AG-1, Article FK-4000, Design

Type [1, 2, or 4] HEPA filter

Type [A, B, C or D (A and B only apply to Type 2 and 4 HEPA filters)] Filter Pack

Case Material: [Wood (for Type 4 only)] [Metal]

Gasket Type and Location: [Elastomer Seal] [Gelatinous Seal] on [Internal or External (for Type 1 HEPA filter only)] [Upstream Face, Downstream Face, or Both Faces (for Types 2 and 4 HEPA filters only)]

[Faceguard:  [Galvanized steel] [Stainless steel] on both faces (for Types 2 and 4 HEPA filters only)]

[Grilles:  [Stainless steel [Perforated metal] [Expanded metal] (for Type 1 HEPA filters only)]

*************************************************************************************************************

Separators are only specified for Type A Filter Packs. Separators used for Type A Filter Packs are made from aluminum.  If aluminum will be corroded by the airstream the filter will be exposed to then a coated separator (vinyl coating) should be specified.  Type B and D filter packs have glass fiber or noncombustible threads as part of the media.  So separators for these filter packs are not called out.

*************************************************************************************************************

Separators (for Type A Filter Packs only): [Coated]  [Uncoated] Aluminum

ACTION Submittals

*************************************************************************************************************

Submittal of QA plan is not necessary if filter manufacturer is on the current LANL IESL (see internal QPA-IQ web site).

The Submittals as listed are required for ML-1, ML-2, and ML-3 HEPA filters.  For ML-4 HEPA filters, the Submittals listed may be edited to include fewer requirements.

For Safety Class (ML-1) and Safety Significant (ML-2) applications the filters must be qualified to ASME AG-1, Section FK.

*************************************************************************************************************

From Manufacturer before order placement

*************************************************************************************************************

Article FK-5100 is used for qualification testing of Type 1 Radial flow filters.

Article FK-5200 is used for qualification testing of Type 2 Axial flow circular filters

Article FK-5400 is used for qualification testing of Type 4 Axial flow rectangular filters

*************************************************************************************************************

[Certification documentation from an independent test facility indicating that HEPA filter model(s) have been successfully qualified or requalified within the past five years in accordance with ASME AG-1, Article [FK-5100] [FK-5200] [FK-5400] (with DOE-STD-3020-2015, Section 6.1.2 allowances).]

From Manufacturer before shipment

Certified performance test results by the manufacturer for aerosol penetration and airflow resistance.  Test results are to be identified for each filter by serial number.

[Copy of the HEPA filter manufacturer’s QA plan identifying procurement, fabrication, test & inspection, material traceability and non-conformity controls for approval.]

Certificate of Conformance (C of C) that is signed or otherwise authenticated by authorized individuals certifying the degree to which items or services meet specified requirements.  (Paraphrased from ASME AG-1, Article AA-1400.)

The C of C shall include:

Purchase Order (PO) number.

Purchased item identified by model number.

The serial numbers of all filters included in the shipment to which the C of C is applicable.

Any approved changes, waivers, or deviations from this Section.

Statement indicating that filters meet the following requirements:

        - The filters conform to the requirements in ASME AG-1, Section FK, manufacturer’s QA plan, and Article 1.7.

        - Filter construction is per DOE-STD-3020-2015- and Article 1.5 of this Section.

        - Qualification and Acceptance Test reports submitted above are applicable to the items delivered, and (if necessary) cross reference by serial number and any other item identifier.

        - [Gaskets shall be glued firmly and continuously to the case. Gasket shall not extend more than 1/16 in. (1.6 mm) over either side of the seating surface at any point.]

*************************************************************************************************************The following statement regarding case panels only applies to Type 4 filters with a metal case.  It is included here to meet a requirement in DOE-HDBK-1169-2003, Appendix B.

*************************************************************************************************************

        - [Case panels have been assembled into the frame by potting a sub-assembly consisting of the filter pack and side panels into the top and bottom panels (but not corners) using adhesive meeting the requirements of DOE-STD-3020-2015.]

        - Certification of compliance with UL-586, and appropriate label applied to filter case, as evidence of compliance with requirements for resistance to flame and heated air.

Warranty documentation - guarantee against failure in proper use or operation caused by defective materials and/or workmanship for a period of 1 year from the date of acceptance at LANL.

From the FTF before shipment

      - Certified performance test results by the FTF for aerosol penetration and airflow resistance.  Test results identified for each filter by serial number.

quality assurance

Seller’s Quality Assurance Requirements

Manufacture, inspect, test, and ship filters under a quality assurance program meeting the applicable requirements of ASME AG-1-2008 with 2009 addenda.

Packaging and shipping

Package and ship filters in accordance with Article FK-7000; DOE-STD-3020-2015, Sections 7.2 and 7.3; and:

Place filter cartons in a sturdy wooden crate with the lid/top secured with removable screws or lag bolts to eliminate unit handling at carrier inter change points and avoid unnecessary damage.  Shipping crates shall be labeled in accordance with Article FK-9200.

Ship filters properly oriented, as indicated on shipping container.

For large shipments, ship the entire shipment in a sealed dedicated trailer to provide an additional quality assurance of product shipping and handling.

Filters returned to the manufacturer from the FTF or shipped from the FTF to LANL must be re-packaged per the above requirements.

products

product options and substitutions

No substitutions allowed.

manufacturers

The following is a list of some of the manufacturers that produce nuclear grade HEPA filter products that may meet the requirements of this Section and ASME AG-1, Section FK.  However, these manufacturers are not exempt from any seller requirements [including the submission of qualification certification for approval].

AAF International (American Air Filter

AAF|Flanders

Camfil Inc.

Materials of construction

General

The following are unacceptable materials of construction:  particle board, asbestos, cadmium-coated metals, and any material that generates EPA regulated wastes as specified in 40 CFR 261.

Filter Media

Manufacture silicate media in accordance with ASME AG-1, Article FK-3130.

[Separatorless filter packs shall use formed media to fulfill the function of the separator.]

[End Caps, Grilles, and Flanges for Type 1 Filters]

[Stainless Steel, Type [304] [316], minimum 18 gauge in accordance with ASME AG-1, Article FK-3110 and Article FK-4121.]

[Case for Type 2 Filters]

[Stainless Steel, Type [304] [316], minimum 14 gauge in accordance with ASME AG-1, Article FK-3110 and Article FK-4122.]

[Case for Type 4 Filters]

[Stainless Steel, Type [304] [316], minimum 14 gauge in accordance with ASME AG-1, Article FK-3110 and Article FK-4123.]

[OR]

************************************************************************************************************* Before specifying wood-case filters, verify that they are still allowed under the current combustible load analysis for the facility.  Facilities with large filter plenums may now be restricting the use of wood-case HEPA filters.   Note:  Wood-case filters generally cost less than metal-case filters but are more likely to be rejected during receipt inspection due to being out of square. Also, metal-case filters weigh approximately 50% more than wood-case filters, so ensure mounting frames can support the additional weight.

*************************************************************************************************************

[Plywood in accordance with ASME AG-1, Article FK-3110 (a) (marine plywood), or Article FK-3110 (b) (exterior plywood).]

[Fasteners (when used)]

[Use fasteners that are in accordance with DOE-STD-3020-2015 (Section 5.3.7).]

*************************************************************************************************************

Select only one type of separator per filter Type.

*************************************************************************************************************

[Separators (when used)]

[Aluminum, conforming to ASME AG-1, Article FK-3160, (a).]

[OR]

[Acid Resistant Aluminum, conforming to ASME AG-1, Article FK-3160, (b).]

[OR]

[Glass Ribbon, conforming to ASME AG-1, Article FK-3160, (c).]

[OR]

[String, conforming to ASME AG-1, Article FK-3160, (d).]

[OR]

[Hot Melt, conforming to ASME AG-1, Article FK-3160, (e).]

*************************************************************************************************************A single splice is allowed only for Type 1 HEPA filters.  No other filters are allowed to have splices.

*************************************************************************************************************

Adhesives used to [splice the media,] fasten gaskets to filter case, and seal the filter pack or faceguards to the case.

Self-extinguishing in accordance with ASME AG-1, Article FK-3150.

Gaskets and Seals

[Elastomer Gasket – in accordance with ASME AG-1, Article FK-3121.]

[OR]

[Gelatinous Seal – in accordance with ASME AG-1, Article FK-3122.]

*************************************************************************************************************Faceguards only apply to Type 2 and Type 4 filters.

*************************************************************************************************************

[Faceguards]

[Faceguards – galvanized steel in accordance with ASME AG-1, Article FK-3140.]

[OR FOR HIGHLY-CORROSIVE ATMOSPHERES]

[Faceguards -Type 304 stainless steel in accordance with ASME AG-1, Article FK-3140.]

*************************************************************************************************************Grilles only apply to Type 1 filters.

*************************************************************************************************************

[Grilles]

[Grilles - in accordance with ASME AG-1, Article FK-3170.]

Fabrication

General

        - Fabricate in accordance with ASME AG-1, Articles FK-6000, DOE-STD-3020-2015 (Section 5.4), and ASME NQA-1-2008 with 2009 addenda.

        - [Install faceguards on each face of all Type 2 and Type 4 filters.  Install faceguards such that they are held firmly in-place, do not interfere with the sealing of the gasket, and do not pose a puncture hazard to personnel handling the filter.]

        - [Install [internal] [external] elastomer gasket on Type 1 HEPA filters in accordance with ASME AG-1, Article FK-4141.]

        - [Install [internal] [external] gelatinous seal gasket on Type 1 HEPA filters in accordance with ASME AG-1, Article FK-4142.]

        - [Install elastomer gasket on [upstream] [downstream] [both] face[s] of Type 2 and Type 4 HEPA filters in accordance with ASME AG-1, Article FK-4141.]

        - [Install gelatinous seal gasket on [upstream] [downstream] face of Type 2 and Type 4 HEPA filters in accordance with ASME AG-1, Article FK-4142.]

*************************************************************************************************************The labeling includes a UL label indicating successful testing per UL-586.  The UL label is required for all qualified HEPA filters.

*************************************************************************************************************

        - Label each filter and shipping container (carton containing one filter) in accordance with DOE-STD-3020-2015 (Section 6.1.6).  Labels must be permanently affixed to the filter.

  - QUALIFICATION AND Acceptance testing

************************************************************************************************************* As of the date of this Master Specification Section, no Section FK Type 1 HEPA filters have been qualified by any of the three manufacturers from which LANL usually buys filters.  However, both Type 2 and Type 4 filters may be deemed qualified based on the qualification of a filter size listed in ASME AG-1, Section FC, Table FC-4110-1.  The filters listed in the Specifier’s Reference webposted under 23 4133.13 in Div 23 are all HEPA filters that have been qualified to Article 5000 of ASME AG-1, Section FC.  These filters can be used as the basis for determining if a Type 2 or Type 4 Section FK filter is eligible to be considered qualified.  See Section FK, Article FK-5200 and Article FK-5400, and DOE-STD-3020-2015 (Section 6.1.2) for guidance on determining how to use the information contained in the Specifier’s Reference for Safety Class (ML-1) and Safety Significant (ML-2) applications require that a qualified filter be specified.

*************************************************************************************************************

    - [Have qualification testing of filters and filter media performed by an independent test facility in accordance with ASME AG-1, Article FK-5000 (with DOE-STD-3020-2015, Section 6.1.2 allowances) prior to start of manufacturing of filters for this purchase.]

    - Perform factory inspection of filters in accordance with ASME AG-1, Article FK-5500.  [Additionally, LANL will be inspecting Type 4 filters to LANL QPA-RIT-WI-002.007 (see Appendix A of this Section, specifically Attachment 1, Table 2 for inspection criteria).  Filters that do not meet these inspection criteria will be rejected.]

    - Perform factory production testing of aerosol penetration and resistance to air flow for each filter in accordance with ASME AG-1, Article FK-5600.

    - Ship filters to the FTF (Air Techniques International Testing Laboratories, Suite 104, 1708 Whitehead Rd., Baltimore, MD 21207, phone 410-277-8981, fax 410-277-3448, email ATITL@atitest.com) to have inspection and performance acceptance testing performed in accordance with ASME AG-1, Article FK-5600,[and] DOE-STD-3020-2015[, and LANL QPA-RIT-WI-002.007, Table 2 (see Appendix A of this Section) for Type 4 filters.  Filters that do not meet these inspection criteria are not acceptable].

- execution (performed by AND AT lanl)

  - Examination

    - [Inspect all ASME Section FK, Type 4 filters upon shipment receipt to LANL QA-RIT-WI-002.007. Verify documentation from Article 1.6 is included and is complete.]

    - [Inspect all ASME Section FK, Type 1 and 2 filters upon shipment receipt to the requirements contained on LANL Form 1952.  Verify documentation from Article 1.6 is included and is complete.]

  - Storage

- Store filters in accordance with Article FK-7000, DOE-HDBK-1169-2003, Appendix A or in accordance with the manufacturer’s requirements, whichever is more restrictive, and:

- Store filters properly oriented, as indicated on shipping container.

- When stored out of the shipping container, stagger the box pattern on each level so as to not have columns of boxes that can easily topple.

- Shelf life: Do not store filters for more than 10 years after manufacture date.

  - Handling and installation

- Handle and install HEPA filters in accordance with DOE-HDBK-1169, Appendix A, Parts A.5 and A.6.

  - Field Quality control

- Test filters after installation for leakage in accordance with LANL requirements.

- Replace all filters that fail LANL in-place leakage test.

- Notify Seller, Purchasing Group, and Quality Assurance Group of filter rejections and re-evaluate the future procurement status of that manufacturer and/or model.

*************************************************************************************************************Appendix A is to be included with all ML-1, ML-2, and ML-3 filter procurements; verify that it is latest at https://caosp.lanl.gov/dc/default.aspx

*************************************************************************************************************

APPENDIX A

LANL QPA-RIT-WI-002.007 Excerpts:  Attachment 1, Table 2 (only) and Attachments 2 & 3

end of section MAIN BODY

*********************************************************

Do not delete the following reference information:

*********************************************************

THIS STATEMENT IS for lanl use only

This project specification section is based on LANL Master Specification Section 23 4133.16 Rev. 0, dated December 12, 2018.

APPENDIX A

LANL QPA-RIT-WI-002.007 Excerpts:

(Attachment 1, Table 2 (only) and Attachments 2 & 3)

|  | Receipt Inspection of ML-1, ML-2, and ML-3 HEPA Filters Used in Ventilation Systems QPA-RIT-WI-002.007 |
| --- | --- |
|  | Supplementary Inspection Plan for ML-1, ML-2, and ML-3 HEPA filters |
|  | Quality & Performance Assurance Division |

(Portion of Attachment 1)

| Table 2 |
| --- |
| Item | Feature | Inspection Method | Acceptance Criteria |
| 12 | Packaging | Visual | The filters must be packed with the pleats vertical. (Exception for Type B “mini-pleat” filters, which should be packed with the pleats horizontal.) |
| 13 | Workmanship | Visual | The filter must be free from foreign matter (dirt, oil, or viscous material) and damage, such as distorted or cracked case, or deformation or sagging of the medium, separators, and faceguards. The filter must also be free of any cracks in the adhesive bond, and cracks or holes in the exposed portions of the filter medium. All required fasteners must be securely installed. |
| 14 | Filter Construction | Measurement (Refer to Attachment 3) | Filter Height and Width: The filter’s height and width must conform to purchase order requirements within the following tolerances (from DOE-STD-3020-2015, Table 5-2): Face Dimension < 24” (610 mm) = tolerance of -1/16”, +0” (-1.6mm, +0mm) Face Dimension > 24” (610 mm) = tolerance -1/8”, +0” (-3 mm, +0mm) |
| 15 |  | Measurement (Refer to Attachment 3) | Filter Depth: The filter’s depth must conform to purchase order requirements within the following tolerance, for all filter sizes (from DOE-STD-3020-2015, Table 5-2): Tolerance: -0”, +1/16” (-0 mm, +1.6 mm) |

|  | Receipt Inspection of ML-1, ML-2, and ML-3 HEPA Filters Used in Ventilation Systems QPA-RIT-WI-002.007 |
| --- | --- |

| 16 |  | Measurement (Refer to Attachment 3) | The length of both filter diagonals must be equal within a tolerance of 1/8 inches (-3 mm) (tolerance from DOE-STD-3020-2015, Table 5-2). Note: Measuring the diagonals is the preferred method. However if diagonals cannot be measured accurately (due to configuration anomalies at the corners) the following alternatives method may be used. Straddle each corner with a 24”x16” (minimum size) carpenters square. The case must be square such that the maximum gap allowed along the 24” length is 5/64”. This alternate method is mainly used on metal filters because the metal case corners generally do not allow the determination of the true corner. |
| --- | --- | --- | --- |
| 17 |  | Measurement (Refer to Attachment 3) | The width of the filter’s gasket surface must be ¾” (19 mm), within a tolerance of + 1/16” (+ 1.6 mm) |
| 18 |  | Visual | There must be no signs of repaired, tears, pinholes, or other defects in the portion of the filter media that is visible. |
| 19 |  | Visual | There must be no missing separators (where used). |
| 20 |  | Visual | The pleats must be visually perpendicular to the top and bottom of the case, and must be straight with no deviations more than ½” (12 mm) from a line drawn from one end of the pleat to the other end of the pleat. |
| 21 | Filter Construction—Wooden Cases Only | Visual | The case panels must be joined with rabbet joints. |
| 22 |  | Visual | The end points of the fasteners must not penetrate the outside surface of the case. |
| 23 |  | Visual | There must be no splinters or rough edges that might penetrate or cut worker’s gloves or injure the fingers of personnel handling the filters. |
| 24 |  | Visual | The case faces, edges, and joints must be thoroughly coated with sealant to minimize permeability. |
| 25 | Filter Construction—Metal Cases Only | Visual | Metal cases must have a double-turned, ¾” (19 mm) wide flange on each face, OR a fluid-seal socket or sleeve. |
| 26 |  | Visual | Case panels must be assembled into the frame by riveting or bolting the corners. |
| 27 | Gaskets (n/a for Fluid Seal) | Visual | The gasket adhesion across the width may vary however the full length of the gasket must be firmly and continuously glued to the filter case and not be loose, distorted, peeling away from the case. |
| 28 |  | Visual | The gasket must not extend more than 1/16” (1.6mm) over either side of the seating surface at any point. |
| 29 |  | Visual | Gaskets must be of one-piece or made up of strips joined at the corners by keyhole, keystone, or other interlocking type joints. If applicable, edges of any gasket joint shall be thoroughly coated with adhesive. |
| 30 | Fluid Seal (n/a for Gasket Seal) | Visual | Fluid must be present in the entire length and width of the channel and at approximately the same depth as the channel. |
| 31 |  | Visual | Small particles such as wood chips and metal filings must not be present on the external surface of the fluid seal. |
| 32 | Faceguards (When Specified) | Visual | Faceguard must be installed so that projecting wires or edges do not form a puncture hazard to personnel handling the filter. |
| 33 |  | Visual | Faceguard must be installed in the face of the filter in such a manner that it shall not directly contact the gasket or create a leak path. Note: N/A for wood case filters which have the face guard stapled to the case and where this condition can be verified by inspecting the non-gasket end of the filter. |
| 34 |  | Visual | Faceguard edges must be firmly embedded in adhesive or otherwise secured. |

APPENDIX A, LANL QPA-RIT-WI-002.007 Excerpts, CONTINUED

|  | Receipt Inspection of ML-1, ML-2, and ML-3 HEPA Filters Used in Ventilation Systems QPA-RIT-WI-002.007 |
| --- | --- |

Attachment 2:

DOE-STD-3020-2015, Table 5-1

APPENDIX A, LANL QPA-RIT-WI-002.007 Excerpts, CONTINUED

|  | Receipt Inspection of ML-1, ML-2, and ML-3 HEPA Filters Used in Ventilation Systems QPA-RIT-WI-002.007 |
| --- | --- |

Attachment 3:

DOE-STD-3020-2015, Table 5-2