SECTION 26 0529

Hangers and supports for electrical systems

*************************************************************************************************************

LANL MASTER SPECIFICATION SECTION

Word file available at https://engstandards.lanl.gov

Rev. 7 Summary of Changes: Added notes about raceways 2" and less and submittals for hangars. Minor wording changes, added “or equivalent” to manufacturers callouts, removed requirement for swivel hangers, added allowance for using u-channel from different manufacturers, removed requirement for concrete bases.

This section is for non-seismic supports only.  For seismic, use 26 0548.16.

Electrical raceways that are 2 inches or less are exempt from seismic design.  This should be considered when designing systems.  For example, for a 400-amp system, the designer might want to use parallel 3/0 conductors in two, 2-inch raceways instead of 600 kcmil conductors in a single larger raceway that might require seismic design.

This template must be edited for each project.  In doing so, specifier must add job-specific requirements.  Brackets are used in the text to indicate designer choices or locations where text must be supplied by the designer.  Once the choice is made or text supplied, remove the brackets.  This document must also be edited to delete specification requirements for processes, items, or designs that are not included in the project -- and specifier’s notes such as these.  To seek a variance from requirements that are applicable, contact the Engineering Standards Manual Electrical POC. Please contact POC with suggestions for improvement as well.

When assembling a specification package, include applicable Sections from all Divisions, especially Division 1, General requirements.

Section developed for ML-4 projects.  For ML-1, 2, and 3 applications, additional requirements and independent reviews should be added if increased confidence in procurement or execution is desired; see ESM Chapter 1 Section Z10 Specifications and Quality Sections.

*************************************************************************************************************

- GENERAL

  - SECTION INCLUDES

    - Furnish and install, hangers, supports, anchors, concrete bases, and other positive fastenings for electrical components such that gravity loads are adequately transferred to the structure.

QUALITY ASSURANCE

    - Furnish and install hangers and supports that conform to the requirements of the following codes and standards:

NFPA 70, National Electric Code (NEC)

IBC, International Building Code

NECA 1, Standard Practices for Good Workmanship in Electrical Contracting

Metal Framing Manufacturers Association

MFMA-4, Metal Framing Standards Publication

MFMA-102, Guidelines for the Use of Metal Framing

*************************************************************************************************************

Edit the following to match project requirements.   In most cases, this section should be deleted as these are, generally, commodity items.  If there is a special hangar or support, the Engineer of Record might want to have this reviewed.  In this case, specify the particular item in the bracket.

*************************************************************************************************************

ACTION SUBMITTALS

    - Submit the following in accordance with project submittal procedures.

Catalog Data: Submit catalog data for [each type of product specified] [__].  Include information substantiating equivalent corrosion resistance to zinc coated steel of alternative treatment, finish, or inherent material characteristic.

Receiving, Storing and Protecting

    - Receive, store, and protect products according to NECA 1.

PRODUCTS

  - Substitutions

    - Alternate products may be accepted; follow Section 01 2500, Substitution Procedures.

COATINGS and Materials

    - Furnish products for use indoors protected with zinc coating or with treatment of equivalent corrosion resistance using approved alternative treatment, finish, or inherent material characteristic.

    - Furnish products for use outdoors or in damp or corrosive indoor locations with hot-dip galvanized coating or with treatment of equivalent corrosion resistance using approved alternative treatment, finish, or material such as stainless steel with inherent corrosion resistant characteristics.

RACEWAY SUPPORTING DEVICES

    - Furnish supports as described below for the installation of raceway systems.

    - Use pressed steel, single bolt hangers to support individual RMC, IMC, or EMT raceways from threaded rods or beam clamps.  Manufacturer:  Steel City “6H_ B Series,” or equivalent.

    - For individual runs of EMT up to trade size 1, above accessible ceilings, use spring steel conduit clips with positive snap closure.  Manufacturer: ERICO CADDY “M Series,” or equivalent

    - Use malleable iron conduit clamps to secure individual RMC, IMC, or EMT raceway runs across, parallel, or perpendicular to beams, channels and angle supports.  Manufacturer: Steel City “RC, EC, and PC Series,” or equivalent

    - Use two-piece carbon steel riser clamps for individual vertical raceways passing through floors.  Manufacturer: Kindorf “C-210 Series,” or equivalent.

    - Use snap-on type, one-hole steel straps to secure individual raceways up to trade size 2 to flat, dry interior surfaces.  Manufacturer: T&B “1210 Series” for RMC and IMC, and “4100 Series” for EMT, or equivalent.

    - Use one-hole malleable iron straps to secure individual raceways up to trade size 4 to flat, dry interior surfaces.  Manufacturer: T&B “1275 Series,” or equivalent.

    - Use one-hole malleable iron straps and backing plates to secure individual conduits to flat exterior or damp flat interior surfaces.  Manufacturer: T&B “1275 Series” straps with 1350 Series” spacers, or equivalent.

OUTLET BOX SUPPORTING DEVICES

    - Furnish prefabricated sheet steel brackets to support outlet boxes from metal studs in dry-wall construction.

    - Single outlet boxes: Provide brackets that are inset to allow for dry-wall ring and have a far-side support leg.  Manufacturer: ERICO CADDY “H Series” or “MEB1” attached with “SMS8” low-profile, self-tapping screws, or equivalent.

    - Multiple outlet boxes: Provide brackets that are inset to allow for dry-wall rings and span from stud to stud.  Manufacturer: ERICO CADDY “RBS Series” attached with “SMS8” low-profile, self-tapping screws, or equivalent.

HANGER RODS

    - Furnish mild steel rods that conform to ASTM A 307, Standard Specification for Carbon Steel Bolts and Studs, 60 000 PSI Tensile Strength.

    - Furnish rods that are threaded on both ends, threaded on one end, or continuous threaded with UNC (coarse) thread pitch.

## Fasteners

    - Pre-set Concrete Inserts

Furnish pre-set concrete inserts as shown on the Drawings.

Manufacturers:

Continuous inserts for wood forms: B-Line “B22I-12” or longer.

Spot inserts for wood forms or metal decks: B-Line “B2500” with “N2500” nut, “B2501”

    - Post-installed Concrete Anchors

Furnish post-installed expansion, adhesive, or undercut concrete and masonry anchors as shown on the Drawings and Section [05 0520, Post-Installed Concrete and Grouted-Masonry Anchors – Normal Confidence] [and/or] [05 0521, Post-Installed Concrete Anchors – Nuclear Safety].

Power-actuated threaded studs: Use zinc-plated carbon steel or stainless steel suitable for the intended service:

        - 1/4-20 threaded stud: Manufacturer: Hilti X-W6

        - 3/8-16 threaded stud: Manufacturer: Hilti W10

    - Beam Clamps:

Furnish beam clamps that are NRTL-listed and compliant with Federal Specification WW-H-171E Type 23 or Manufacturers’ Standardization Society SP-69 and SP-58 Type 23.

Provide beam clamps with a locknut on the setscrew.

Provide NRTL-listed restraining strap for each beam clamp. Strap shall be not less than 16-gauge thickness, not less than 1 inch wide, and of sufficient length to wrap around the beam flange not less than 1 inch.

*************************************************************************************************************

ML-1/2 caution on U-channel systems when using an upgraded version of this section (or if specifying in other sections) for SC/SS nuclear safety related installations:

Based on TRP II project experience, projects should not purchase B-Line (and possibly not competitor) products through a typical distributor who is on the LANL IESL and consider it as meeting NQA-1 due to material traceability problems.  Instead, use the Commercial Grade Dedication method for all safety credited components and have sufficient testing and documentation with traceability to allow use.  The exception may be Unistrut when NOVA Machine Products, their sole IESL/NQA-1 nuclear-pedigree-line distributor is utilized (verify on current IESL).

*************************************************************************************************************

FRAMING CHANNEL SYSTEMS

    - Furnish U-channel framing systems that conform to MFMA-4 and are fabricated using minimum 12-gage steel.

    - Furnish fittings and accessories that mate and match with U-channel and are of the same manufacturer. Use two-piece, single bolt type conduit straps on U-channel supports.  In existing buildings, where items from the same manufacturer are not available, fittings and accessories that mate and match are acceptable.

    - Manufacturers: Unistrut, B-Line, Superstrut.

FABRICATED SUPPORTING DEVICES

    - Furnish shop- or field-fabricated supports or manufactured supports assembled from U-channel components.

    - Furnish steel brackets fabricated from angles, channels, and other standard structural shapes.  Connect with welds, machine bolts, or both to form rigid supports.

EXECUTION

  - GENERAL

    - Install hangers and supports according to the NEC, IBC, NECA 1, the requirements in this Section, and specific supporting requirements in other Sections.

    - Conform to manufacturer's instructions and recommendations for selection and installation of hangers and supports.

    - Do not use wire or perforated strap for permanent supports.

    - Do not support conduits, boxes, or raceways from ceiling suspension wires.

EXAMINATION

    - Examine surfaces to receive hangers and supports for compliance with installation tolerances and other conditions affecting performance of the system.  Do not proceed with installation until unsatisfactory conditions have been corrected.

*************************************************************************************************************

Edit the following article to match project requirements.  Select either A or B as appropriate.  It is typical for the anchors to be post-installed.  In some cases, both A and B will be deleted.  Confirm with structural as to who should specify this.

*************************************************************************************************************

FASTENERS

    - [Pre-set inserts: Install pre-set inserts, in accordance with design drawings or as specified by structural engineering, for anchoring to reinforced concrete slabs, sides of reinforced concrete beams, and reinforced concrete walls.]

    - [Post-installed concrete anchors: Install in accordance with Section [05 0520, Post-Installed Concrete and Grouted-Masonry Anchors – Normal Confidence] [05 0521, Post-Installed Concrete Anchors – Nuclear Safety], the design drawings or as specified by the structural engineer, and the product’s ICC-ES report conditions of use.]

    - Masonry screw anchors: Use in accordance with NECA 1 and the product’s ICC-ES report conditions of use.

    - Powder-actuated threaded studs:

      - Use only to fasten clips or straps for individual RMC or IMC conduits trade size 1.5 and smaller or EMT trade size 2.5 and smaller.

      - Install in accordance with the product’s ICC-ES report conditions of use and the manufacturer’s instructions using recommended tools and loads.

      - Use only in uncracked concrete.

      - Install to provide embedment as indicated on the Drawings.

    - Hollow wall anchors: Use hollow wall anchors for fastening to wallboard, plaster, or paneling.

    - Toggle bolt anchors: Use toggle bolt anchors for fastening to block, wallboard, or plaster.

    - Use wood screws for fastening to wood construction.

    - Use beam clamps for fastening to structural metal beams, joists, and purlins.

      - Install a restraining strap at each beam clamp. Wrap the restraining strap around the beam flange not less than 1 inch. Where purlins or beams do not provide a secure lip for the restraining strap, secure the strap with a self-tapping screw or by through-bolting.

      - Use a locknut on each beam clamp set screw.

    - Use self-tapping screws or machine bolts, nuts, and washers for fastening to metal studs or metal surfaces.

    - The use of lead-cinch drop-in anchors is not allowed.

    - Torque threaded fasteners as recommended by the manufacturer’s instructions.

RACEWAY SUPPORTS.

    - Install individual and multiple (trapeze) raceway hangers and riser clamps as necessary to support raceways.  Provide U-bolts, clamps, attachments, and other hardware necessary for hanger assembly and for securing hanger rods and conduits.

    - Support individual horizontal raceways by separate conduit hangers.

    - Do not support raceways from ceiling suspension wires.

BOXES AND CABINETS

    - Support sheet metal boxes directly from the building structure, or by approved brackets or bar hangers, as shown on the Drawings or as required.  Where bar hangers are used, attach the bar to structure on opposite sides of the box.

    - Install surface-mounted cabinets and panelboards as shown on the Drawings or as required.

Framing Channel Systems

    - Select and install framing channel systems in accordance with MFMA-103.

    - Use framing channel to support electrical equipment that is mounted free of walls.

    - Use framing channel to support equipment mounted on walls that do not have sufficient strength to resist pull-out or wallowing out of equipment mounting bolts.

*************************************************************************************************************

Edit the following article to match project conditions; delete if there is no floor-mounted electrical equipment, Concrete bases must be designed by the Engineer of Record based on the properties of the load to be supported, the properties of the supporting structure, the required anchor bolt embedment lengths, etc. Construction details and dimensions for concrete bases must be shown on the Drawings.

*************************************************************************************************************

HANGER RODS

*************************************************************************************************************

Coordinate the following article with the Drawings.  Delete if there is no suspended equipment.

*************************************************************************************************************

    - Use minimum 3/8-inch diameter threaded rod; use larger diameter rod as indicated on the Drawings, in other Sections, or in the supported equipment manufacturer’s installation instructions.

    - Where threaded rod supports slotted channel, use a nut and helical split ring lock washer on both the top and bottom of the slotted channel.

END OF SECTION

*********************************************************

Do not delete the following reference information.

*********************************************************

THE FOLLOWING STATEMENT IS FOR LANL USE ONLY

This project specification section is based on LANL Master Specification Section 26 0529 Rev. 7, dated June 27, 2022.