SECTION 26 0548

VIBRATION AND Seismic CONTROLS FOR Electrical Systems

*************************************************************************************************************

LANL MASTER SPECIFICATION

Available online at http://engstandards.lanl.gov

This template must be edited for each project.  In doing so, specifier must add job-specific requirements.  Brackets are used in the text to indicate designer choices or locations where text must be supplied by the designer.  Once the choice is made or text supplied, remove the brackets.  The specifications must also be edited to delete specification requirements for processes, items, or designs that are not included in the project -- and specifier’s notes such as these.  To seek a variance from requirements in the specifications that are applicable, contact the Engineering Standards Manual Electrical POC.  Please contact POC with suggestions for improvement as well.

When assembling a specification package, include applicable specifications from all Divisions, especially Division 1, General requirements.

Specification developed for ML-4 projects.  For ML-1, 2, and 3 applications, additional requirements and independent reviews should be added if increased confidence in procurement or execution is desired; see ESM Chapter 1 Section Z10 Specifications and Quality sections.

*************************************************************************************************************

*************************************************************************************************************

The focus of this Section is seismic control / protection requirements for Performance Category (PC)-1 and PC-2 electrical nonstructural components.

Refer to LANL ESM Chapter 5, Sect. III, for seismic design and control for PC-3 nonstructural components.

Use this specification in conjunction with Section 13 4800 Sound, Vibration, and Seismic Control.

Hangers and supports addressed in this Section are non-structural and are intended support electrical components that must have either vibration isolation or designed anchors that will satisfy the seismic force and relative displacement requirements in the IBC and ASCE 7.

To be exempt from the requirement for a designed anchor, an electrical component must meet one of the following criteria:

1.	It is a PC-0 electrical component.

2.	It is an electrical component where all of the following apply:

a.	The seismic performance category is PC-1 or the component importance factor, Ip, is equal to 1.0. (Note that an electrical component that is required to function for life-safety purposes after an earthquake will have an importance factor, Ip, of 1.5; examples of such components include emergency lights, exit signs, and their associated emergency power supply circuits.)

b.	Flexible connections are provided between the component and associated conduit, busway, wireway, or similar electrical distribution system, and either

i.	The component weighs 400 lb or less and has a center of mass located 4 ft or less above the adjacent floor surface, or

ii.	The component weighs 20 lb or less, or, in the case of a distributed system (e.g. conduit), weighs 5 lb/ft or less.

NOTE: For the purpose of this exemption, conduits 2-1/2 trade size and smaller connected to panelboards, cabinets, and similar equipment are considered to be “flexible.”

3.	It is a PC-1, PC-2, Ip = 1.0, or Ip = 1.5, individually-supported conduit that is smaller than 2-1/2” trade size.

4.	It is a trapeze-supported assembly of PC-1, PC-2, Ip = 1.0, or Ip = 1.5 raceways with a total weight (including conductors) of less than 10 lb/ft.

5.	It is a PC-1, PC-2, Ip = 1.0, or Ip = 1.5 raceway (e.g. conduit, cable tray, wireway, busway) that is supported by hangers, and each hanger in the run is 12” or less in length from the raceway support point to the supporting structure, and, for rod hangers, has a swivel installed at the top of the rod to prevent inelastic bending of the rod.

If the project includes electrical components exceeding the above criteria, designed anchors are required for such components. The anchors must be designed for the seismic forces and relative displacements defined in ASCE 7, and construction details for each anchor must be shown on the Drawings and specified in this Section.

Electrical components that typically require seismic designed anchors include the following:

- Battery racks and battery cabinets.

- Cable trays:

  - All PC-3 and PC-4 cable trays.

  - Cable tray that is supported by hangers and any hanger in the cable tray run is longer than 12 inches.

- Conduits:

  - All PC-3 and PC-4 conduits.

  - Conduit that is larger than 2 inches trade size and is rigidly attached to the structure.

  - Conduit that is larger than 2 inches trade size, is supported by hangers, and any hanger in the conduit run is longer than 12 inches.

  - Trapeze supported conduits with an aggregate weight of 10 lb/ft or more including conductors.

- Busways (enclosed bus assemblies):

  - All PC-3 and PC-4 busways.

  - Busway that is supported by hangers and any hanger in the busway run is longer than 12 inches.

- Enclosed circuit breakers and safety switches:

  - All PC-4, PC-3, PC-2, and Ip = 1.5 enclosed circuit breakers and safety switches.

  - Enclosed circuit breaker or safety switch that weighs more than 20 lb with the center of gravity located more than 4 ft above the adjacent floor level.

  - Enclosed circuit breaker or safety switch that weighs more than 400 lb.

- Enclosed controllers:

  - All PC-4, PC-3, PC-2, and Ip = 1.5 enclosed controllers.

  - Enclosed controller that weighs more than 20 lb with the center of gravity located more than 4 ft above the adjacent floor level.

  - Enclosed controller that weighs more than 400 lb.

- Engine-generators

- Luminaires:

  - All emergency luminaires and exit signs.

  - Luminaire that weighs more than 20 lb.

  - Luminaire that is mounted above a designated exit pathway.

- Motor control centers

- Motors:

  - All PC-4, PC-3, PC-2, and Ip = 1.5 motors.

  - Motor that weighs more than 20 lb with the center of gravity located more than 4 ft above the adjacent floor level.

  - Motor that weighs more than 400 lb.

- Paging system speaker assemblies:

  - All PC-4, PC-3, PC-2, and Ip = 1.5 paging system speaker assemblies.

  - Paging system speaker assembly that weighs more than 20 lb.

  - Paging system speaker assembly that is mounted above a designated exit pathway.

- Panelboards:

  - All PC-4, PC-3, PC-2, and Ip = 1.5 panelboards.

  - Panelboard that weighs more than 20 lb with the center of gravity located more than 4 ft above the adjacent floor level.

  - Panelboard that weighs more than 400 lb.

- Switchboards

- Switchgear

- Transformers:

  - All PC-4, PC-3, PC-2, and Ip = 1.5 transformers.

  - Transformer that weighs more than 20 lb with the center of gravity located more than 4 ft above the adjacent floor level.

  - Transformer that weighs more than 400 lb.

- Uninterruptible power supplies

- Unit substations

- Variable frequency motor controllers:

  - All PC-4, PC-3, PC-2, and Ip = 1.5 variable frequency motor controllers.

  - Variable frequency motor controller that weighs more than 20 lb with the center of gravity located more than 4 ft above the adjacent floor level.

  - Variable frequency motor controller that weighs more than 400 lb.

- Wireways:

  - All PC-3 and PC-4 wireways.

  - Wireway that is rigidly attached to the structure.

  - Wireway that is supported by hangers, and any hanger in the wireway run that is longer than 12 inches.

  - Trapeze supported wireways with an aggregate weight of 10 lb/ft or more including conductors.

- Any component, essential or non-essential, where the failure of the component or its mounting could cause the failure of an essential architectural, mechanical, or electrical component.

All post-installed concrete and masonry anchors for use in non-structural applications must be chosen from qualified anchors in compliance with the IBC and ESM Chapter 16, IBC Program.

Components that are exempt from requirements for a designed anchor have hangers and supports that meet the requirements of Section 26 0529 – Hangers and Supports for Electrical Systems.

*************************************************************************************************************

# GENERAL

*************************************************************************************************************

The intent of this Section is to provide for adequate resistance to forces induced by earthquakes for electrical components and systems so as to preclude injury or impeded egress of personnel.

In addition, if required by IBC and other Project Record Documents, this Section is intended to ensure (1) operability of active electrical components and/or (2) containment of hazardous material in electrical components, following the design seismic event.

Verify that seismic protection details do not interfere with vibration isolation systems.

*************************************************************************************************************

## SECTION INCLUDES

    - Provide and install, hangers, supports, anchors, concrete bases, and other positive fastenings for electrical nonstructural components for which designed anchors are shown on the Drawings, such that in-service loads and seismic forces are safely transferred to the structure and relative seismic displacements of supporting structures are adequately accommodated.

    - Provide vibration isolation for electrical components as specified in this Section or indicated on the Drawings.

  - Non-Seismic Hangers and Supports

    - Follow Section 26 0529 – Hangers and Supports for Electrical Systems for hangers and supports for electrical components not identified on the Drawings as requiring vibration isolators or seismic designed anchors or braces.

QUALITY ASSURANCE

    - Furnish and install hangers and supports that conform to the requirements of the following codes and standards:

NFPA 70, National Electric Code (NEC)

IBC, International Building Code

ASCE 7, Minimum Design Loads for Buildings and Other Structures

NECA 1, Standard Practices for Good Workmanship in Electrical Contracting

Metal Framing Manufacturers Association

        - MFMA-4, Metal Framing Standards Publication

        - MFMA-102, Guidelines for the Use of Metal Framing

    - Where a Nationally Recognized Testing Laboratory (NRTL) has requirements for such products, provide products that are NRTL listed and labeled for the application, installation condition, and the environment in which installed.

*************************************************************************************************************

Edit the following article to match project requirements.

*************************************************************************************************************

ACTION/INFORMATIONAL SUBMITTALS

    - Catalog Data: Submit catalog data for each type of product specified.  Include information substantiating equivalent corrosion resistance to zinc coated steel of alternative treatment, finish, or inherent material characteristic.

    - Material List: Submit schedule showing manufacturer's figure number, size, spacing, features, and application for each required type of hanger, support, sleeve, seal, vibration isolator, and fastener to be used.

    - Test reports:

Pre-set Concrete Anchors: Submit either of the following:

        - ICC Evaluation Service, Inc (ICC-ES) evaluation report stating that the product is compliant with the current edition of the IBC and the intended conditions of use.

        - Drawing showing use as an approved component a in fixed equipment anchorage design that have been approved by an agency such as the State of California Office of Statewide Health Planning and Development.

Vibration Isolators: Submit either of the following:

        - ICC Evaluation Service, Inc (ICC-ES) evaluation report stating that the product is compliant with the current edition of the IBC and the intended conditions of use.

        - Drawing showing use as an approved component a in fixed equipment anchorage design that have been approved by an agency such as the State of California Office of Statewide Health Planning and Development.

*************************************************************************************************************

Edit the following article to match project conditions; add items to list as required; delete items not included in the Project.

*************************************************************************************************************

    - Shop Drawings: Submit shop drawings showing details of fabricated hangers, vibration isolators, supports, and seismic control of the electrical nonstructural components listed below.  Provide detail drawings along with catalog cuts, templates, and erection and installation details, as appropriate, for the components listed below. Submittals shall be complete in detail; shall indicate thickness, type, grade, class of metal, and dimensions; and shall show construction details, reinforcement, anchorage, and installation with relation to the building construction.

Battery racks and battery cabinets

Cable trays

Enclosed bus assemblies

Transformers

[___________]

*************************************************************************************************************

Edit the following article to match Project conditions; add items to list as required; delete items not included in the Project.  Delete the article if there are no electrical components that must maintain containment and /or active electrical components that must remain operable.

It may be necessary to note the equipment IDs for the particular items (e.g. SWGR-B, MCC-E) that must meet the requirements of this paragraph.

Seismic control does not guarantee that an electrical component is rugged enough to maintain containment, or that an active electrical component is rugged enough to remain operable, following the design seismic event.  When such additional capability is required, the component must be certified as being able to do so by the manufacturer / supplier in accordance with the design structural-engineer-of-record’s direction.

*************************************************************************************************************

    - Component Certifications: Submit certification from the manufacturer / supplier that the following items furnished under this Subcontract will be able to a) maintain containment of hazardous content, and / or b) remain operable following the design seismic event.  Certification shall be in accordance with the Project’s Statement of Special Inspections document.

Unit substation [SUS-A]

Transformers [XFMR-A, XFMR-3]

Switchgear [SWGR-B]

Switchboard [SWBD-E]

Panelboards [EP-A, EP-1]

Enclosed circuit breakers and safety switches [CBE-G, CDD-E]

Motor control center [MCC-D]

Variable frequency motor controllers [VFD-F, VFD-H]

Engine-generator [GDE-A]

Uninterruptible power supply [UPS-D]

[___________]

Receiving, Storing and Protecting

    - Receive, store, and protect, and handle products according to NECA 1.

# products

  - General

    - Refer to Section 13 4800, Sound, Vibration and Seismic Control for general seismic control products.

## Substitutions

    - Alternate products may be accepted; follow Section 01 2500, Substitution Procedures.

    - As is the case with all LANL projects, substitutions are permitted unless noted otherwise; however, “approved equal” seismically controlled nonstructural components must be reviewed and approved by the design structural-engineer-of-record.

COATINGS and Materials

    - Furnish products for use indoors that are protected with zinc coating or with treatment of equivalent corrosion resistance using approved alternative treatment, finish, or inherent material characteristic.

    - Furnish products for use outdoors or in damp or corrosive indoor locations with hot-dip galvanized coating or with treatment of equivalent corrosion resistance using approved alternative treatment, finish, or inherent material characteristic.

## Bolts

    - Furnish bolts, anchor rods, washers, and nuts as specified in Section 13 4800, Sound, Vibration and Seismic Control.

## Pre-set concrete inserts

    - Furnish pre-set concrete inserts as shown on the Drawings and specified below.

    - Permissible uses and allowable load capabilities of pre-set concrete inserts shall be documented in either of the following two ways:

      - Have an ICC-ES evaluation report stating that the product is compliant with the current edition of the IBC and the intended conditions of use.

      - Be shown as approved components in fixed equipment anchorage designs that have been approved by an agency such as the State of California Office of Statewide Health Planning and Development.

    - Manufacturers:

      - Continuous inserts for wood forms: B-Line “B22I-12” or longer.

      - Spot inserts for wood forms or metal decks: B-Line “B2500” with “N2500” nut, “B2501”

## POST-INSTALLED CONCRETE ANCHORS

    - Furnish post-installed expansion, adhesive, and undercut concrete and masonry anchors as shown on the Drawings and Section [05 0521, Post Installed Concrete Anchors – High Confidence] [and/or] [05 0520, Post Installed Concrete and Grouted-Masonry Anchors – Normal Confidence].

## Beam Clamps:

    - Furnish beam clamps that are NRTL-listed and compliant with Federal Specification WW-H-171E Type 23 or Manufacturers’ Standardization Society SP-69 and SP-58 Type 23.

    - Provide beam clamps with a locknut on the setscrew.

    - Provide NRTL-listed restraining strap for each beam clamp. Strap shall be not less than 16 gauge thickness, not less than 1 inch wide, and of sufficient length to wrap around the beam flange not less than 1 inch.

  - HANGER RODS

    - Furnish mild steel rods that conform to ASTM A 307, Standard Specification for Carbon Steel Bolts and Studs, 60 000 PSI Tensile Strength.

    - Furnish rods that are threaded on both ends, threaded on one end, or continuous threaded with UNC (coarse) thread pitch.

## sway bracing materialS

    - Furnish sway bracing materials (e.g. rods, plates, cable, angles) as shown on the Drawings and specified in Section 13 4800, Sound, Vibration and Seismic Control.

  - FRAMING CHANNEL SYSTEMS

    - Furnish U-channel framing systems that conform to MFMA-4 and are fabricated using minimum 12-gage steel, with 9/16 inch diameter holes, from 1-1/2 to 1-7/8 inches on center, in the surface opposite the “U” opening.

    - Furnish fittings and accessories that mate and match with U-channel and are of the same manufacturer. Use two-piece, single bolt type conduit straps on U-channel supports.

    - Manufacturers: Unistrut, B-Line, Superstrut.

*************************************************************************************************************

Delete the following article if not required by Project.

*************************************************************************************************************

## Reinforced Concrete

    - Refer to Section 03 3001, Reinforced Concrete.

    - Furnish housekeeping pad anchors to connect concrete bases to the structural floor.

      - Material: ductile iron.

      - Anchorage to concrete base: two #3 reinforcing bars

      - Anchorage to structural floor: post-installed stud-type anchor as specified in [Section 05 0520 Post Installed Concrete and Grouted-Masonry Anchors– Normal Confidence] [and/or] [Section 05 0521 Post Installed Concrete Anchors – High Confidence] [as applicable to the Management Level of the component.]

      - Manufacturer: Mason Industries “HPA”

*************************************************************************************************************

Edit the following article to match Project requirements. Electrical equipment (e.g. engine-generators, UPSs, and transformers) can generate substantial structure-borne noise that may be objectionable in noise-sensitive locations (e.g. offices, conference rooms, auditoriums, some laboratories). Noise-generating electrical equipment should be located as far as practicable from noise sensitive locations. In cases where structure-born noise must be mitigated, select vibration isolators in accordance with the manufacturer’s recommendations based on equipment weight and noise spectra. Verify seismic suitability of each vibration isolator with the design agency’s structural engineer of record. Provide a schedule of the selected vibration isolators for each equipment item on the Drawings including indicate vibration isolator model number, rating, and loaded deflection. Indicate locations of isolators on the Drawings.

Floor mounted elastomeric vibration isolator mountings are suitable for relatively light floor-mounted electrical equipment (e.g. dry-type transformers). Heavy floor-mounted equipment (e.g. engine-generators) will require floor mounted spring vibration isolator mountings. Suspended equipment (e.g. transformers) will need the combination spring / rubber vibration isolator hangers.

Refer to footnotes to Table 13.6-1 in ASCE 7 for changes to seismic design forces that may result from the use of seismically-restrained vibration isolators.

Delete the article if vibration isolation is not required.

*************************************************************************************************************

## Vibration Isolators

    - Furnish vibration isolators as described below and indicated on the Drawings.

    - Permissible uses and allowable load capabilities of vibration isolators shall be documented in either of the following two ways:

      - Have an ICC-ES evaluation report stating that the product is compliant with the current edition of the IBC and the intended conditions of use.

      - Be shown as approved components in fixed equipment anchorage designs that have been approved by an agency such as the State of California Office of Statewide Health Planning and Development.

    - Floor Mounted Elastomeric Vibration Isolator Mountings:

Furnish captive elastomeric mounting molded from neoprene or EPDM compound meeting the requirements of ASTM D200. Load bearing elastomer mount shall be housed in steel or cast ductile iron housing.

Mounting shall incorporate a fail-safe captive design, and shall be capable of providing vertical compression dynamic deflections from approximately 0.15 inches to 0.3 inches at rated capacity.

Manufacturer: Mason Industries, Inc. “RBA”, “RCA”, “RDA”, “BR”

    - Floor Mounted Spring Vibration Isolator Mountings:

Furnish seismic steel spring isolator mountings that have elastomeric snubbing in all directions.

Springs shall be color coded using polyester epoxy powder coat to indicate rated load capacity. Spring diameter shall be not less than 0.8 times the compressed height of the spring at rated load. Springs shall have a minimum additional travel to solid not less than 50 percent of the rated deflection.

Snubber shall be adjustable in the vertical direction to allow a maximum of 0.25 inch travel before contacting the elastomer cushion.

Housing shall be cast ductile iron, malleable cast iron, or welded steel construction; grey iron castings are not acceptable. Housings shall include provision to adjust the rebound plate and to inspect the spring(s).

Hardware shall be stainless steel or zinc coated.

Manufacturer: Mason Industries, Inc. “SLR”, “SLREBP”, “SLRS”, “SLRSEBP”, “SSLFH”

    - Combination Spring / Rubber Vibration Isolator Hangers:

Furnish combination spring / rubber vibration isolator hangers consisting of a steel compression spring in series with compression elastomer elements with elastomeric snubbing in all directions.

Springs shall be color coded to indicate rated load capacity and shall have a minimum additional travel to solid not less than 50 percent of the rated deflection.

Snubber shall be adjustable in the vertical direction to allow a maximum of 0.25 inch travel before contacting the elastomer cushion.

Manufacturer: Mason Industries, Inc. “PC30N”

# EXECUTION

  - GENERAL

*************************************************************************************************************

Locate each item of electrical equipment entirely on one side only of a building expansion joint.

Electrical conduits larger than 2-1/2” trade size, cable trays, wireways, busways, etc. which cross an expansion joint or connect to rigid electrical equipment, shall have flexible joints that are capable of accommodating calculated thermal and seismic displacements.

*************************************************************************************************************

    - Refer to Section 13 4800, Sound, Vibration and Seismic Control for general seismic protection installation requirements.

    - Install hangers, supports, vibration isolation, and seismic control according to the Drawings, the requirements in this Section, and the requirements of the applicable codes. Where overlap exists, the more stringent of the requirements will govern.

    - Conform to manufacturer's instructions and recommendations for installation of hangers, supports, anchors, seismic controls, and vibration isolators.

    - Do not use wire or perforated strap for permanent electrical supports.

    - Anchor each item of electrical equipment as shown on the Drawings.

    - Refer to Section 26 5100, Interior Lighting for installation requirements for interior luminaires.

    - Refer to Section 26 5200, Emergency Lighting for installation requirements for emergency luminaires and exit signs.

## EXAMINATION

    - Examine surfaces to receive hangers, supports, and seismic control for compliance with installation tolerances and other conditions affecting performance of the system.  Do not proceed with installation until unsatisfactory conditions have been corrected.

## Seismic Relative Displacements

*************************************************************************************************************

Using LANL ESM Ch. 5, and the applicable codes / standards referred to therein, the design agency shall determine the expected seismic relative displacements and drift ratios.

For the purpose of seismic relative displacements and drift ratios, conduits 2-1/2” trade size and smaller connected to panelboards, cabinets, and similar equipment are considered to be “flexible.”

Joints for vertical electrical distribution systems (e.g. conduits, cable trays, busways) between floors of the building, where electrical distribution systems pass through a building seismic or expansion joint, or where rigidly supported electrical distribution systems connect to equipment with vibration isolators must be capable of accommodating the required relative displacements.

Horizontal electrical distribution systems across expansion joints must be capable of accommodating the resultant of the drifts of each building portion in each orthogonal direction.

Edit the following articles to match Project requirements. Insert the required flexibility (e.g., inches of relative displacement) in the blank space.

*************************************************************************************************************

    - Furnish and install flexible joints, fittings, or hangers capable of accommodating [____] inches of seismic relative displacement for vertical conduits larger than 2-1/2” trade size, cable trays, busways, etc. attached at different levels or stories of the building.

    - Furnish and install flexible joints, fittings, or hangers capable of accommodating [____] inches of seismic relative displacement for horizontal conduits larger than 2-1/2” trade size, cable trays, busways, etc. attached on either side of a building seismic or expansion joint.

    - Furnish and install flexible joints, fittings, or hangers capable of accommodating [____] inches of seismic relative displacement for horizontal conduits larger than 2-1/2” trade size, cable trays, busways, etc. attached to separate structures.

## Sleeves and seals

*************************************************************************************************************

The design agency shall determine the amount of differential movement of electrical distribution systems at sleeves passing through walls and partitions and will indicate on the drawings the amount of clearance required between the pipe and the sleeve based on deflection of the electrical distribution systems between sway braces on either side of the wall.

The design agency should avoid penetrations through fire-rated assemblies.

Edit the following article to match Project requirements.

*************************************************************************************************************

    - Furnish and install and install sleeves in concrete slabs and walls and all other fire- rated floors and walls for installation of conduits, cable trays, wireways, busways, etc.

    - Furnish and install sleeves through fire-rated walls or floor construction that conform to the requirements in Section 07 8400, Firestopping.  Follow manufacturer's instructions to restore original fire rating of wall or slab.

    - Size sleeves in interior non-fire-rated walls as indicated on the Drawings or as required to provide clearances that will permit differential movement of conduits, cable trays, wireways, busways, etc. without the items striking the pipe sleeve.

*************************************************************************************************************

Edit the following article to match Project requirements.

*************************************************************************************************************

    - Furnish seals for electrical conduit penetrations of slabs on grade and exterior walls below grade and where indicated.  Tighten sleeve seal screws until sealing grommets have expanded to form watertight seal.

    - Request inspection of firestop installations through the LANL Subcontract Technical Representative (STR) both before and after installation of firestop materials.

## Spreaders

*************************************************************************************************************

Spreaders are required between adjacent runs of conduits, cable trays, wireways, busways, fire sprinkler pipes, plumbing pipes, etc. to prevent contact during seismic activity whenever the force and displacement provisions of LANL ESM Ch. 5 indicate that such contact could result in damage to critical distribution systems.

Spreaders shall be designed such that they occur at same interval as sway braces and at an equal distance between the sway braces.

If rack type hangers are used where the components are restrained from contact by mounting to the rack, spreaders are not required for conduits, cable trays, wireways, busways, etc. mounted in the rack.

*************************************************************************************************************

    - Install spreaders between adjacent runs of conduits, cable trays, wireways, busways, fire sprinkler pipes, plumbing pipes, etc. as shown on the Drawings.

## sway braces

*************************************************************************************************************

Sway braces are required to prevent uncontrolled movement of conduits, cable trays, wireways, busways, etc. under seismic loading.

Design of sway braces for conduit, cable tray, wireway, or busway run shall be such that attachment to two dissimilar structural elements of a building that may respond differentially during an earthquake does not result, unless a flexible joint is part of the design.  Refer to the SEISMIC RELATIVE DISPLACEMENTS paragraph.

Braces are required in both the longitudinal and transverse directions, relative to the axis of the conduit, cable tray, wireway, busway, etc.

*************************************************************************************************************

    - Transverse Sway Bracing

*************************************************************************************************************

The bracing layout must be supported by design calculations and shown on the drawings.

All runs (length of conduit, cable tray, wireway, busway, etc. between end joints) shall have a minimum of two transverse braces.

*************************************************************************************************************

Install transverse sway bracing for conduits, cable trays, wireways, busways, etc as shown on the Drawings.

    - Longitudinal Sway Bracing

*************************************************************************************************************

The bracing layout must be supported by design calculations and shown on the drawings.

All runs shall have one longitudinal brace minimum.

Branch lines, walls, or floors shall not be used as sway braces.

*************************************************************************************************************

Install longitudinal sway bracing for conduits, cable trays, wireways, busways, etc. as shown on the Drawings.

    - Vertical Runs

*************************************************************************************************************

The bracing layout must be supported by design calculations and shown on the drawings, and must be such that bracing occurs above the center of gravity of the segment being braced.

All runs shall have one longitudinal brace minimum.

Branch lines, walls, or floors shall not be used as sway braces.

*************************************************************************************************************

Run is defined as length of conduit, cable tray, wireway, busway, etc. between end joints.

Install sway bracing for vertical runs of conduit, cable tray, wireway, busway, etc. as shown on the Drawings.

    - Anchor Rods, Angles and Bars

Bolt anchor rods, angles, and bars to either electrical component clamps hangers at one end and to cast-in-place concrete or masonry insert, or clip angles bolted to the steel structure, on the other end.

Furnish bolts for attachment of anchors as shown.

Rods shall be solid metal or pipe.

*************************************************************************************************************

Edit the following article to match project conditions; delete if there is no floor-mounted electrical equipment.  Concrete bases must be designed by the Engineer of Record based on the properties of the load to be supported, the properties of the supporting structure, required anchor bolt embedment lengths, etc. Construction details and dimensions for concrete bases must be shown on the Drawings.

*************************************************************************************************************

## CONCRETE BASES

    - Install a reinforced concrete base for each item of floor- mounted electrical equipment.

Construct bases as dimensioned and detailed on the Drawings.

Make bases not less than 5 inches thick.

Make bases level to within 1/8 inch per 3-foot distance in any direction.

    - Anchor each concrete base to the structural floor.

Install housekeeping pad anchors in accordance with the manufacturer’s instructions.

Attach housekeeping pad anchors to the structural floor using post installed concrete anchors as shown on the Drawings.

Attach housekeeping pad anchors to the concrete base reinforcing steel using two #3 reinforcing bars per anchor.

*************************************************************************************************************

Edit the following article to match project conditions; delete if not required. Use concrete bases with a permanent steel perimeter for heavy equipment such as unit substations, transformers 300 kVA and larger, engine generators, etc. Edit references to concrete work to match sections used in Division 3 of the Project Specifications.

*************************************************************************************************************

    - Support each [unit substation] [engine generator] [rotary UPS] [transformers 300 kVA and larger] [     ] on a reinforced concrete equipment base with a permanent steel perimeter frame.

Form base using ASTM A-36 steel channels.

Construct base not less than 4 inches larger in both directions than supported equipment. Miter and weld corners and provide cross bracing.

Install reinforcing as shown on the Drawings. Refer to Section 03 3001, Reinforced Concrete.

Place pre-set anchors, conduits, and sleeves using the equipment manufacturer's installation template or instructions. Install post-installed anchors in accordance with Post-Installed Concrete Anchors article below.

Place concrete and provide a level, steel trowel finish on top.  Refer to Section 03 3001, Reinforced Concrete.

Clean exposed steel frames and apply 2 coats of rust preventative metal primer and 2 coats of gray exterior, gloss, alkyd enamel.

*************************************************************************************************************

Edit the following article to match project conditions; delete if not required. Use concrete bases without a permanent steel perimeter for relatively light floor–mounted equipment such as transformers smaller than 300 kVA, motor control centers, switchboards, etc. Edit references to concrete work to match sections used in Division 3 of the Project Specifications.

*************************************************************************************************************

    - Support each [switchboard] [power panelboard] [motor control center] [transformers smaller than 300 kVA] [    ] on a formed concrete equipment base.

Form concrete equipment bases using framing lumber with form release compounds. Refer to Section 03 3001, Reinforced Concrete.

Construct concrete base not less than 4 inches larger in both directions than supported unit.

Install reinforcing as shown on the Drawings. Refer to Section 03 3001, Reinforced Concrete.

Place pre-set anchors, conduits, and sleeves using the equipment manufacturer's installation template or instructions. Install post-installed anchors in accordance with Post-Installed Concrete Anchors article below.

Place concrete and provide a level, steel trowel finish on top; chamfer top edges and corners. Refer to Section 03 3001, Reinforced Concrete.

    - Cure concrete not less than seven days before installing equipment.

*************************************************************************************************************

Edit the following article to match project conditions; delete if pre-set concrete inserts are not required.

*************************************************************************************************************

## Pre-set concrete inserts

    - Install pre-set concrete inserts as shown on the Drawings and in accordance with the manufacturer’s instructions.

    - Schedule and coordinate placement of pre-set concrete inserts with the work of other trades.

## Post-Installed Concrete Anchors

    - Install post-installed concrete and masonry anchors as shown on the Drawings and in accordance with [05 0521, Post Installed Concrete Anchors – High Confidence] [and/or] [05 0520, Post Installed Concrete and Grouted-Masonry Anchors –Normal Confidence].  Test as specified therein.

## FASTENING

    - Refer to Section 13 4800, Sound, Vibration and Seismic Control.

    - Use beam clamps for fastening to structural metal beams, joists, and purlins.

      - Install a restraining strap at each beam clamp. Wrap the restraining strap around the beam flange not less than 1 inch. Where purlins or beams do not provide a secure lip for the restraining strap, secure the strap with a self-tapping screw or by through-bolting.

      - Use a locknut on each beam clamp set screw.

    - Use self-tapping screws or machine bolts, nuts, and washers for fastening to metal studs or metal surfaces.

    - Torque threaded fasteners as recommended by the manufacturer’s instructions.

*************************************************************************************************************

Delete the following article if not required by Project.

*************************************************************************************************************

  - Framing Channel Systems

    - Install framing channel systems as detailed on the Drawings and in accordance with MFMA-103.

## Vibration Isolation

    - Install and adjust vibration isolators as indicated on the Drawings in accordance with the manufacturer’s installation instructions.

    - Make flexible electrical connections to equipment supported by vibration isolators.

  - HANGER RODS

*************************************************************************************************************

Coordinate the following article with the Drawings.  Delete if there is no suspended equipment.

*************************************************************************************************************

    - Use minimum 3/8-inch diameter threaded rod; use larger diameter rod as indicated on the Drawings, in other Sections, or in the supported equipment manufacturer’s installation instructions.

    - Install a locknut at every hanger rod connection.

  - PAINTING

*************************************************************************************************************

Coordinate the following article with the Drawings; delete if there is no requirement for painting. Coordinate painting with project architect.

*************************************************************************************************************

    - Paint exposed hangers and supports to match finish of adjacent surfaces.

    - Refer to Section 09 9100, Painting for materials and installation requirements.

END OF SECTION

*************************************************************************************************************

Do not delete the following reference information.

*************************************************************************************************************

FOR LANL USE ONLY

This project specification is based on LANL Master Specification 26 0548 Rev. 3, dated November 06, 2014.