SECTION 26 0700

INDUCTION Motors – 500hp and smaller

*******************************************************************************************************

LANL MASTER SPECIFICATION

Available online at http://engstandards.lanl.gov

This template must be edited for each project.  In doing so, specifier must add job-specific requirements.  Brackets are used in the text to indicate designer choices or locations where text must be supplied by the designer.  Once the choice is made or text supplied, remove the brackets.  The specifications must also be edited to delete specification requirements for processes, items, or designs that are not included in the project -- and specifier’s notes such as these.  To seek a variance from requirements in the specifications that are applicable, contact the Engineering Standards Manual Electrical POC.  Please contact POC with suggestions for improvement as well.

When assembling a specification package, include applicable specifications from all Divisions, especially Division 1, General requirements.

Specification developed for ML-4 projects.  For ML-1, 2, and 3 applications, additional requirements and independent reviews should be added if increased confidence in procurement or execution is desired; see ESM Chapter 1 Section Z10 Specifications and Quality Sections.
*******************************************************************************************************

GENERAL

Section Includes

Section includes single- and three-phase induction motors rated 500 horsepower and smaller and 600 volts and less for application on equipment provided under other sections and motors furnished loose to Project.

Section does not address motors intended for used in hazardous locations as defined in the National Electrical Code.

Section does not address sealed (hermetic type) motor-compressor parts.

Section does not address special-purpose motors such as submersible pump motors.

Quality Assurance

Comply with the National Electrical Code (NEC) for components and installation.

Motors shall be listed and labeled by a Nationally Recognized Testing Laboratory (NRTL) to the following standards as applicable to the intended use, installation condition, and the environment in which installed:

UL 1004-1, Standard for Rotating Electrical Machines - General Requirements

UL 1004-2, Standard for Impedance Protected Motors

UL 1004-3, Standard for Thermally Protected Motors

UL 1004-5, Standard for Fire Pump Motors

UL 1004-8, Standard for Inverter Duty Motors

SUBMITTALS

Submit the following in accordance with project submittal procedures:

Catalog Data: Submit catalog data for each motor furnished loose. Indicate nameplate data, standard compliance, electrical ratings and characteristics, and physical dimensions, weights, mechanical performance data, and support points.

Calculations: Motor selection calculations including brake horsepower of the load, ambient temperature range at the motor location, and characteristics of moving air stream (if any) at the motor location.

*************************************************************************************************************

Edit the following article to match project requirements; delete if no motor on the Project is designated with a “component importance factor” (Ip) greater than 1.0.

*************************************************************************************************************

Certification: Submit certification and backup information that motors can perform required functions after a design earthquake as specified in "SERVICE CONDITIONS" below.

        - Motors designated with a component importance factor (Ip) greater than 1.0 shall be certified by the manufacturer to withstand the total lateral seismic force and seismic relative displacements specified in the International Building Code (IBC) or ASCE 7 – Minimum Design Loads for Buildings and Other Structures.

        - Manufacturer’s certification shall be based on shake table testing or experience data (i.e., historical data demonstrating acceptable seismic performance), or by more rigorous analysis providing for equivalent safety.

        - Required response spectra shall exceed 1.1 times the in-structure spectra determined in accordance with IBC AC156 – Acceptance Criteria for Seismic Qualification by Shake-Table Testing of Nonstructural Components and Systems.

Certification: Submit certification that motors meet specified performance, efficiency, and selection requirements.

Test Reports: Indicate procedures and results for specified factory testing.

Installation instructions including handling, storage, setting, mechanical connections, lubrication, wiring, and testing.

Operation and maintenance data:

        - Operation data including instructions for safe operating procedures.

        - Maintenance data including assembly drawings, bearing data with replacement sizes, and lubrication instructions.

SERVICE CONDITIONS

    - Motors shall perform satisfactorily in the following service conditions:

      - Elevation: 7500 feet above sea level.

      - Maximum ambient temperature: 104 degrees F.

      - Minimum ambient temperature: -20 degrees F.

      - 24-hour average temperature: not exceeding 86 degrees F.

      - Site-specific International Building Code seismic criteria:

        - Seismic Design Category = D

        - SDS = spectral acceleration, short period = 0.75g

        - SD1 = spectral acceleration, 1-second period = 0.64g

        - ap = component amplification factor = 1.0

        - Rp = component response modification factor = 2.5

*****************************************************************************************************

Edit the following article to match project requirements; indicate the applicable importance factor. If more than one applies, indicate specific motors that have an importance factor greater than 1.0.

*****************************************************************************************************

        - Ip = Component importance factor
Ip = 1.5 for life safety related components such as emergency system motors
Ip = 1.5 for safety class or safety significant system motors.
Ip = 1.0 for all other motor applications

*****************************************************************************************************

Edit the following article to match project requirements; use only for outdoor equipment.

*****************************************************************************************************

      - Maximum solar heat gain: 110 W/sq ft.

Receiving, Storing and Protecting

Receive, store, and protect, and handle products according to NECA 1—Standard Practices for Good Workmanship in Electrical Construction (ANSI), and NECA 230—Standard for Selecting, Installing, and Maintaining Electric Motors and Motor Controllers (ANSI).

Upon delivery of motors to site, inspect thoroughly for damage.

Store, protect and handle motors following manufacturer’s instructions.  Provide slings and spreader bars as required.  Lift only with lugs provided. Do not lift motors using shaft as an attachment point.

Protect products from weather and moisture by covering with plastic or canvas and by maintaining heating within enclosure.

For extended outdoor storage, remove motors from equipment and store separately.

project Record Documents

Submit the following in accordance with Section 01 7839, Project Record Documents:

Report of field tests showing compliance with and field quality control specified in Part 3 of this specification section.

********************************************************************************************************

Edit the following article to match project requirements; delete if not needed.  See instructions for MANUFACTURER’S START-UP SERVICE article of this Section.

********************************************************************************************************

Start-up report from motor manufacturer’s start-up service to certify that motors have been installed, adjusted, and tested in accordance with manufacturer’s recommendations.

PRODUCTS

  - PRODUCT OPTIONS AND SUBSTITUTIONS

Alternate products may be accepted, follow Section 01 2500, Substitution Procedures.

  - MANUFACTURERS

Baldor

Emerson Motors

GE Motors

Siemens

TECO-Westinghouse

  - GENERAL CONSTRUCTION AND REQUIREMENTS

Motors less than 250 watts for general applications may be equipment manufacturer's standard product and need not conform to these specifications.

Provide NRTL-listed motors with electrical and mechanical performance in accordance with NEMA MG-1, Motors and Generators, unless specified otherwise in this Section.

********************************************************************************************************

Edit the following article to match project requirements.

********************************************************************************************************

Electrical Service:

3/4 horsepower and smaller: single phase, 60 Hz motors, voltage as indicated on the Drawings.

Greater than 3/4 horsepower: 3-phase, 60 Hz motors, voltage as indicated on the Drawings.

********************************************************************************************************

Edit the following article to match project requirements.

********************************************************************************************************

Enclosure

For clean, dry, indoor locations furnish open drip-proof type motors.

For unfiltered air stream locations in manufacturer assembled equipment furnish either totally enclosed non-ventilated (TENV) or totally enclosed fan-cooled (TEFC) type motors.

For [exterior locations] [damp locations] [air cooled condensers] [direct drive axial fans] [roll filters] [dust collection systems] [unfiltered air streams] [________] furnish totally enclosed fan-cooled (TEFC) type motors.

For [outdoor locations] [wash down locations] [wet air streams downstream of sprayed coil dehumidifiers] [draw thru cooling towers] [humidifiers] [corrosive] [________] furnish totally enclosed fan-cooled (TEFC) severe duty type motors that conform to IEEE Std 841 - IEEE Standard for Petroleum and Chemical Industry-Premium-Efficiency, Severe-Duty, Totally Enclosed Fan-Cooled (TEFC) Squirrel Cage Induction Motors-Up to and Including 370 kW (500 hp).

Provide 120 volt space heaters in motors as indicated on the Drawings.

Rating

Motors shall be rated on a continuous-duty basis.  The output rating shall be available at the shaft at the specified speed, frequency and voltage.

De-rate motors for operation at 7500 feet altitude in accordance with NEMA MG-1.  Do not use motor service factor to compensate for altitude.  Refer to motor selection table below.

Nameplates:

Each motor shall have a stainless steel nameplate indicating information required by the NEC and NEMA MG-1.

Additional nameplate information may be required by other articles in this Section.

Attach nameplates to motor frame with stainless steel fasteners.

Wiring Terminations:

Terminal lugs shall match branch circuit conductor quantities, sizes, and materials indicated.  Enclose terminal lugs in a terminal box sized to the NEC, and threaded for conduit.

For fractional horsepower motors where connection is made directly, provide conduit connection in end frame.

There shall be a frame grounding screw or lug inside terminal cover or terminal box.

Motors shall meet NEMA MG-1 noise level standards.

  - SINGLE PHASE POWER - SPLIT PHASE MOTORS

Use single-phase power, split phase motors for applications less than 1/4 brake horsepower.

Split phase motors shall have the following characteristics:

Starting Torque: Less than 150 percent of full load torque.

Starting Current: Up to 7 times full load current.

Breakdown Torque: Approximately 200 percent of full load torque.

Insulation: Class A (50 degrees C temperature rise) or better.

Service Factor: Minimum of 1.35 for drip-proof motors and 1.0 for enclosed motors.

Bearings: Pre-lubricated ball bearings.

  - SINGLE PHASE POWER - PERMANENT-SPLIT CAPACITOR MOTORS

Use single-phase power, permanent split capacitor motors for shaft mounted fans or blowers 3/4 brake horsepower and smaller.

Permanent split capacitor motors shall have the following characteristics:

Starting Torque: Exceeding 1/4 of full load torque.

Starting Current: Up to 6 times full load current.

Multiple Speed: Through tapped windings.

Insulation: Class A (50 degrees C temperature rise) or better.

Service Factor: 1.0

Bearings: Pre-lubricated ball or sleeve bearings.

Integral Protection: Automatic reset overload protector.

  - SINGLE PHASE POWER - CAPACITOR START MOTORS

Use single-phase power, capacitor start motors for applications 1/4 brake horsepower through 3/4 brake horsepower.

Capacitor start motors shall have the following characteristics:

Starting Torque: 3 times full load torque.

Starting Current: Less than 5 times full load current.

Pull-up Torque: Up to 350 percent of full load torque.

Breakdown Torque: Approximately 250 percent of full load torque.

Motors: Capacitor in series with starting winding. Provide capacitor-start / capacitor-run motors with 2 capacitors in parallel with run capacitor remaining in circuit at operating speeds.

Insulation: Class A (50 degrees C temperature rise) or better.

Service Factor: Minimum of 1.25 for drip-proof motors and 1.0 for enclosed motors.

Bearings: Pre-lubricated ball bearings.

  - THREE PHASE POWER - SQUIRREL CAGE MOTORS

Use 3-phase power, squirrel cage induction motors for applications more than 3/4 brake horsepower

********************************************************************************************************

Edit the following article to match project requirements. NEMA design B motors will be used for most centrifugal fan and centrifugal pump applications. Special applications such as positive displacement pumps may require motors with higher starting torque than NEMA Design B.

********************************************************************************************************

3-phase power, squirrel cage motors shall have the following characteristics:

Starting Torque:  NEMA Design B characteristics.

Locked Rotor Current: NEMA Design B characteristics.

Power Output, Locked Rotor Torque, Breakdown or Pull-Out Torque: NEMA Design B characteristics.

Design, Construction, Testing, and Performance: Conform to NEMA MG 1 for Design B motors.

Insulation System: NEMA Class F or better.

Service Factor: 1.15 minimum.

Test motors in accordance with NEMA MG-1-12 and IEEE 112, IEEE Standard Test Procedure for Polyphase Induction Motors and Generators.  Each motor shall receive a routine commercial test to verify freedom from electrical or mechanical defects.  Provide prototype test reports for each rating.

Motors shall be NEMA Standard T-Frames of steel, aluminum, or cast iron with end brackets of cast iron or aluminum with steel inserts.

Motors shall have  grease lubricated anti-friction ball bearings, with housings equipped with provision for re-lubrication,

The bearings shall have a rated L-10 fatigue life per ANSI/ABMA 9 - Load Ratings and Fatigue Life for Ball Bearings of 150,000 hours for direct-coupled applications and 50,000 hours for belted applications minimum. Belted rating shall be based on radial loads and pulley sizes called out in NEMA MG1. The calculation will be determined from the pulley centerline being at the end of the motor shaft.

Bearing cavities and greasing passages shall be thoroughly cleaned of all debris before lubricating. Motors shall be lubricated at the factory with Exxon Mobil Polyrex™ EM grease, or equal.

Stamp ANSI/ABMA bearing identification number on motor nameplate.

For belted applications, provide an adjustable sliding base; for applications above 10 horsepower, sliding base shall have 2 adjusting bolts.

General purpose, single-speed motors shall be NEMA PremiumTM labeled motors or motors with full-load nominal efficiency not less than that tabulated below when tested in accordance with IEEE Std. 112, sub clause 6.4, Method B.

| NOMINAL FULL-LOAD EFFICIENCY |
| --- |
| MOTOR HP | NUMBER OF POLES / SYNCHRONOUS SPEED, RPM |
|  | ODP MOTORS | TEFC MOTORS |
|  | 2 3600 | 4 1800 | 6 1200 | 2 3600 | 4 1800 | 6 1200 |
| 1 | 77.0 | 85.5 | 82.5 | 77.0 | 85.5 | 82.5 |
| 1.5 | 84.0 | 86.5 | 86.5 | 84.0 | 86.5 | 87.5 |
| 2 | 85.5 | 86.5 | 87.5 | 85.5 | 86.5 | 88.5 |
| 3 | 85.5 | 89.5 | 88.5 | 86.5 | 89.5 | 89.5 |
| 5 | 86.5 | 89.5 | 89.5 | 88.5 | 89.5 | 89.5 |
| 7.5 | 88.5 | 91.0 | 90.2 | 89.5 | 91.7 | 91.0 |
| 10 | 89.5 | 91.7 | 91.7 | 90.2 | 91.7 | 91.0 |
| 15 | 90.2 | 93.0 | 91.7 | 91.0 | 92.4 | 91.7 |
| 20 | 91.0 | 93.0 | 92.4 | 91.0 | 93.0 | 91.7 |
| 25 | 91.7 | 93.6 | 93.0 | 91.7 | 93.6 | 93.0 |
| 30 | 91.7 | 94.1 | 93.6 | 91.7 | 93.6 | 93.0 |
| 40 | 92.4 | 94.1 | 94.1 | 92.4 | 94.1 | 94.1 |
| 50 | 93.0 | 94.5 | 94.1 | 93.0 | 94.5 | 94.1 |
| 60 | 93.6 | 95.0 | 94.5 | 93.6 | 95.0 | 94.5 |
| 75 | 93.6 | 95.0 | 94.5 | 93.6 | 95.4 | 94.5 |
| 100 | 93.6 | 95.4 | 95.0 | 94.1 | 95.4 | 95.0 |
| 125 | 94.1 | 95.4 | 95.0 | 95.0 | 95.4 | 95.0 |
| 150 | 94.1 | 95.8 | 95.4 | 95.0 | 95.8 | 95.8 |
| 200 | 95.0 | 95.8 | 95.4 | 95.4 | 96.2 | 95.8 |
| 250 | 95.0 | 95.8 | 95.4 | 95.8 | 96.2 | 95.8 |
| 300 | 95.4 | 95.8 | 95.4 | 95.8 | 96.2 | 95.8 |
| 350 | 95.4 | 95.8 | 95.4 | 95.8 | 96.2 | 95.8 |
| 400 | 95.8 | 95.8 | 95.8 | 95.8 | 96.2 | 95.8 |
| 450 | 95.8 | 96.2 | 96.2 | 95.8 | 96.2 | 95.8 |
| 500 | 95.8 | 96.2 | 96.2 | 95.8 | 96.2 | 95.8 |

Do not select motors to operate continuously above rated load in the service factor area.

De-rate motors for operation at 7500 ft. altitude in accordance with the following table, taking into consideration the ambient temperature of the motor environment. Select motor based on 104 degrees F ambient temperature unless motor is in a moving air stream when operating.

| MAXIMUM MOTOR SHAFT LOADe (bhp) |
| --- |
| Motor Nameplate (hp) | Ambient Temperaturea, b, c (deg F) |
|  | 81.1 | 85 | 90 | 95 | 100 | 104d |
| 1 | 1.00 | 0.98 | 0.95 | 0.92 | 0.89 | 0.87 |
| 1.5 | 1.50 | 1.47 | 1.43 | 1.38 | 1.34 | 1.31 |
| 2 | 2.00 | 1.96 | 1.90 | 1.85 | 1.79 | 1.75 |
| 3 | 3.00 | 2.93 | 2.85 | 2.77 | 2.68 | 2.62 |
| 5 | 5.00 | 4.89 | 4.75 | 4.61 | 4.47 | 4.36 |
| 7.5 | 7.50 | 7.34 | 7.13 | 6.92 | 6.71 | 6.55 |
| 10 | 10.0 | 9.78 | 9.51 | 9.23 | 8.95 | 8.73 |
| 15 | 15.0 | 14.7 | 14.3 | 13.8 | 13.4 | 13.1 |
| 20 | 20.0 | 19.6 | 19.0 | 18.5 | 17.9 | 17.5 |
| 25 | 25.0 | 24.5 | 23.8 | 23.1 | 22.4 | 21.8 |
| 30 | 30.0 | 29.3 | 28.5 | 27.7 | 26.8 | 26.2 |
| 40 | 40.0 | 39.1 | 38.0 | 36.9 | 35.8 | 34.9 |
| 50 | 50.0 | 48.9 | 47.5 | 46.1 | 44.7 | 43.6 |
| 60 | 60.0 | 58.7 | 57.0 | 55.4 | 53.7 | 52.4 |
| 75 | 75.0 | 73.4 | 71.3 | 69.2 | 67.1 | 65.5 |
| 100 | 100 | 97.8 | 95.1 | 92.3 | 89.5 | 87.3 |
| 125 | 125 | 122 | 119 | 115 | 112 | 109 |
| 150 | 150 | 147 | 143 | 138 | 134 | 131 |
| 200 | 200 | 196 | 190 | 185 | 179 | 175 |
| 250 | 250 | 245 | 238 | 231 | 224 | 218 |
| 300 | 300 | 293 | 285 | 277 | 268 | 262 |
| 350 | 350 | 342 | 333 | 323 | 313 | 305 |
| 400 | 400 | 391 | 380 | 369 | 358 | 349 |
| 450 | 450 | 440 | 428 | 415 | 403 | 393 |
| 500 | 500 | 489 | 475 | 461 | 447 | 436 |
| Notes: |  |  |  |  |  |  |
| a. | Select motor based on 104 degrees F ambient temperature unless motor is in a moving air stream when operating. |
| b. | Document selection of an ambient temperature lower than 90 degrees F. |
| c. | Do not extrapolate to ambient temperatures below 81.1 or above 104 degrees F. If the ambient temperature is outside the 81.1 °F to 104 °F range, refer to NEMA MG 1 and/or the motor manufacturer for guidance. |
| d. | If ambient temperature exceeds 104 degrees F, select motor with greater nameplate hp rating in accordance with NEMA MG 1. |
| e. | Motor selection criteria developed from temperature rise considerations in NEMA MG 1-2003, clauses 12.43, 12.51, and 14.4. |

********************************************************************************************************

Edit the following article to match project requirements. Coordinate with equipment schedules on the Drawings. Delete if no motors are controlled by part-winding starters.

********************************************************************************************************

Where indicated on Drawings, provide motors suitable for use with part winding starting systems to reduce locked rotor current to approximately 60 percent of full winding locked rotor current while providing approximately 50 percent of full winding locked rotor torque.

********************************************************************************************************

Edit the following article to match project requirements. Coordinate with equipment schedules on the Drawings. Delete if there are no 2-speed motors.

********************************************************************************************************

Where indicated on Drawings, provide motors suitable for use in a single winding, variable torque connection for 2 speed fan and centrifugal pump applications.

********************************************************************************************************

Edit the following article to match project requirements. Coordinate with equipment schedules on the Drawings. Delete if no motors are on adjustable frequency controllers.

********************************************************************************************************

Where indicated on Drawings, provide motors suitable for use with adjustable frequency controllers as follows:

Provide motors that comply with Part 31 of NEMA MG-1 for use with pulse width modulation (PWM) adjustable frequency AC controllers.

Provide motors that comply with Part 30 or 31 of NEMA MG-1 for use with six step adjustable frequency controllers.

********************************************************************************************************

Edit the following article to match project requirements. Coordinate with equipment schedules on the Drawings. Delete if not used. Only large or critical motors warrant winding thermistors.

********************************************************************************************************

For motor Frame Sizes 254T and larger provide three positive thermal coefficient (PTC) thermistors imbedded in motor windings and epoxy encapsulated solid state control relay for wiring into motor starter.

EXECUTION

  - EXISTING WORK

********************************************************************************************************

Delete this article when existing construction is not affected.

********************************************************************************************************

Disconnect and remove abandoned motors

Maintain access to existing motors and other installations remaining active and requiring access. Modify installation or provide access panel.

Clean and repair existing motors to remain or are to be reinstalled.

EXAMINATION

Examine surfaces to receive motors for compliance with installation tolerances and other conditions affecting performance of the control system.  Do not proceed with installation until unsatisfactory conditions have been corrected.

  - INSTALLATION

Install motors and accessories in accordance with manufacturer's instructions and NECA 230; have manufacturer’s installation instructions available at the construction site.

Remove any slushing compound on shaft or other parts using a petroleum-type solvent.

Remove shaft shipping braces after motor is placed in its final location.

Install motor securely on firm, level foundation; refer to Section 26 0548, Vibration and Seismic Controls for Electrical Systems.

Install shaft coupling or sheave in accordance with manufacturers instructions.  Do not modify motor shaft to accommodate coupling or sheave.

Align the motor shaft with the load shaft. Meet the most stringent of the motor manufacturer’s requirements for shaft alignment, the driven equipment manufacturer’s requirements for shaft alignment, or the following requirements for shaft alignment. The minimum acceptable criteria for motor installation and shaft alignment for motors 10 horsepower and larger are as follows:

Load and motor casing distortion (soft foot): Not more than 0.002 inch (0.0508 mm) at each foot. Use stainless steel pre-stamped shims as required in bringing soft foot within acceptable limits.

Load and motor shaft runout: Not more than 0.001 inch.  If load shaft exceeds criteria contact the LANL Subcontract Technical Representative (STR). If motor shaft runout exceeds criteria, replace the motor.

Alignment tolerances for coupled shafts with short couplings:

| Speed, rpm | SHAFT OFFSET At center, inch (mm) | ANGULARITY/GAP Inch/10 inches (mm/254 mm) |
| --- | --- | --- |
| 600 | 0.005 (0.1270) | 0.010 (0.2540) |
| 900 | 0.003 (0.0762) | 0.007 (0.1778) |
| 1200 | 0.0025 (0.0635) | 0.005 (0.1270) |
| 1800 | 0.002 (0.0508) | 0.003 (0.0762) |
| 3600 | 0.001 (0.0254) | 0.002 (0.0508) |
| 7200 | 0.0005 (0.0127) | 0.001 (0.0254) |

Alignment tolerances for coupled shafts having couplings with spacers:

| Speed, rpm | SHAFT OFFSET Per inch (25.4 mm) of spacer length |
| --- | --- |
| 600 | 0.0018 (0.0457) |
| 900 | 0.0012 (0.0305) |
| 1200 | 0.0009 (0.0229) |
| 1800 | 0.0006 (0.0152) |
| 3600 | 0.0003 (0.0076) |
| 7200 | 0.00015 (0.0038) |

For belt driven loads use string or straight edge alignment of pulley grooves to minimize offset, angle, and twist so belts are not distorted. Verify roundness of pulleys; replace pulleys with total indicator runout exceeding 0.005 inch. Set belt tension as low as possible.

Verify that line voltage and phases agree with motor nameplate.

********************************************************************************************************

Edit the following article to match the current LANL standard specification numbers. Specifications are being updated in phases during 2003. The first section listed is the current number; the second is the intended future number.

********************************************************************************************************

Ground motors according to manufacturer’s instructions and the requirements in Section 26 0526, Grounding and Bonding for Electrical Systems.

Make electrical connections to motors using materials and methods specified in Sections 26 0519, Low Voltage Electrical Power Conductors and Cables and 26 0533, Raceways and Boxes for Electrical Systems. Use flexible conduits, 2 ft. minimum lengths, for connections to motor. Use motor lead splicing kits to insulate and seal connections to leads.

  - FIELD Quality Control

Perform the following inspections for all field installed motors:

Verify that motor nameplate data agrees with Drawings and Specifications.

Inspect physical and mechanical condition of motor.

Verify that motor is properly anchored.

Verify that motor is properly grounded.

Verify that the area around motor fan cooling air inlets is free of debris that could be drawn into motor or motor fan during operation.

Verify that motor is lubricated in accordance with manufacturer’s instructions.

Before energizing, turn motor shaft by hand to verify free rotation.

Perform the following inspections and tests for all field installed motors 10 hp and larger:

Verify the tightness of accessible bolted electrical connections with a calibrated torque-wrench.

Check electrical connections for high resistance using a low-resistance ohmmeter; investigate any values that deviate from similar connections by more than 50 percent.

Perform insulation-resistance tests in accordance with ANSI/IEEE Standard 43; investigate if stator phase-to-phase resistance values deviate by more than 10 percent.

Before energizing motor with driven equipment, verify proper alignment of motor shaft with load shaft.

Verify proper rotation direction as required by the load.

Keep records of inspections and tests for each motor; submit them to the LANL STR.

*****************************************************************************************************

Edit the following article to match project requirements. Delete if formal electrical acceptance testing is not required; refer to LANL Master Specification Section 26 0813.

*****************************************************************************************************

Coordinate inspections and tests with those required by Section 26 0813 -Electrical Acceptance Testing.

********************************************************************************************************

Edit the following article to match project requirements.  Balance the benefits of start-up services against the cost of the motor and the importance of the load it serves.  Delete the following article if the cost of the manufacturer’s start-up service is not warranted.

********************************************************************************************************

  - manufacturer’s Start-up Services

For motors [100] horsepower and larger, provide services of a factory-trained manufacturer’s service representative to verify proper installation and start-up of equipment.

Submit certification that motors have been installed, adjusted, and tested in accordance with manufacturer’s recommendations.

END OF SECTION

********************************************************************************************************

Do not delete the following reference information:

********************************************************************************************************

This project specification is based on LANL Master Specification 26 0700, Rev. 2, dated June 29, 2010.