SECTION 26 2416

Panelboards

*************************************************************************************************************

LANL MASTER SPECIFICATION

Available online at http://engstandards.lanl.gov

This template must be edited for each project.  In doing so, specifier must add job-specific requirements.  Brackets are used in the text to indicate designer choices or locations where text must be supplied by the designer.  Once the choice is made or text supplied, remove the brackets.  The specifications must also be edited to delete specification requirements for processes, items, or designs that are not included in the project -- and specifier’s notes such as these.  To seek a variance from requirements in the specifications that are applicable, contact the Engineering Standards Manual Electrical POC. Please contact POC with suggestions for improvement as well.

When assembling a specification package, include applicable specifications from all Divisions, especially Division 1, General requirements.

Specification developed for ML-4 projects.  For ML-1, 2, and 3 applications, additional requirements and independent reviews should be added if increased confidence in procurement or execution is desired; see ESM Chapter 1 Section Z10 Specifications and Quality Sections.
*************************************************************************************************************

- GENERAL

SECTION INCLUDES

*****************************************************************************************************

Edit the following articles to match project requirements.

*****************************************************************************************************

Panelboards for feeder and branch circuit loads.

Panelboards for instrument and computer loads.

*************************************************************************************************************

The use of load center panelboards is limited to ML-4, single-phase 120/240 V panelboards with a maximum mains rating of 100 amperes, a maximum of 12 single-pole spaces, and an available short-circuit current not exceeding 10,000 amperes RMS symmetrical. Delete this article if there is no need for load center type panelboards.

*************************************************************************************************************

Load center type panelboards for 120/240 V single-phase branch circuit loads.

SUBMITTALS

Submit the following in accordance with Section 01 3300, Submittal Procedures:

Catalog Data: Submit catalog data describing each type panelboard, accessory item, and component specified. Include data substantiating that materials comply with specified requirements.

*************************************************************************************************************

Edit the following articles to match project requirements; delete if no panelboard on the Project is designated with an Ip greater than 1.0.

*************************************************************************************************************

Certification: Submit certification and backup information that panelboard can perform required functions after a design earthquake as specified in "SERVICE CONDITIONS" below.

Panelboards designated with Ip greater than 1.0 shall be certified by the manufacturer to withstand the total lateral seismic force and seismic relative displacements specified in the International Building Code (IBC) or ASCE 7 – Minimum Design Loads for Buildings and Other Structures.

Manufacturer’s certification shall be based on shake table testing or experience data (ie, historical data demonstrating acceptable seismic performance), or by more rigorous analysis providing for equivalent safety.

Required response spectra shall exceed 1.1 times the in-structure spectra determined in accordance with IBC AC156 – Acceptance Criteria for Seismic Qualification by Shake-Table Testing of Nonstructural Components and Systems.

Shop Drawings: Submit shop drawings for each panelboard including dimensioned plans and elevations and component lists. Include front and side views of enclosure showing overall dimensions, enclosure type, enclosure finish, unit locations, and conduit entrances. Include the following:

Enclosure type with details for types other than NEMA Type 1.

Bus configuration and current ratings.

Short-circuit current rating of panelboard.

Features, characteristics, ratings, and factory settings of individual protective devices and auxiliary components.

Wiring Diagrams: Submit detailing schematic wiring diagrams including control wiring, and differentiating between manufacturer-installed and field-installed wiring.

Installation Instructions: Indicate application conditions and limitations of use stipulated by Product testing agency specified under Quality Assurance. Include instructions for storage, handling, protection, examination, installation, and starting of Product.

Operation and Maintenance Instructions: Submit operation and maintenance instructions. Include instructions for testing circuit breakers.

QUALITY ASSURANCE

Comply with the National Electrical Code (NEC) for components and installation.

Furnish products that are listed and labeled by a Nationally Recognized Testing Laboratory (NRTL) for the application, installation condition, and the environment in which installed.

Comply with NEMA PB 1 Panelboards, NEMA PB 1.1 General Instructions for Proper Installation, Operation, and Maintenance of Panelboards Rated 600 Volts or Less, and NEMA AB 3 Molded Case Circuit Breakers and Their Application.

Comply with UL 67 Panelboards, UL 50 Enclosures for Electrical Equipment, and UL 489 Molded Case Circuit Breakers.

The manufacturer of the panelboards shall have an ISO 9001 certified quality management system.

Furnish products suitable for operation at 7500 ft. altitude.

Receiving, Storing and Protecting

Receive, inspect, handle, and store panelboards according to NECA 1 Standard Practices for Good Workmanship in Electrical Construction (ANSI) and NECA 407 Recommended Practice for Installing and Maintaining Panelboards (ANSI).

Perform receipt inspection of panelboard circuit breakers in accordance with LANL P 840-1 Procurement Quality. For each panelboard complete a LANL Form 838c, Quality Assurance Supplement, specifically using clause QC-27 Suspect/Counterfeit Items. Examine each panelboard circuit breaker to verify that it is genuine, new, and unaltered. Report any suspect/counterfeit circuit breakers to the LANL Subcontract Technical Representative and the LANL Suspect/Counterfeit Item Coordinator (SCIC). Indicators of suspect/counterfeit molded-case circuit breakers include the following:

Missing date code.

Date code is older than two years, or style is no longer manufactured.

Factory seals broken or removed.

Mislabeled or over-labeled to change size or type.

Non-English text in labels.

Missing or suspect UL sticker; CE is not an acceptable NRTL.

Low quality labeling and/or misspelled words on labels.

Outdated manufacturer’s label or logo, or refurbisher’s name on label.

Not received in original, sealed packaging.

Screwdriver or wrench marks on terminals.

Handle modified to change ampere rating.

Contradicting amperage, voltage, or interrupting ratings.

EXTRA MATERIALS

Furnish six spare keys of each type for panelboard cabinet locks.

Furnish one spray can of touch-up paint that matches panelboard finish.

  - SERVICE CONDITIONS

    - Provide panelboards and accessories that will perform satisfactorily in the following service conditions:

Elevation of 7500 feet above sea level.

Maximum ambient temperature of 104 °F.

24-hour average temperature not exceeding 86 °F.

Load current harmonic factor not exceeding 5% THD.

International Building Code seismic criteria:

Seismic Design Category = D

SDS = spectral acceleration, short period = 0.75g

SD1 = spectral acceleration, 1-second period = 0.64g

ap = component amplification factor = 2.5

Rp = component response modification factor = 6.0

Ip = Component importance factor
Ip = 1.5 for life safety related components such as emergency system panelboards
Ip = 1.5 for safety class or safety significant system panelboards.
Ip = 1.0 for all other panelboard applications

*****************************************************************************************************

Edit the following article to match project requirements; use only for outdoor equipment.

*****************************************************************************************************

Maximum solar heat gain: 110 W/sq ft.

    - Conform to NEMA PB1 service conditions during and after installation of panelboards.

PRODUCTS

  - PRODUCT OPTIONS AND SUBSTITUTIONS

Alternate products may be accepted; follow Section 01 2500, Substitution Procedures.

PANELBOARDS

Furnish panelboards as indicated on the Drawings and specified in this Section.

Panelboards shall be UL67 listed and shall conform to NEMA PB1.

Main bus rating for the panelboards described in this Section shall not exceed 1200 amperes and main circuit breaker frame size shall not exceed 800 amperes. Refer to Section 26 2413, Switchboards, when main bus rating exceeds 1200 amperes or main circuit breaker frame size exceeds 800 amperes.

Where practical combine adjacent panelboards into integrated assemblies of 90-inch high modular components.

Furnish panelboard cabinets for flush or surface mounted as indicted on the Drawings.

Furnish NEMA Type 1 enclosures, except where the Drawings or conditions of installation indicate the following enclosure requirements:

NEMA 3R: Raintight

NEMA 3S: Raintight and dust tight

NEMA 4X: Corrosion-resistant fiberglass enclosure, watertight, dust tight, and resistant to oil and coolant seepage

NEMA 12: Dust tight, dripproof, and resistant to oil and coolant seepage.

Cabinets shall be not less than 20 inches wide.

Furnish galvanized steel cabinets constructed according to UL 50 requirements.

NEMA 1 boxes shall have removable end walls. NEMA 3, 3S, 4X and 12 boxes shall have end walls welded and sealed.

Furnish trim fronts that meet the strength and rigidity requirements of UL 50.

Each panelboard trim front shall include a door.

Fronts for surface-mounted panels shall be same dimensions as box.

Fronts for flush panels shall overlap boxes at least 1 inch.

Fronts shall have ANSI 49 medium gray enamel electro-deposited over cleaned, phosphatized steel.

For NEMA 1 panelboards, furnish fronts with hinged door-in-door trim construction.  The front shall contain a smaller lockable door, which when open, shall provide access to all device handles and rating labels.  The hinged front, when open, shall provide access to all conductors and wiring terminals.  The panelboard door shall open by a single lockable latch; the entire hinged front trim shall open by removing screws.

Furnish a panelboard circuit directory card in a metal frame mounted inside the panelboard door. The directory card shall include spaces for circuit numbers and sufficient spaces to allow each circuit to be described in sufficient detail to be distinguished from all others.

Furnish cylindrical tumbler type locks for doors. Furnish sliding vault locks with 3-point latching for enclosures more than 48 inches high. Key all lock assemblies alike.  Furnish two (2) keys with each lock plus spares as required in the Extra Materials paragraph above.

Panelboard phase and neutral bus shall be copper.  Panelboard bus current ratings shall be determined by heat-rise tests conducted according to UL 67.  Panelboards used on 480V and 480Y/277V systems shall have bus insulators and separations rated for 600V.

Furnish panelboard box with dimensions as required to accommodate compression lugs on cables for the panelboard mains, neutral bar, and circuit breakers rated 100 amperes and larger. Refer to Section 26 0519 - Low Voltage Electrical Power Conductors and Cables for compression lug requirements.

Furnish copper equipment ground bus that is adequate for feeder and branch circuit equipment ground conductors.  Bond ground bus to cabinet.

Panelboards having a main circuit breaker shall be NRTL-listed for use as service entrance equipment.

Equip panelboards with mounting brackets, bus connections, and necessary appurtenances, for the future installation of circuit breakers in the “spaces” scheduled on the Drawings.

Furnish panelboards having NRTL-listed short circuit current ratings not less than the available fault current indicated on the Drawings.  With the exception of panelboard with a current-limiting main circuit breaker, do not use “series ratings” for circuit breaker interrupting capacities.  The short circuit rating for a panelboard without a current-limiting main circuit breaker shall not exceed the lowest interrupting capacity rating of any circuit breaker installed in the panelboard.

Furnish thermal-magnetic circuit breakers that meet the requirements of UL 489 and NEMA AB 3.

Furnish circuit breakers of the type, rating, and features as indicated on the Drawings.

Furnish 600V-rated two-pole and three-pole circuit breakers for 480V or 480Y/277V systems.

Furnish circuit breakers with the following minimum NRTL-listed interrupting capacities:

208Y/120V and 120/240V applications: 10,000 amperes, RMS symmetrical

480V and 480Y/277V applications: 14,000 amperes, RMS symmetrical.

Furnish field adjustable instantaneous trip setting for circuit breakers with frame size greater than 100 amperes.

Do not use tandem circuit breakers.

Furnish multi-pole breakers with a common trip.

Furnish bolt-on type circuit breakers or circuit breakers that connect to the panel bus through positive gripping connector jaws and are secured by an independent mechanical locking device.

Single-pole, 15 and 20 ampere circuit breakers intended to switch fluorescent lighting loads on a regular basis shall have the SWD marking.

Circuit breakers intended to switch high intensity discharge lighting loads on a regular basis shall have the HID marking.

Furnish UL Class A ground fault interrupter circuit breakers where scheduled on Drawings.

Furnish circuit breakers with provisions for connecting the size and number of conductors indicated on the Drawings. Refer to Section 26 0519 - Low Voltage Electrical Power Conductors and Cables for conductor connection requirements.

Furnish a permanently-installed handle lock-off device for each circuit breaker.

Furnish handle lock-off device that will accept a 1/4-inch padlock shackle.

Securely attach the device to the circuit breaker case; the attachment shall not depending on a friction fit or the presence of the panelboard front for the handle lock-off device to remain in place and be functional.

*************************************************************************************************

Edit the following articles to match project requirements. Delete accessories that are not required.

*************************************************************************************************

Furnish the following accessories, modifications, or special features for panelboards as indicated on the Drawings.

Split Bus: Vertical buses of indicated panels divided into two vertical sections with connections as indicated.

Conduit Covers for Surface Mounted Panels: Same gage and finish as panel front with flanges for attachment to panel, wall, and the floor.

Contactors in Mains: Mechanically held, with current rating, poles, and connections as indicated on the Drawings.

Shunt trip: Shunt-trip main circuit breaker or shunt-trip branch circuit breakers.

Control Power Source: Control power transformer of capacity indicated, for contactor shunt trip or other devices.  Mount in cabinet of panel indicated.  Protect primary with current-limiting fuses.  Furnish fused protection of control circuits.

Extra Gutter Space: Dimensions and arrangement as indicated on the Drawings.

Gutter Barrier: Arranged to isolate section of gutter as indicated.

Auxiliary Gutter: Conform to UL 870, "Wireways, Auxiliary Gutters and Associated Fittings."

Column Type Panelboard Configuration: Narrow cabinet extended as wireway to overhead junction box equipped with ground and neutral terminal buses.

Neutral bus rated 200% of the phase bus for high harmonic applications.

Subfeed circuit breaker or lug provision as indicated.

Feed-Through Lugs: Sized to accommodate feeders indicated.

Surge Arresters: Refer to Section [26 4100, Lightning Protection] [26 4116, Lightning Protection for Explosives Facilities].

Transient Voltage Surge Suppressors: Refer to Section 26 4123, Lightning Protection Surge Arresters and Suppressors, and Section 26 4313, Transient Voltage Suppressors.

Manufacturers:

Eaton:

480 V and 480Y/277 V: “PRL3a” and “PRL4”

208Y/120 V and 120/240 V: “PRL1a” and “PRL2a”

Siemens:

480 V and 480Y/277 V: “P2”, “P3”, and “P4”

208Y/120 V and 120/240 V: “P1”

Square D:

480 V and 480Y/277 V: “NF” and “I-LINE”

208Y/120 V and 120/240 V: “NQ” and “I-Line”

*************************************************************************************************************

Delete this article if there is no need for isolated ground power systems; refer to Section D5010 in Chapter 7 of the LANL Engineering Standards Manual.

*************************************************************************************************************

PANELBOARDS FOR INSTRUMENT AND COMPUTER LOADS

Furnish panelboards for 208Y/120V or 120/240V instrument and computer loads.

Furnish panelboards that meet requirements in article 2.2 PANELBOARDS and have the following additional features:

Enclosures shall be not less than 20 inches or more than 26 inches wide.

Furnish a 200% rated neutral bus.

Furnish an isolated ground bus in addition to the equipment ground bus.  Size isolated ground bus to accept feeder and branch-circuit isolated ground conductors that are the same size as the corresponding circuit phase conductors.

Manufacturers:

Eaton: “PRL1a” and “PRL2a”

Siemens: “P1"

Square D: “NQ” and “I-Line”

*************************************************************************************************************

The use of load center panelboards is limited to ML-4, single-phase 120/240 V panelboards with a maximum mains rating of 100 amperes, a maximum of 12 single-pole spaces, and an available short-circuit current not exceeding 10,000 amperes RMS symmetrical. Delete this article if there is no need for load center type panelboards.

*************************************************************************************************************

Load Center Panelboards

Furnish UL67 listed and labeled load center type panelboards as indicated on the Drawings and specified in this Section for single-phase 120/240V branch circuit loads.

Main bus rating for the load center type panelboards described in this Article shall not exceed 100 amperes. Refer to the PANELBOARDS Article in this Section when main bus rating exceeds 100 amperes.

Furnish steel load center cabinets for flush or surface mounted as indicted on the Drawings.

Furnish NEMA Type 1 enclosures for indoor applications.

Furnish NEMA Type 3R enclosures for outdoor applications.

Furnish steel trim fronts that meet the strength and rigidity requirements of UL 50.

Fronts for surface-mounted panels shall be same dimensions as box.

Fronts for flush panels shall overlap boxes at least 1 inch.

Fronts shall have medium gray enamel finish.

Furnish equipment ground bus that is adequate for feeder and branch circuit equipment ground conductors.  Bond ground bus to cabinet.

Load centers identified for use as service equipment shall be NRTL-labeled for this application.

Furnish thermal-magnetic circuit breakers that meet the requirements of UL 489 and NEMA AB 3.

Furnish circuit breakers of the type, rating, and features as indicated on the Drawings.

Furnish circuit breakers with an NRTL-listed interrupting capacity of 10,000 amperes, RMS symmetrical:

Furnish circuit breakers that are not less than 3/4 inches wide; do not use tandem circuit breakers.

Furnish 2-pole 120/240 V breakers with a common trip.

Furnish a permanently-installed handle lock-off device for each load center circuit breaker.

Furnish handle lock-off device that will accept a 1/4-inch padlock shackle.

Firmly attach the device to the circuit breaker case; the attachment shall not depending on a friction fit or the presence of the load center front for the handle lock-off device to remain in place and be functional.

Manufacturers:

Eaton: “BR” and “CH”

Siemens: “EQ" and “Ultimate”

Square D: “QO”

EXECUTION

  - EXISTING WORK

*************************************************************************************************************

Delete this article when existing construction is not affected.

*************************************************************************************************************

Disconnect and remove abandoned panelboards.

Maintain access to existing panelboards and other installations that are to remain active and to require access.  Modify installation or furnish access panel.

Clean and repair existing panelboards that are to remain or be reinstalled.

EXAMINATION

Examine surfaces to receive panelboards for compliance with installation tolerances and other conditions affecting performance of the control system.  Do not proceed with installation until unsatisfactory conditions have been corrected.

INSTALLATION

Install panelboards where indicated on the Drawings and according to manufacturer's instructions, NEMA PB 1.1, NECA 407, and the NEC.  Have the manufacturer’s installation instructions available at the construction site.

Furnish supports in accordance with the requirements of Section 26 0529 Hangers and Supports for Electrical Systems

Position panelboards so the top circuit breaker handle is not more than 6’-7” above the surface of the working space in front of the panelboard.

Ground and bond panelboards as required in Section 26 0526 Grounding and Bonding for Electrical Systems.

*****************************************************************************************************

Edit the following article to match project requirements.

*****************************************************************************************************

At flush panelboards install four 1-inch conduits to junction boxes in accessible ceiling space or space designated to be ceiling space in future.  [Install four 1-inch conduits to junction boxes in raised floor space.]  Install branch circuit conductors from panelboard spare circuit breakers to junction boxes for future extension.

Install an auxiliary gutter with permanently installed terminal blocks where a panel is tapped to a riser at an intermediate location.

IDENTIFICATION

Furnish typed circuit directories for each branch circuit panelboard.  Revise directories to reflect circuiting changes required to balance phase loads.

Furnish one hard copy and an electronic copy of the panelboard schedule to the Facility Manager at project closeout.

Install a plastic-laminated copy of the circuit directory on the inner side of the panelboard door.

Identify panelboards and install warning signs and arc-flash warning labels as required in Section 26 0553, Identification for Electrical Systems.

Mark floor in front of panelboards to show NEC required working space according to Section 26 0553, Identification for Electrical Systems..

FIELD QUALITY CONTROL

Clean, inspect, test, and energize panelboards in accordance with NECA 407. Exercise each circuit breaker three times to verify smooth mechanical operation.

*****************************************************************************************************

Edit the following article to match project requirements. Delete if formal electrical acceptance testing is not required; refer to LANL Master Specification Section 26 0813.

*****************************************************************************************************

Coordinate inspections and tests with those required by Section 26 0813, Electrical Acceptance Testing.

After completing installation, cleaning, and testing, touch-up scratches and mars on finish to match original finish.

LOAD BALANCING

After Substantial Completion, but not more than two months after Final Acceptance, conduct load-balancing in accordance with NECA 407 and as follows:

Do measurements during period of normal working loads as advised by the User.

Make load-balancing circuit changes outside the normal occupancy/working schedule of the facility.  Arrange with User to avoid disrupting critical services.

Recheck loads after circuit changes during a normal load period.  Record all load readings before and after changes and submit test records.

END OF SECTION

****************************************************************************************************

Do not delete the following reference information.

****************************************************************************************************

FOR LANL USE ONLY

This project specification is based on LANL Master Specification 26 2416 Rev. 2, dated August 3, 2009.