SECTION 26 2419

MOTOR CONTROL CENTER

*************************************************************************************************************

LANL MASTER SPECIFICATION

Available online at http://engstandards.lanl.gov

This template must be edited for each project.  In doing so, specifier must add job-specific requirements.  Brackets are used in the text to indicate designer choices or locations where text must be supplied by the designer.  Once the choice is made or text supplied, remove the brackets.  The specifications must also be edited to delete specification requirements for processes, items, or designs that are not included in the project -- and specifier’s notes such as these.  To seek a variance from requirements in the specifications that are applicable, contact the Engineering Standards Manual Electrical POC. Please contact POC with suggestions for improvement as well.

When assembling a specification package, include applicable specifications from all Divisions, especially Division 1, General requirements.

Specification developed for ML-4 projects.  For ML-1, 2, and 3 applications, additional requirements and independent reviews should be added if increased confidence in procurement or execution is desired; see ESM Chapter 1 Section Z10 Specifications and Quality Sections.

*************************************************************************************************************

*************************************************************************************************************

NOTE: At the time Revision 3 is being generated, there is no standard for arc-resistant MCCs; the manufacturers’ products referenced in this Section are designed to reduce the arc-flash hazard associated with MCCs, but they each use different strategies to achieve that goal. The NFPA 70E definition of arc-resistant switchgear is used to establish performance requirements for arc-resistant MCCs.

*************************************************************************************************************

GENERAL

  - SECTION INCLUDES

- Motor control center (MCC) rated 600 volts and less.

  - DEFINITIONS

- Arc-resistant: Designed to withstand the effects of an internal arcing fault and to direct the internally released energy away from employees

  - SUBMITTALS

- Provide the following submittals according to the requirements of Section 
01 7700 and Project submittal procedures:

  - Catalog Data: Submit manufacturer’s descriptive literature describing each MCC. Include data substantiating that materials comply with specified requirements including a full description of the arc-resistant design features.

  - Shop Drawings: Submit shop drawings for each MCC including dimensioned plans and elevations and component lists. Show ratings, including short time and short circuit ratings, and horizontal and vertical bus ampacities. Include: front and side views of enclosure showing overall dimensions, enclosure type, enclosure finish, unit locations, and conduit entrance locations.

  - Wiring Diagrams: Submit interconnecting wiring diagrams pertinent to the class and type specified for the MCC. Submit a schematic diagram of each type of controller unit supplied.

*************************************************************************************************************

Edit the following article to match Project requirements; delete if no MCC on the Project is designated with an Ip greater than 1.0.

*************************************************************************************************************

  - Certification: Submit certification and backup information that MCC can perform required functions after a design earthquake as specified in “SERVICE CONDITIONS” below.

        - MCC designated with Ip greater than 1.0 shall be certified by the manufacturer to withstand the total lateral seismic force and seismic relative displacements specified in the International Building Code (IBC) or ASCE 7, Minimum Design Loads for Buildings and Other Structures.

        - Certification shall be based on shake table testing or experience data (i.e., historical data demonstrating acceptable seismic performance), or by more rigorous analysis providing for equivalent safety.

        - Required response spectra shall exceed 1.1 times the in-structure spectra determined in accordance with IBC AC156, Acceptance Criteria for Seismic Qualification by Shake-Table Testing of Nonstructural Components and Systems.

  - Certification: Submit certification by manufacturer’s field technical representative that the subcontractor has installed, adjusted, and tested each MCC according to the manufacturer’s recommendations.

  - Installation Instructions: Indicate application conditions and limitations of use stipulated by Product testing agency specified in “QUALITY ASSURANCE”.  Include instructions for storage, handling, protection, examination, installation, and starting of Product, including equipment anchoring requirements to meet the seismic conditions specified in “SERVICE CONDITIONS”.

  - Operation and Maintenance Instructions:

        - Submit complete operation and maintenance instructions including step-by-step inspection, and maintenance procedures.

        - Include the manufacturer’s name, equipment model number, service manual, parts list, and brief description of equipment and its basic operational features.

  - Test and Inspection Records: Submit records of inspections, tests, and adjustments performed under FIELD QUALITY CONTROL.

  - QUALITY ASSURANCE

- MCC shall be listed and labeled to the current edition of UL 845 – UL Standard for Safety for Motor Control Centers by a Nationally Recognized Testing Laboratory (NRTL) for the application, installation condition, and the environment in which installed.

- MCC shall be manufactured in a certified ISO 9001 or 9002 facility.

- Comply with the National Electrical Code (NEC) for components and installation.

  - COORDINATION

- Coordinate the features of each motor controller with the ratings and characteristics of the supply circuit, the motor, the required control sequence, the duty cycle of the motor, drive, load, the pilot device, and control circuit affecting controller functions.  Furnish controllers that are horsepower rated to suit the motor controlled.

  - DELIVERY, STORAGE, AND HANDLING

- Receive, handle, and store MCC according to NECA 402 – Recommended Practice for Installing and Maintaining Motor Control Centers and NEMA ICS 2.3 – Instructions for Handling, Installation, Operation, and Maintenance of Motor Control Centers.

- Perform receipt inspection of MCC molded-case circuit breakers in accordance with LANL P 840-1 Procurement Quality. For each MCC complete a LANL Form 838c, Quality Assurance Supplement, specifically using clause QC-27 Suspect/Counterfeit Items. Examine each MCC molded-case circuit breaker to verify that it is genuine, new, and unaltered. Report any suspect/counterfeit circuit breakers to the LANL Subcontract Technical Representative and the LANL Suspect/Counterfeit Item Coordinator (SCIC). Indicators of suspect/counterfeit molded-case circuit breakers include the following:

      - Missing date code.

      - Date code is older than two years, or style is no longer manufactured.

      - Factory seals broken or removed.

      - Mislabeled or over-labeled to change size or type.

      - Non-English text in labels.

      - Missing or suspect UL sticker; CE is not an acceptable NRTL.

      - Low quality labeling and/or misspelled words on labels.

      - Outdated manufacturer’s label or logo, or refurbisher’s name on label.

      - Not received in original, sealed packaging.

      - Screwdriver or wrench marks on terminals.

      - Handle modified to change ampere rating.

      - Contradicting amperage, voltage, or interrupting ratings.

  - SERVICE CONDITIONS

- MCC shall perform satisfactorily in the following service conditions without mechanical or electrical damage or degradation of operating characteristics:

- Operating elevation of 7500 feet above sea level.

- Operating ambient temperature extremes of 32 to 104 degrees F.

- 24-hour average operating ambient temperature not exceeding 86 °F.

- Operating relative humidity: 0 to 95 percent, without condensation.

- International Building Code seismic criteria:

      - Seismic Design Category = D

      - SDS = spectral acceleration, short period = 0.75g

      - SD1 = spectral acceleration, 1-second period = 0.64g

      - ap = component amplification factor = 2.5

      - Rp = component response modification factor = 6.0

      - Ip = component importance factor
Ip = 1.5 for life safety related components such as emergency system MCCs
Ip = 1.5 for safety class or safety significant system MCCs.
Ip = 1.0 for all other MCC applications

*****************************************************************************************************

Edit the following article to match project requirements; use only for outdoor equipment.

*****************************************************************************************************

- Maximum solar heat gain: 110 W/sq ft.

  - EXTRA MATERIALS

- Furnish six spares of each size and type fuse required.

- Furnish one spray can of touch-up paint that matches finish for each MCC.

  - FIELD MEASUREMENTS

- Verify field measurements against manufacturer’s shop drawings prior to fabrication.

PRODUCTS

  - PRODUCT OPTIONS AND SUBSTITUTIONS

- Alternate products may be accepted; follow Section 01 2500, Substitution Procedures.

  - GENERAL

- Furnish arc-resistant MCC as indicated on the Drawings that complies with UL 845 and NEMA ICS 18 – Standard for Motor Control Centers and is designed to withstand the effects of an internal arcing fault and to direct the internally released energy away from employees.

*************************************************************************************************************

Edit the following article to match Project requirements; typically use Class I, Type B.

*************************************************************************************************************

- MCC shall have wiring classification [Class I, Type A] [Class I, Type B] [Class I, Type C] [Class II, Type B] [Class II, Type C], as defined in NEMA ICS 2.

*************************************************************************************************************

Edit the following article to match Project requirements; typically use Type 1A for indoor installations.

*************************************************************************************************************

- MCC shall have NEMA [Type 1 (general purpose)] [Type 1A (gasketed general purpose)] [Type 12 (industrial duty)] [Type 3R non-walk-in (rainproof)][Type 3R walk-in with 48” minimum aisle, interior lighting, door at each end, automatic ventilation system, sloped roof, and anti-skid floor]enclosure as defined in NEMA 250—Enclosures for Electrical Equipment, except as otherwise indicated.

- MCC sections and components shall have UL 508 short-circuit current withstand or interrupting ratings equal to or greater than the available fault current, in RMS symmetrical amperes, available at the MCC line terminals.

- Manufacturers:

  - Allen-Bradley, “CENTERLINE 2100”

  - Eaton, “Freedom 2100 Series”

  - STRUCTURE

- MCC structure shall consist of vertical sections that are bolted together to form a rigid, self-supporting, free-standing assembly and are designed to permit future additions or rearrangement of control units.

- Design enclosure to be rodent proof with maximum 1/4" diameter unprotected openings.

- Fabricate individual vertical sections from 12 gauge minimum steel continuous top and bottom frames. These steel frames shall be connected by vertical members consisting of cold-rolled steel box-sills at each corner and 12 gauge minimum vertical C-channels.

- Each MCC shipping section shall have removable lifting angles. Mount each shipping section on steel channel sills.

- Vertical sections shall be a nominal height of 90 inches and width of 20 inches. The depth of all sections shall be 15 to 16 inches nominal.

- Each section shall have dead-front and dead-back construction. Rear access shall not be necessary for inspection or maintenance. The structure arrangement shall be for front only mounting of units.

- Each vertical section shall have a conduit entrance area on the top. This opening shall be covered with a bolted flat plate which may be removed and drilled. Provide the bottom of each structure with a rectangular area for termination of conduit.

- Each vertical section shall have a top and a bottom horizontal wireway, aligned with adjacent sections, to form wireways extending the entire length of the motor control center. End vertical sections shall have cover plates which can be easily removed to allow addition of future vertical sections

- Furnish each vertical section with a vertical wireway extending the full height of the structure and connecting to the top and bottom wireways. The vertical wireway shall have its own separate hinged door. Provide wire tie retainers in vertical wireway.

- Doors shall be formed of 16 gauge steel or heavier, with all edges flanged 5/8 inches deep minimum. Doors shall be mounted on adjustable and removable pin type concealed hinges and so arranged that unit doors may be removed without disturbing unit doors above or below.

- Isolate all power bussing and splice connections from the unit compartments and from the vertical and horizontal wireways.

- Barriers in the structure and units shall prevent the contact of any energized bus or terminal by a fish tape inserted through the conduit or wireway areas.

  - FINISH

- Paint enclosure and unit parts using an electro-deposition process. Interior and exterior surfaces as well as bolted joints shall have a complete finish coat on and between them. The paint process shall consist of cleaning, rinsing, phosphating, pre-paint rinses, painting, post paint rinses, a bake cure, and cool down.

- Paint exterior surfaces with medium light gray acrylic enamel. Paint the unit interior surfaces white for greater internal visibility.

- Furnish all unpainted parts with corrosion-resistant plating or material.

  - BUS BARS AND BRACING

- Main horizontal bus shall extend the entire length of the MCC. Bus shall be fabricated from tin-plated copper with ratings as shown on the Drawings.

- The vertical bus in each section shall be tin-plated copper with a current capacity of not less than 300 amps. The bus support system shall be high dielectric strength, low moisture absorbing, and high-impact material.

*************************************************************************************************************

Edit the following article to match Project requirements.

*************************************************************************************************************

- Bus assembly shall be braced and NRTL-listed to withstand the mechanical stress caused by fault currents of [42,000][65,000][100,000] sym. RMS amperes.

- A continuous copper ground bus, with a minimum current rating of 300 amperes, shall be located in the bottom of the structure, with cable lugs at each end of the line-up. A copper vertical ground bus shall make contact with the plug-in units before the bus stabs engage the vertical bus.

- Bolted connections at each bus joint shall be front accessible for servicing with a torque wrench. Indicate the location of all splices with a label located on the inside of the vertical wireway door.

  - ISOLATION AND INSULATION

- Horizontal bus access covers and vertical bus covers shall isolate the energized buses to guard against the hazard of accidental contact.

- Cutouts shall be located in the vertical isolation barriers for stab connections to the vertical bus. A shutter mechanism shall close the cutouts when a plug-in unit is removed. Provide the vertical bus with phase isolation barriers.

- Isolate all units from one another, above and below, by unit support pans or steel barriers which remain in place when the units are withdrawn.

- Isolate incoming line compartments from horizontal and vertical wireways by steel barriers.

- Units shall have a side barrier to provide isolation from the vertical wireway.

  - UNITS

- Furnish combination motor starter units, Size 1 through Size 5, as well as other electrical assemblies including feeder tap units through 225 amps, with appropriately rated stab assemblies for plug-in type construction. Starter units Size 6 and larger, as well as feeder tap units above 225 amps, shall be bolt-in construction.

- Support and guide each plug-in unit so that unit arrangement is easily accomplished. After insertion, each plug-in unit shall be positively held in place.

- Each plug-in unit shall have a safety grounding device that makes connection to the vertical ground bus before the power stabs engage.

- An operator mechanism mounted on the unit shall provide the means for operating the disconnect. This operator shall extend through an opening in the unit door and shall clearly indicate whether the disconnect is 'ON', 'OFF', or 'TRIPPED'. This indication shall function whether the compartment door is open or closed.

- With the disconnect in the 'ON' position, a mechanical interlock shall prevent opening of the unit door. This interlock shall be provided with a defeater so that authorized personnel may gain access to the compartment without interrupting service. This interlock shall also prevent unintentional closing of the disconnect when the compartment door is open, a second mechanical interlock shall prevent any possibility of removing or re-inserting the plug-in unit while the disconnect is in the 'ON' position.

- The operator mechanism design shall provide for padlocking the disconnect in the 'OFF' position with up to three padlocks.

- The operator mechanism shall be so designed as to allow easy access to the magnetic trip settings on circuit breakers and motor circuit protectors.

- Each unit shall have a removable door mounted on removable pin type hinges which allow the door to swing open at least 110 degrees. Doors shall be removable from any location in the center without disturbing any other doors. The unit door shall be fastened to the stationary structure so that it can be closed to cover the unit space when the insert has been removed. The unit doors shall be held closed with 1/4 turn pawl type latches, designed to resist forces during fault conditions.

*************************************************************************************************************

Edit the following article to match Project requirements.

*************************************************************************************************************

  - INCOMING MAIN AND FEEDER TAP UNITS

- Furnish incoming main and feeder tap units as indicated on the Drawings.

- Overcurrent devices shall be 600 volt, molded case, thermal magnetic circuit breakers that conform to NEMA AB 1 – Molded Case Circuit Breakers.

- The UL listed interrupting capacity of the circuit breakers shall equal or exceed the maximum available fault current at the motor control center.

- Provide adequate space for terminating conductors using circumferential compression lugs on main lugs and on main and feeder tap circuit breaker frames larger than 100 amperes.

  - CIRCUIT BREAKER TYPE NON-REVERSING STARTER UNITS

- Furnish starter units containing combination magnetic motor controllers with motor circuit protector disconnects as indicated on the Drawings.

- Motor circuit protector shall conform to UL 845 and NEMA AB 1 - Molded Case Circuit Breakers, with an integral instantaneous magnetic trip in each pole.

  - Trip units shall be calibrated to coordinate with the actual locked-rotor current of the connected motor and the controller overload relays.

  - Furnish motor circuit protectors that are factory assembled with the controller, interlocked with unit cover or door, and arranged to disconnect the controller.

  - The short circuit rating of the motor circuit protector and starter combination shall equal or exceed the maximum available fault current at the MCC.

  - Furnish motor circuit protectors rated 600 volts when used on 480 volt systems.

- Controllers shall be AC general purpose Class A magnetic, full-voltage, non-reversing controllers for induction motors rated in horsepower and conforming to the requirements of NEMA ICS 2 – Industrial Control Devices, Controllers, and Assemblies.

  - Coil shall be of the encapsulated type, 120 volts, 60 Hz.

  - Controllers shall be the sizes and number of poles as indicated on the Drawings.

  - Contacts shall be totally enclosed, double-break, silver-cadmium-oxide power contacts. Contact inspection and replacement small be possible without disturbing line or load wiring.

  - Each controller shall have not less than two sets of NEMA ICS 2 field convertible auxiliary contacts in addition to the seal-in contact.

- Controllers for motors rated up to 100 full-load amperes shall have solid-state overload units with the following characteristics:

*************************************************************************************************************

Edit the following article to match Project requirements. Class 20 tripping is suitable for most applications.

*************************************************************************************************************

  - NEMA Class [10][20] tripping characteristics

  - Field selectable motor full load current.

  - Ambient temperature insensitive.

  - Phase loss protection.

  - Manual reset after time delay.

  - Integral current transformers.

*************************************************************************************************************

Edit the following articles to match Project requirements; delete if no motors on Project are rated from 100 to 300 full-load amperes. Refer to Section D5020 in the LANL Engineering Standards Manual for overload protection for motors rated over 300 full-load amperes.

*************************************************************************************************************

- Controllers for motors rated from 100 to 300 full-load amperes shall have solid-state overload units with the following characteristics:

*************************************************************************************************************

Edit the following article to match Project requirements; some motor/load combinations require a Class 10 start time characteristic.

*************************************************************************************************************

  - NEMA Class [10] [20] tripping characteristics.

  - Field selectable/adjustable overload trip current.

  - Phase unbalance and phase loss protection.

  - Manual or electric reset after time delay.

  - Current sensing using external current transformers with 5 ampere secondary.

- Controllers shall have heavy duty, 22 mm or 30 mm, metal operator, oil tight pilot devices as listed below with NEMA ICS 2, Form Z, A600 rated contacts. Mount pilot devices on a removable panel located on the starter, not on the compartment door; there shall be no conductors across the unit door hinge.

  - Selector Switches:  Rotary type

      - Use HAND-OFF-AUTO or ON-OFF-AUTO selector switch if controller is connected to an automatic control system.

      - Unless indicated otherwise on the Drawings, selector switch is not required if controller is not connected to an automatic control system.

  - Push buttons:

      - Use flush, momentary-contact START and STOP pushbuttons if controller is not connected to an automatic control system.

      - Unless indicated otherwise on the Drawings, START-STOP pushbuttons are not required if controller is connected to an automatic control system.

*************************************************************************************************************

Edit d to match Project requirements. Delete if not required

*************************************************************************************************************

      - Furnish mushroom head, maintained action, turn-to-release or pull-to-release EMERGENCY STOP pushbutton as indicated on the Drawings.

  - Use push-to-test LED type indicating lights as follows:

      - Red RUNNING pilot light.

      - Green STOPPED pilot light.

      - Additional pilot lights as indicated on the Drawings.

  - Push-buttons, pilot lights and selector switches shall have legend plates.

- Each motor overload unit shall have an externally operable manual reset operator.

- Each motor starter unit shall have a control power transformer with 120 volt secondary and sufficient capacity to operate starter coil and all connected pilot, indicating and control devices, plus 100 percent spare capacity. Primary and secondary circuits of transformer shall be fused. Bond un-fused leg of secondary to enclosure.  Use fuse blown indicating fuses mounted in fuse blocks.

- Adhere to accepted industry standards of neatness and bending radius for wiring of controller units. Use MTW (AWM) wire for control and power wiring. Install wrap-around wire markers at both ends on all control wiring.

- Pull-apart control terminal blocks shall be mounted on the side or near the bottom of each unit to permit clear and easy access to the terminals. Terminal blocks shall facilitate disconnection and removal of the unit without damage to wiring.

- Controller shall have auxiliary control relay(s) as indicated in the drawings or as required by sequence of operation. Relays shall be heavy-duty general purpose type, having 115 volt 60 Hertz operating coils.

- In units serving loads greater than 100 amperes, provide adequate space for terminating load conductors using circumferential compression lugs.

  - IDENTIFICATION

- Each unit shall have an identification nameplate label, indicating either a catalog number or serial number description.

- Each vertical section shall have a stamped metallic identification nameplate, indicating serial number, bus rating and vertical section reference numbering. The nameplate shall be externally mounted near the center of the vertical wireway door of each section.

- Attach nameplates using sheet metal screws or approved alternate method.

EXECUTION

EXISTING WORK

*************************************************************************************************************

Delete this article when existing construction is not affected.

*************************************************************************************************************

- Disconnect and remove each abandoned MCC.

- Maintain access to each existing MCC that is to remain active.

- Clean and repair each existing MCC that is to remain or be reinstalled.

EXAMINATION

- Examine spaces and surfaces to receive MCCs for compliance with installation tolerances and other conditions affecting performance of the product.  Do not proceed with installation until unsatisfactory conditions have been corrected.

INSTALLATION

- General:  Install each MCC where indicated on the Drawings in accordance with NECA 402 – Recommended Practice for Installing and Maintaining Motor Control Centers, NEMA ICS 2.3 – Instructions for the Handling, Installation, Operation, and Maintenance of MCCs, and with the manufacturer's written installation instructions.

- Provide a minimum of 1/2 inch space between the back of MCC and a wall; provide a minimum of 6-inch space for damp locations.

- Install each MCC on a reinforced concrete housekeeping pad, minimum 5” thick. Refer to Section 26 0548 – Vibration and Seismic Controls for Electrical Systems for materials and installation requirements.

- Remove temporary lifting eyes, channels, brackets, and temporary blocking of moving parts from MCC units and components.

- Ground and bond MCC as required in Section 26 0526 – Grounding and Bonding for Electrical Systems.

- Install conduits as required in Section 26 0533 – Raceways and Boxes for Electrical Systems.

  - Terminate conduits in the MCC section containing the corresponding device.

  - Install plugged couplings set flush with the top of the concrete pad. After MCC is set in place, extend conduits to 1-1/4 inch above the pad and terminate with insulated grounding bushings.

- Install conductors as required in Section 26 0519 – Low Voltage Electrical Power Conductors and Cables.

- Train conductors neatly in groups; bundle and secure as recommended by manufacturer to withstand fault current.

- Use compression type lugs to connect all service, feeder, and branch circuit cables greater than 100 amperes.

- Tighten electrical connectors and terminals, including bus bar and grounding connections, according to the manufacturer’s published torque-tightening values. Where manufacturer’s torque values are not indicated, use those specified in UL 486A-486B.

- Set overload relays in motor controllers to match installed motor characteristics.

IDENTIFICATION

- Identify MCC and install warning signs and arc-flash warning labels as required in Section 26 0553 – Identification for Electrical Systems.

- Provide Category I nameplate for each starter unit or overcurrent protective device. Refer to Section 26 0553.

- At indoor locations, mark floor in front of motor control center to show NEC required working clearances according to Section 26 0553.

- Provide neatly typed label inside each motor starter enclosure door identifying motor served, nameplate horsepower, full load amperes, code letter, service factor, and voltage/phase rating.

- Post one-line diagrams data and operating instructions in accordance with Section 26 0553.

FIELD QUALITY CONTROL

- Clean, inspect, test, adjust, and energize MCCs in accordance with the manufacturer’s instructions and NECA 402.

      - Inspect each MCC for physical damage, proper alignment, and proper anchorage.

      - Keep records of inspections, tests, and adjustments; submit them to the LANL STR.

*****************************************************************************************************

Edit the following article to match project requirements. Delete if formal electrical acceptance testing is not required; refer to LANL Master Specification Section 26 0813.

*****************************************************************************************************

- Coordinate inspections and tests with those required by Section 26 0813 – Electrical Acceptance Testing.

- After completing installation, cleaning, and testing, touch-up scratches and mars on finish to match original finish.

MANUFACTURER'S FIELD SERVICE:

- Provide the services of a factory trained representative from the MCC manufacturer to inspect and certify the installation and to oversee energizing and testing.

- Manufacturer’s representative shall certify in writing that each MCC has been installed, adjusted, and tested in accordance with the manufacturer’s recommendations.

- Provide one full work day of training for up to three owner’s representatives at the project site.  A manufacturer’s qualified representative shall conduct training session.  The training program shall consist of instruction on the operation and maintenance of the MCC, starter units, and other major components.

END OF SECTION

*****************************************************************

Do not delete the following reference information:

*****************************************************************

FOR LANL USE ONLY

This project specification is based on LANL Master Specification 26 2419 Rev. 3, dated September 14, 2009.