SECTION 26 2713

ELECTRICITY Metering

*************************************************************************************************************

LANL MASTER SPECIFICATION

Available online at http://engstandards.lanl.gov

This template must be edited for each project.  In doing so, specifier must add job-specific requirements.  Brackets are used in the text to indicate designer choices or locations where text must be supplied by the designer.  Once the choice is made or text supplied, remove the brackets.  The specifications must also be edited to delete specification requirements for processes, items, or designs that are not included in the project - and specifiers’ notes such as these.  Additional tailoring requirements are contained in ESM Chapter 1 Section Z10 Att. F, Specifications.

To seek a variance from requirements in the specifications that are applicable, contact the Engineering Standards Manual Electrical POC. Please contact POC with suggestions for improvement as well.

When assembling a specification package, include applicable specifications from all Divisions, especially Division 1, General requirements.

Specification developed for ML-4 projects.  For ML-1, 2, and 3 applications, additional requirements and independent reviews should be added if increased confidence in procurement or execution is desired; see ESM Chapter 1 Section Z10 Specifications and Quality requirements.

NOTE:  Metering is required when (1) buildings are 5000 square feet or more or (2) the Main or Service is 400 Amps or greater.

Electrical systems connected to the LANL distribution system but billed for electrical services by LA County are not covered by this Section.

*************************************************************************************************************

GENERAL

Section Includes

*************************************************************************************************************

Edit list to match project requirements.

*************************************************************************************************************

Multi-function, digital electrical meter

Test switches.

Instrument transformers.

Meter cabinets.

*************************************************************************************************************

Edit the following article match Project requirements.

************************************************************************************************************

LANL-PERFORMED WORK

LANL Utilities will inspect, test, program, and adjust the meter, meter wiring, Ethernet communication wiring, and Ethernet communications interface.

SUBMITTALS

Submit the following:

Catalog data and manufacturer's technical data.  Provide catalog sheets showing ratings, dimensions, and enclosure details.

Installation instructions indicating application conditions and limitations of use stipulated by Product testing agency specified under Regulatory Requirements.  Include instructions for storage, handling, protection, examination, preparation, installation, and starting of Product.

Operation and maintenance instructions.

REGULATORY REQUIREMENTS

Conform to requirements of the National Electrical Code (NEC).

Conform to requirements of ANSI C12.1, American National Standard Code for Electricity Metering.

Furnish products listed and labeled by a Nationally Recognized Testing Laboratory (NRTL)

COORDINATION

*************************************************************************************************************

Edit the following article match project requirements. Delete A if metering will be installed in metering cabinets.

*************************************************************************************************************

Coordinate installation of metering components in the service, or main, [switchboard] [switchgear assembly].

Coordinate the features of the meter and associated instrument transformers with the ratings and characteristics of the circuit to be metered.

*************************************************************************************************************

Edit the following article match project requirements. Delete C if a socket-mounted single-phase watt-hour meter is installed.

*************************************************************************************************************

Provide not less than 14 working days’ notice to LANL STR to arrange for LANL Utilities to inspect, program, and test the meter prior to Project final inspection.

EXTRA MATERIALS

Furnish spare fuses—not less than one set of three of each size and type.

Receiving, Storing and Protecting

Receive, store, and protect, and handle products according to NECA 1, Standard Practices for Good Workmanship in Electrical Construction.

PRODUCTS

  - PRODUCT OPTIONS AND SUBSTITUTIONS

Substitutions are not allowed on the meter itself.  For other products, see Section 01 2500.

MULTI-FUNCTION DIGITAL ELECTRICAL METER

Provide addressable multi-function, microprocessor-based, digital electrical meter(s) as indicated on the Drawings.  Meter shall meet the following standards:

Be NRTL-listed to UL 508 Standard for Safety Industrial Control Equipment.

Meet requirements of ANSI C12.16, American National Standard for Solid-State Electricity Meters.

Meet NEMA C12.20, Electricity Meters 0.2 and 0.5 Accuracy Classes, class 0.5S for energy revenue metering.

Setup parameters required for the meter shall be stored in non-volatile memory and retained in the event of a control power interruption.  Any battery used to provide non-volatile memory must be serviceable from the front of the meter.

Manufacturer:  Square D. Contact LANL UI Metering at umetering@lanl.gov for current meter selection/standard. No substitution.

*************************************************************************************************************

Edit the following article to match Project requirements.  Adequate instrument transformers may exist in retrofit applications. Instrument transformers are not used with the specified single-phase meter. Delete this article if not needed.

*************************************************************************************************************

INSTRUMENT TRANSFORMERS

Provide current and potential transformers, conforming to NEMA EI 21.1 and ANSI C57.13, metering accuracy class 0.3, of suitable ratio and burden for specified metering.

Provide current transformers (CT) having 5 Amp secondary and a continuous current rating factor of not less than 1.33.

Current transformers for low voltage circuits (600 V and less) shall have 10 kV BIL.  Current transformers for 13.8 kV circuits shall have 110 kV BIL.

Provide with window opening adequate for the conductors or bus bars.

*************************************************************************************************************

Edit the following articles to match Project requirements.  Select CT to match system voltage and current.

*************************************************************************************************************

Manufacturer: ABB

Type CMS, through 200:5 at 600 V or less.

Type CMF, through 1200:5 at 600 V or less.

Type CMV, through 3000:5 at 600 V or less.

Type CLC, through 4000:5 at 600 V or less.

Type CLE, through 5000:5 at 600 V or less.

Type KIR-11, indoors at 13.8 kV.

Type KOR-11, outdoors at 13.8 kV.

Type KON-11, outdoors at 13.8 kV.

*************************************************************************************************************

Edit the following article to match Project requirements.  The specified multi-function digital meter does not require potential transformers when connected to a 480Y/277 V system.

*************************************************************************************************************

Provide potential transformers (PT) having 120 VAC secondary.

Potential transformers for low voltage circuits (600 V and less) shall have 10 kV BIL.  Potential transformers for 13.8 kV circuits shall have 110 kV BIL.

*************************************************************************************************************

Edit the following article to match Project requirements.  Select PT to match system voltage.

*************************************************************************************************************

Manufacturer: ABB

Type VIZ-11 with 2 primary fuses for 13.8 kV system indoors

Type VOY-11 for 13.8 kV system outdoors

Type PPW for 480 V system

*************************************************************************************************************

Edit the following article to match Project requirements.  Adequate test switches and plugs may exist in retrofit applications. Test switches and plugs are not required with the specified single-phase meter. Delete this article if not needed.

*************************************************************************************************************

TEST SWITCHES AND PLUGS

Provide semi-flush mounted test switches in meter potential and current circuits to facilitate testing of the meter installation and also external connection of additional portable metering equipment.

Provide test switches that comply with ANSI C12.9 and automatically short circuit current transformer circuits when the switches are opened preparatory to inserting the test plug.

Test switch shall have enough potential and shorting type current poles as are needed by the number of potential transformers and current transformers being used.

Provide plastic cover for each test switch.

Provide matching test plugs designed for in-service testing.

Manufacturers: States “Type FMS”.

*************************************************************************************************************

Edit the following article to match Project requirements.  Delete if there is no three-phase metering.

*************************************************************************************************************

POTENTIAL CIRCUIT FUSES

Provide UL Class CC, time-delay, 600 V, 3-ampere fuses to protect each potential lead to the meter.

Provide each fuse with a cover having a blown-fuse indicator.

Manufacturer: Bussman “Type FNQ-R fuses, BC Series fuse blocks, and SAMI-7I fuse covers.”

*************************************************************************************************************

Edit the following article to match Project requirements.  Delete on low-voltage systems.

*************************************************************************************************************

For indoor medium-voltage metering installations, protect the primary of each potential transformer with indoor, current-limiting, 1/2 Amp, 14,400 V fuses having blown fuse indication.  Manufacturer: S&C “Fusistor.”

*************************************************************************************************************

Edit the following article to match Project requirements.  Delete on low-voltage systems.

*************************************************************************************************************

For outdoor medium-voltage metering installations, protect the primary of each potential transformer with outdoor, 1 Amp, 14,400 V power fuses.  Manufacturer: S&C “SMD-20 with SMU-20 fuse unit”.

CURRENT TRANSFORMER SHORTING BLOCK

Provide 600v, 30A, 6-terminal CT shorting block to isolate all CT circuits to meter.

WIRING AND TERMINATIONS

Current transformer secondary circuits: TYPE SIS SWITCHBOARD WIRE stranded copper.  Use 12 AWG for circuits less than 50 ft.; when 50 ft or more, use 10 AWG.

Potential transformer secondary circuits:  use 12 AWG, Type, TYPE SIS SWITCHBOARD WIRE stranded copper,

Use crimp-on, nylon-insulated, insulation-grip, brazed-seam terminals for instrument wiring as follows:

On Nutted studs:  Use ring tongue terminals.  Manufacturer: Burndy “Type TN” for all current circuits.

On Barrier terminal strips: Use flanged fork terminals.  Manufacturer: Burndy “YAE-Z” for potential circuits.

On DIN-type terminal blocks: Use pin terminals.  Manufacturer: 3M “MNG-P”.

Use 18 AWG shielded, twisted pair, Belden 8723 cable for RS-485 connections per meter manufacturer recommendations.

*************************************************************************************************************

Edit the following article to match Project requirements.  Use meter cabinets for retrofit applications or where there is insufficient space to mount the meter and test switches in the service entrance panelboard or switchgear.  Meter cabinet is not needed for a single-phase, socket-mounted meter. Delete article if not needed.

*************************************************************************************************************

METER CABINETS

Provide a metal current transformer (CT) cabinet with hinged door to house the meter test switches, fuse blocks, [potential transformers,] current transformers, and CT shorting block.

Minimum cabinet size: 36” high, 30” wide, 11” deep.

Manufacturer: Hoffman A-363011HCT

Provide a meter cabinet with hinged door to house the meter module, display module, communications interfaces, and accessories.

Minimum cabinet size: 12” high, 12” wide, 6” deep.

Manufacturer: Hoffman A-12R126HCLO.

Outdoor installations shall be rated NEMA 3R minimum with a door-in-door enclosure (for meter display protection)

EXECUTION

*************************************************************************************************************

Delete the following article when existing construction is not affected.

*************************************************************************************************************

  - EXISTING WORK

Maintain access to existing meters and other installations remaining active and requiring access. Modify installation or provide access panel.

Clean and repair existing, LANL-acceptable meters and associated cabinets, instrument transformers and test blocks to remain or to be reinstalled.

EXAMINATION

Examine surfaces to receive meters and associated cabinets, instrument transformers and test blocks for compliance with installation tolerances and other conditions affecting performance of the raceway system.  Do not proceed with installation until unsatisfactory conditions have been corrected.

INSTALLATION

Install metering equipment according to manufacturer's instructions.  Have the manufacturer’s installation instructions available at the construction site.

Tighten electrical connectors and terminals according to manufacturers published torque-tightening values.  Where manufacturer's torque values are not furnished, use those specified in UL 486A.

*************************************************************************************************************

Edit the following article to match project requirements.

*************************************************************************************************************

Identify meter, [test switches,] [instrument transformers,] and meter wiring according to Section 26 0553, Identification for Electrical Systems. [Install voltage and arc-flash warning labels on cover of instrument transformer cabinet.]

*************************************************************************************************************

Use the following article when instrument transformers will NOT be installed within a service, or main, switchboard or switchgear assembly. Provide sufficient space adjacent to the service, or main, equipment for the CT cabinet and meter cabinet. Delete this article if not required.

*************************************************************************************************************

Install CT cabinet and meter cabinet adjacent to service, or main, equipment.

Install 3/4” plywood backboard painted with two coats of fire-retardant paint in the CT cabinet.

Mount current transformers on plywood backboard in the CT cabinet; position transformers to minimize stress from power conductors.

Mount potential circuit fuse block and CT shorting block on plywood backboard in the CT cabinet.

Recess mount meter test switches in current transformer CT cabinet door.

Locate meter cabinet so display is approximately 60 inches above the floor.

Interconnect metering components as indicated on the Drawings.

*************************************************************************************************************

Use the following article when instrument transformers will be installed within a service, or main, switchboard or switchgear assembly. Coordinate this article with Section 26 2300 – Low-Voltage Switchgear or Section 26 2413 – Switchboards as applicable. Delete this article if not required.

Coordinate with NIE.  If the work indicated in 3.3 H is performed by NIE, delete.

*************************************************************************************************************

Install metering components within the electrical service, or main, switchgear. Refer to [Section 26 2300 – Low-Voltage Switchgear] [Section 26 2413 – Switchboards].

Install potential transformers and associated potential fuses in dedicated potential transformer compartment.

Install current transformers on main bus in accordance with switchgear manufacturer’s standard details.

Install meter in a dedicated metering compartment.

Recess mount meter test switches in switchgear metering compartment door.

Locate meter display on switchgear metering compartment door approximately 60 inches above the floor.

Interconnect metering components as indicated on the Drawings.

Provide control power to meter in accordance with the manufacturer’s instructions.

Use a dedicated, fuse-protected, 120 v circuit or a dedicated, fuse-protected, control power transformer if potential transformers are required for the metering voltage inputs.

Control power may be derived from the fuse-protected metering voltage inputs when potential transformers are not required.

Wire current and potential leads through test switch.

Install fuse protection in the potential leads on the line side of the test switch.

Use shorting-type switches for the current transformer leads.

[Provide communications connection between the building telecommunications system and the Ethernet port associated with the meter.

Install conduit pathway for communications cables from the [meter cabinet] [switchboard or switchgear metering cubicle] to within 1 ft. of the telecommunications outlet.

Install suitable communications cables and terminations.

Connect meter to telecommunications outlet using a CAT-6 cord.]

FIELD QUALITY CONTROL

Inspect accessible components for cleanliness, mechanical, and electrical integrity, and for presence of damage or deterioration before energizing.

LANL STR, Construction Supervisor, or Job Superintendent will contact the Utilities and Infrastructure group at least 7 days before the completion of the project so that UI can inspect, test, program and adjust the meter, meter wiring, and communications interface.

Correct deficiencies in material, wiring, or installation that may be discovered.

After completing installation, cleaning, and testing, touch-up scratches and mars on finish to match original finish.

END OF SECTION

**********************************************************************

Do not delete the following reference information.

**********************************************************************

THE FOLLOWING STATEMENT IS FOR LANL USE ONLY

This project specification is based on LANL Master Specification 26 2713 Rev. 5, dated August 31, 2020.