SECTION 26 2726

WIRING DEVICES

*************************************************************************************************************

LANL MASTER SPECIFICATION

Available online at http://engstandards.lanl.gov			

This template must be edited for each project.  In doing so, specifier must add job-specific requirements.  Brackets are used in the text to indicate designer choices or locations where text must be supplied by the designer.  Once the choice is made or text supplied, remove the brackets.  The specifications must also be edited to delete specification requirements for processes, items, or designs that are not included in the project -- and specifier’s notes such as these.  To seek a variance from requirements in the specifications that are applicable, contact the Engineering Standards Manual Electrical POC. Please contact POC with suggestions for improvement as well.

When assembling a specification package, include applicable specifications from all Divisions, especially Division 1, General requirements.

Specification developed for ML-4 projects.  For ML-1, 2, and 3 applications, additional requirements and independent reviews should be added if increased confidence in procurement or execution is desired; see ESM Chapter 1 Section Z10 Specifications and Quality Sections.
*************************************************************************************************************

GENERAL

SUMMARY

SECTION INCLUDES

Receptacles

Snap switches

Wallbox dimming controls

Wall plates

Multi-outlet assemblies

Occupancy sensing lighting controls

Occupancy sensing lighting/receptacle control system.

LANL PERFORMED WORK

None

SUBMITTALS

Submit the following:

Catalog Data

Wiring Diagrams

QUALITY ASSURANCE

Comply with the National Electrical Code (NEC).

Furnish products listed and labeled by a nationally recognized testing laboratory (NRTL) for the application, installation condition, and the environments in which installed.

Manufacturers of products addressed in this Section shall maintain an ISO 9001 or ISO 9002 certification.

RECEIVING, STORING, AND PROTECTING

Receive, store, and protect, and handle products according to NECA 1, Standard Practices for Good Workmanship in Electrical Construction.

COORDINATION

Coordinate with other work, including painting, electrical boxes and wiring installations, to interface installation of wiring devices with other work.

Field locations of walls, partitions, doors, windows and equipment may vary from locations shown on the Drawings. Prior to locating sleeves, boxes and chases for roughing-in of conduit and equipment, coordinate with other trades to determine exact field location of the above items. Verify direction of door swings so that local switches are properly located on the strike side of the doorway.

*************************************************************************************************************

Edit the following article to match Project requirements.

*************************************************************************************************************

Coordinate wiring device colors with [Architect][Interior Designer][Facility Manager][  ].

Coordinate receptacle requirements for items of equipment provided to the Project under other sections of this Specification or by the Owner.

PRODUCTS

  - PRODUCT OPTIONS AND SUBSTITUTIONS

Alternate products may be accepted; follow Section 01 2500, Substitution Procedures.

RECEPTACLES

Provide back and side wired, screw pressure terminal, straight-blade and locking type, receptacles as indicated on the drawings.

Receptacles shall meet the performance and design requirements of Federal Specification WC596 and UL Standard 498, Electrical Attachment Plugs and Receptacles.

Receptacle configurations shall be in accordance with NEMA WD 6.

Catalog numbers in this article do not indicate receptacle color; see FINISHES article below.

For 120 volt convenience receptacles connected to general purpose 20 amperes branch circuits, provide straight-blade NEMA 5-15R, 15 amperes, 125 volts, grounding duplex receptacles. Receptacle mounting strap, ground terminal, and ground contacts shall be formed from one piece of brass alloy.  Manufacturer: Hubbell “HBL5262”.

Where indicated on the Drawings for special-purpose 120 volt duplex receptacles connected to 20 amperes branch circuits, provide straight-blade NEMA 5-20R, 20 amperes, 125 volts, grounding duplex receptacles. Receptacle mounting strap, ground terminal, and ground contacts shall be formed from one piece of brass alloy.  Manufacturer: Hubbell “HBL5362”.

For 120 volt receptacles connected to individual 20 amperes branch circuits provide straight-blade NEMA 5-20R, 20 amperes, 125 volts, grounding single receptacles. Receptacle mounting strap, ground terminal, and ground contact shall be formed from one piece of brass alloy. Manufacturer: Hubbell “HBL5361”.

For 120 volt receptacles connected to individual 15 amperes branch circuits provide straight-blade NEMA 5-15R, 15 amperes, 125 volts, grounding single receptacles. Receptacle mounting strap, ground terminal, and ground contact shall be formed from one piece of brass alloy. Manufacturer: Hubbell “HBL5261”.

For computer or instrument 120 volt circuit receptacles connected to isolated ground 20 amperes branch circuits provide straight-blade NEMA 5-20R, 20 amperes, 125 volts, isolated grounding duplex receptacles with orange triangle on face. Manufacturer: Hubbell “IG5362”.

For computer or instrument 120 volt circuit receptacles connected to individual isolated ground branch circuits provide straight-blade NEMA 5-20R, 20 amperes, 125 volts, isolated grounding single receptacles with orange triangle on face. Manufacturer: Hubbell “IG5361”.

For ground fault circuit interrupter (GFCI) receptacles provide straight-blade NEMA 5-15R, 15 amperes, 125 volts, grounding, “feed through” type, self-testing GFCI, weather-resistant, duplex receptacle that meet the requirements of UL Standard 943, Ground Fault Circuit Interrupters. Provide units that can be installed in a 2-3/4-inch deep outlet box without an adapter. Manufacturer: Hubbell “GFR5262SG.”

For integral surge-protected 120 volt convenience receptacles connected to general purpose branch circuits provide straight-blade NEMA 5-15R, 15 amperes, 125 volts, grounding duplex receptacles that meet the requirements of UL 1449 3rd Edition. Receptacle mounting strap, ground terminal, and ground contacts shall be formed from one piece of brass alloy. Receptacle shall include an LED to indicate power and surge protection status and an audible alarm with silencer to indicate loss of surge protection. Manufacturer: Hubbell “HBL5262SA”.

Provide straight-blade and twist lock receptacles for special applications as indicated on the Drawings.

Where items of equipment are provided to the Project under other sections of this specification or by LANL, provide a compatible receptacle for the cap or plug and cord of the equipment.

*************************************************************************************************************

Edit the following article to match Project requirements; delete if not required. Match devices to plug connectors for LANL furnished equipment.

*************************************************************************************************************

RECEPTACLES, INDUSTRIAL HEAVY DUTY

For NRTL listed equipment furnished with cords and attachment plugs configured to the current edition of NEMA WD 6, provide the corresponding receptacles. Provide receptacles that meet the performance and design requirements of Federal Specification WC596 and UL Standard 498, Electrical Attachment Plugs and Receptacles. For equipment not furnished with cords and attachment plugs conforming to NEMA WD 6, provide receptacles and matching plugs as specified below.

For 20, 30, 60, and 100 ampere heavy duty receptacle outlets located in dry, damp, or wet locations provide pin and sleeve type receptacles that are color coded and uniquely configured to the particular circuit voltage and current rating.

Pin and sleeve receptacles shall be NRTL listed to UL Standard 1682, Plugs, Receptacles, and Cable Connectors of the Pin and Sleeve Type and UL Classified to IEC Standards 309-1 and 309-2, Plugs, Socket Outlets, and Couplers for Industrial Purposes, and Series II rated for voltages and services.

Provide a back box suitable for each particular receptacle device and installation location.

Where indicated on the Drawings provide 20, 30, 60, and 100 ampere pin and sleeve receptacles with safety interlocks that will prevent making or breaking the receptacle connection under load.

For each receptacle provide a matching plug.

Manufacturer: Pass & Seymour “IEC 309 Industrial Products”

*************************************************************************************************************

Edit the following article to match Project requirements; delete if not required.

*************************************************************************************************************

RECEPTACLES IN HAZARDOUS (CLASSIFIED) LOCATIONS

Provide receptacles for hazardous locations, as indicated on the drawings, that comply with the requirements of NEMA Standard FB 11, Plugs, Receptacles, and Connectors of the Pin and Sleeve Type for Hazardous Locations and UL Standard 1010, Receptacle-Plug Combinations for Use in Hazardous (Classified) Locations.

*************************************************************************************************************

Edit the following article to match Project requirements; delete if not required.

*************************************************************************************************************

PENDANT/CORD CONNECTOR DEVICES

Provide matching, locking type, plug receptacle body connector, NEMA L5-20P and L5-20R, heavy-duty grade for pendant cords as indicated on the Drawings.

Provide connector bodies fabricated from nylon or polycarbonate with screw-open cable-gripping jaws and provision for attaching an external cable grip.

Provide external cable grips of the woven wire mesh type made of high-strength galvanized-steel wire strands, matched to cable diameter and with attachment provision designed for the corresponding connector.

*************************************************************************************************************

Edit the following article to match Project requirements. Refer to LANL Engineering Standards Manual Section D5020 for guidance.

*************************************************************************************************************

Cord shall be [600] [300] volt insulated, stranded copper conductors, with type [SO] [SOO] [SEO] [STO] [SJO] [SJOO] [SJEO] [SJTO] [G] [W] jacket and rated for [105 degree C] [90 degree C].  Grounding conductor not less than that required by the NEC and shall have green insulation. Conductor ampacity shall be equipment rating plus 25 percent minimum.

*************************************************************************************************************

Edit the following article to match Project requirements; delete if not required.

*************************************************************************************************************

CORD AND PLUG SETS

Provide cord and plug sets that match voltage and current ratings and number of conductors to requirements of the equipment being connected.

*************************************************************************************************************

Edit the following article to match Project requirements. Refer to LANL Engineering Standards Manual Section D5020 for guidance.

*************************************************************************************************************

Cord shall be [600] [300] volt insulated, stranded copper conductors, with type [SO] [SOO] [SEO] [STO] [SJO] [SJOO] [SJEO] [SJTO] [G] [W] jacket and rated for [105 degree C] [90 degree C].  Grounding conductor not less than that required by the NEC and shall have green insulation. Conductor ampacity shall be equipment rating plus 25 percent minimum.

Plug shall be male configuration with nylon or polycarbonate body and integral cable-clamping jaws. Match to cord and to receptacle type intended for connection.

SNAP SWITCHES

Provide single pole, double pole, three-way, four-way and illuminated handle snap switches as indicated on the Drawings.

Switches shall be rated 20 amperes, 120-277 volts AC, back and side wired, screw pressure terminal, quiet type AC switch with yoke grounding screw. Switches shall meet the performance and design requirements of UL Standard 20, General Use Snap Switches, and Federal Specification WS896.

Catalog numbers in this article do not indicate receptacle color; see FINISHES article below.

Manufacturer: Hubbell “HBL1220” series

********************************************************************************

Edit the following article to match Project requirements; delete if not required.

********************************************************************************

SNAP SWITCHES IN HAZARDOUS (CLASSIFIED) LOCATIONS

Provide snap switches for hazardous locations that comply with UL Standard 894, Switches for Use in Hazardous (Classified) Locations.

Switch shall be rated 20 ampere, 120-277 volt AC, and shall meet the performance and design requirements of NEMA Standard WD 1, General Purpose Wiring Devices, Federal Specification WS-896E, and UL Standard 20, General Use Snap Switches.

Manufacturer: Appleton “EDS”.

*************************************************************************************************************

Edit the following article to match Project requirements; delete if not required.

*************************************************************************************************************

WALLBOX DIMMING CONTROLS

Provide wallbox-mounted dimming control units that meet the requirements of UL 1492, Solid-State Dimming Controls. NRTL listing shall be specific to the type of load to be controlled.

Each dimming control shall include a solid-state full-wave dimmer, quiet on-off switch, audible noise filter, and electromagnetic noise filter.

Dimmer wattage rating shall exceed connected load by 30 percent minimum, unless otherwise indicated on the Drawings.

Dimmer control shall provide full-range, continuously adjustable light output. Dimmer control may be by vertical slider, toggle, or rotary knob.

Dimmer control shall include voltage compensation to stabilize light output with varying AC line voltage.

Dimmer switch shall be a mechanical air-gap switch that opens at the dimmer minimum setting, with single-pole or 3-way operation as required to control the lighting in each space.

Energized parts shall be behind a screw-secured cover. Removal of a snap-on cover shall not expose any energized parts to finger contact.

Provide wall box dimmers as indicated on the Drawings. Equip dimmers with electromagnetic filter to eliminate noise, RF and TV interference. Manufacturer: Lutron “Nova”

Provide fluorescent lamp dimmers for use with electronic ballasts specified in Section 26 5100, Interior Lighting.  Manufacturer: Lutron “Nova”

WALL PLATES

For flush mounted interior receptacles and wall switches, provide 0.032 inch thick (minimum) brushed 302/304 alloy stainless steel smooth wall plates that meet the requirements of Federal Specification WP-455A.  Manufacturer: Hubbell “S” series.

For surface mounted interior receptacles and switches, furnish galvanized steel 4 inch square raised surface covers. Receptacles installed in raised covers shall be secured by more than one screw. Manufacturer: RACO “800” series.

For GFCI receptacles in damp locations provide weatherproof, cast aluminum, hinged, self-closing device covers. Manufacturer: Hubbell “WP26” or “WPFS26”

For GFCI receptacles in wet locations provide cast aluminum, hinged, “extra duty” self-closing device covers that are weatherproof whether or not the attachment plug cap is inserted. Manufacturer: Hubbell “WP826” or “WP826H”

Provide single, multi-gang, and combination type wall plates that mate and match with corresponding wiring devices.

Use metal plate-securing screws to match plate finish.

*************************************************************************************************************

Edit the following article to match Project requirements; delete if not required. Use Section 
26 0533, Raceway and Boxes for Electrical Systems, where other than simple multi-outlet assemblies are required.

*************************************************************************************************************

MULTIOUTLET ASSEMBLY

Furnish multi-outlet assembly that meets the requirements of UL5 - Surface Metal Electrical Raceways and Fittings, and the NEC.

Components of assemblies shall be products of a single manufacturer designed to be used together to provide a complete matching assembly of raceways and receptacles.

*************************************************************************************************************

Select from the following articles to match Project requirements.  Standard stocked finish should be used in utilitarian spaces or where the raceway will be field painted.  Grey should be used where it will match or accent architectural finishes.  Stainless steel should be used only in laboratory spaces where there is the possibility of corrosion.

*************************************************************************************************************

[Furnish multi-outlet assembly surface metal raceway fabricated from cold rolled galvanized steel and coated with standard stocked baked enamel finish.]

[Furnish multi-outlet assembly surface metal raceway fabricated from cold rolled galvanized steel and coated with a gray baked enamel finish.]

[Furnish multi-outlet assembly surface metal raceway fabricated from Type 304 stainless steel.]

Raceway shall be of a two piece design with a metal base and a snap on metal cover.

Nominal dimensions of the assembled raceway shall be 1-1/4 inches wide by 3/4 inch high.

Furnish fittings required for a complete installation.

*************************************************************************************************************

Use the following article to match Project requirements for “standard” grounding receptacles.

*************************************************************************************************************

Provide multi-outlet assembly with pre-wired single NEMA 5-15R receptacles spaced [6] [9] [12] [18] inches on center and wired alternately to 2 circuits with 3 No. 12 AWG THHN insulated conductors and a green THHN insulated No. 12 AWG ground wire.

*************************************************************************************************************

Use the following article to match Project requirements for isolated ground power systems.

*************************************************************************************************************

[Provide isolated ground multi-outlet assembly with pre-wired single NEMA 5-15R isolated ground receptacles spaced [9] [12] [18] inches on center and connected to 1 circuit with 2 No. 12 AWG THHN insulated conductors and a green THHN insulated No. 12 AWG ground wire]

Manufacturer: Wiremold “Plugmold 2000.”

*************************************************************************************************************

Edit the following article to match Project requirements; delete if not required. In many cases the lighting control system described in the OCCUPANCY-SENSING LIGHTING/RECEPTACLE CONTROL SYSTEM article will be necessary due to the complex control system required by ASHRAE/IES Standard 90.1-2010.

*************************************************************************************************************

OCCUPANCY-SENSING LIGHT SWITCHES

For each private office with less than 400 square feet area, provide an NRTL-listed, dual voltage (120 and 277 volts), passive infrared automatic occupancy-sensing wall switch with 180 degree coverage, built-in light level sensor, adjustable time delay, adjustable sensitivity, and a switching technology that is suitable for electronic ballast inrush currents. Device shall have dual manual buttons and dual relays for user-controlled dual-level lighting switching. Light level sensor shall hold off the second relay when adequate daylighting is present in the office. Relay contacts shall be rated for at least 1200 watts ballast load at 277 volts. Manufacturer: WattStopper “PW-200-U.”

For each private office with greater than 400 square feet area, provide an NRTL-listed, ceiling-mount combination passive-infrared/ultrasonic automatic sensor with built-in light level sensor, adjustable time delay, and adjustable sensitivity. Provide universal voltage power pack to derive operating voltage for sensor and to switch 20 amperes of ballast-type lighting load; power pack shall be suitable for use in air-handling plenums. Where indicated on the Drawings provide auxiliary relay pack for daylighting control. Manufacturer: WattStopper “DT-300-U” with “BZ-U” series power pack.

For open office and laboratory areas provide one NRTL-listed, ceiling mount ultrasonic sensor per 900 square feet or fraction thereof. Provide universal voltage power pack to derive operating voltage for sensor and to switch 20 amperes of ballast-type lighting load; power pack shall be suitable for use in air-handling plenums. Manufacturer: WattStopper “WT-2205” with “BZ-U” series power pack.

For each conference room with less than 400 square feet area, provide an NRTL-listed, dual voltage (120 and 277 volts), passive infrared occupancy-sensing wall switch with 180 degree coverage, built-in light level sensor, adjustable time delay, adjustable sensitivity, and a switching technology that is suitable for electronic ballast inrush currents. Device shall have dual manual buttons and dual relays for user-controlled dual-level lighting switching. Relay contacts shall be rated for at least 1200 watts ballast load at 277 volts. Manufacturer: WattStopper “PW-200-U.”

For each conference room with greater than 400 square feet area provide one NRTL-listed, ceiling-mount combination passive-infrared/ultrasonic automatic sensor per 900 square feet or fraction thereof to control the general lighting. Provide sensor having adjustable time delay and adjustable sensitivity. Provide universal voltage power pack to derive operating voltage for sensor and to switch 20 amperes of ballast-type lighting load; power pack shall be suitable for use in air-handling plenums. Manufacturer: WattStopper “DT-305-U” with “BZ-U” series power pack.

For each computer room provide one NRTL-listed, ceiling-mount combination passive-infrared/ultrasonic automatic sensor per 1000 square feet or fraction thereof. Provide with adjustable time delay and adjustable sensitivity. Provide universal voltage power pack to derive operating voltage for sensor and to switch 20 amperes of ballast-type lighting load; power pack shall be suitable for use in air-handling plenums. Manufacturer: WattStopper “DT-305-U” with “BZ-U” series power pack.”

For each break room, file room, copy machine room, or utility room provide an NRTL-listed, ceiling-mount combination passive-infrared/ultrasonic automatic sensor with adjustable time delay and adjustable sensitivity. Provide universal voltage power pack to derive operating voltage for sensor and to switch 20 amperes of ballast-type lighting load; power pack shall be suitable for use in air-handling plenums. Manufacturer: WattStopper “DT-305-U” with “BZ-U” series power pack.”

For each restroom provide an NRTL-listed, ceiling mount ultrasonic sensor. Sensor shall have isolated relay contacts for interlocking with HVAC system controls. Provide universal voltage power pack to derive operating voltage for sensor and to switch 20 amperes of ballast-type lighting load; power pack shall be suitable for use in air-handling plenums. Manufacturer: WattStopper “WT-1100” with “BZ-U” series power pack.

For each corridor provide one NRTL-listed, ceiling mount ultrasonic sensor per 90 ft or smaller segment. Provide universal voltage power pack to derive operating voltage for sensor and to switch 20 amperes of ballast-type lighting load; power pack shall be suitable for use in air-handling plenums. Manufacturer: WattStopper “WT-2255” with “BZ-U” series power pack.

For each stairwell by each door provide one NRTL-listed, ceiling mount ultrasonic sensor. Provide universal voltage power pack to derive operating voltage for up to 3 sensors and with Form C normally open and normally closed contacts configured to switch 3 amperes of ballast-type lighting load in a fail-on configuration. Manufacturer: WattStopper “WT-600” with “A277C-P” 277 V or “A120C-P” 120 V series power pack.

Catalog numbers in this article do not indicate device color; see FINISHES article below.

*************************************************************************************************************

Edit the following article to match Project requirements; delete if not required. In many cases the lighting control system described in this article will be necessary due to the complex control system required by ASHRAE/IES Standard 90.1-2010.

*************************************************************************************************************

OCCUPANCY-SENSING LIGHTING/RECEPTACLE CONTROL SYSTEMS

For each room provide an integrated digital occupancy-sensing lighting/receptacle control system as described below and as indicated on the Drawings.

The occupancy-sensing lighting/receptacle control systems shall provide the lighting and receptacle control functions required by ASHRAE/IES Standard 90.1 (Chs 8 and 9 in 2010).

Each system shall consist of NRTL-listed components arranged in a free topology local network and interconnected with low-voltage digital communications cables. System components shall include but not be limited to the following as required to provide the required control functions:

Occupancy sensor(s),

Daylighting sensor(s) for spaces with windows of skylights,

Wall-mounted manual control(s),

Lighting circuit controller(s),

Receptacle circuit controller(s) for private offices, open offices, and computer classrooms,

Interconnecting cables,

Configuration and management tools.

Occupancy sensor(s) shall be suitable for the characteristics of the particular space. Set-points for sensitivity, time-out, and other parameters shall be adjustable from the floor using the configuration and management tool described below. The following are minimum requirements for sensor technology and density:

For each private office or conference room with less than 400 square feet area, provide a corner or ceiling mounted passive infrared occupancy sensor.

For each private office with greater than 400 but less than 1000 square feet area, provide a corner or ceiling mounted combination passive-infrared/ultrasonic occupancy sensor.

For open office and laboratory areas provide one ceiling mount ultrasonic occupancy sensor per 900 square feet or fraction thereof.

For each conference room with greater than 400 square feet area provide one ceiling mounted combination passive-infrared/ultrasonic occupancy sensor per 900 square feet or fraction thereof.

For each computer room provide one ceiling mounted combination passive-infrared/ultrasonic occupancy sensor per 1000 square feet or fraction thereof.

For each break room, file room, copy machine room, or utility room provide a ceiling mounted combination passive-infrared/ultrasonic occupancy sensor.

For each restroom provide a ceiling mounted ultrasonic occupancy sensor.

For each corridor provide one ceiling mount ultrasonic sensor per 90 ft or smaller segment.

Provide ceiling-mounted daylighting sensor(s) for each space with skylights or with side-lighting having an effective aperture of 10 percent or more:

Closed loop photosensor measures the ambient light level in order to automatically switch or dim one zone of lighting to maintain desired illuminance in the zone,

Set points and other parameters adjustable from the floor using the configuration and management tool described below.

Provide wall-mounted manual controls as required to accomplish the following:

Multi-level lighting control as described in this Section.

Dimming as indicated on the Drawings.

Multi-scene control as indicated on the Drawings.

Provide lighting circuit controllers with characteristics listed below to interface the digital occupancy-sensing lighting control system with the line-voltage room lighting circuits:

Input/output voltage: 120 or 277 V, 60Hz,

20 A combined load per controller,

One, two, or three output relays as required for room lighting control configuration,

Where dimming is indicated on the Drawings, 0 – 10 Vdc dimmer control signal,

Class 2 power supply for local network,

Zero-crossing circuitry for each relay for reliability and increased product life,

UL 2043 plenum rated.

For private offices, open offices, and computer classrooms provide receptacle circuit controllers with characteristics listed below to interface the digital occupancy-sensing lighting control system with the 120 V general power and computer power receptacle circuits as required by ASHRAE/IES Standard 90.1 (Ch 8 in 2010):

Input/output voltage: 120 VAC, 60Hz,

20 A load,

Class 2 power supply for local network,

Zero-crossing circuitry for relay for reliability and increased product life, and

UL 2043 plenum rated.

Provide a network bridge for each local network (i.e. room) to enable all of the local networks to be aggregated into a larger system, which, in turn, can be remotely managed from the building automation system (BAS) using the BACnet communications protocol. The network bridge may be integral to the lighting circuit controller described above.

Provide cables to interconnect components of the digital occupancy-sensing lighting control system:

Cat 5e cables with RJ45 connectors,

Plenum rated,

Couplers and splitters as necessary to complete interconnections.

Provide a configuration and management tool for each installation to:

Read, store, and modify configuration of occupancy and daylighting sensors,

Copy sensor settings from one room or installation to another,

Use setup and calibration data to prepare LEED documentation,

Monitor communications within a local network for troubleshooting purposes.

Manufacturer: Watt Stopper “DLM”

FINISHES

Wiring device catalog numbers do not designate device color. Provide devices with colors as follows:

Wiring devices connected to normal power system: Ivory or other device color as selected by Architect or Interior Designer, unless otherwise indicated or required by the NEC.

Wiring devices connected to isolated ground power system: Orange triangle on ivory or other device color as selected by Architect or Interior Designer.

Wiring devices connected to emergency or standby power system: Red.

TVSS devices: Surge symbol on ivory or other device color as selected by Architect or Interior Designer.

For renovation or expansion of existing facilities, provide devices and plates to match existing, remaining devices and plates.

EXECUTION

  - PREPARATION

Verify outlet boxes are installed at proper locations and heights.

Verify that outlet boxes in walls or ceilings are positioned in accordance with NEC Section 314.20.

Verify that outlet boxes for GFCI receptacle outlets are in locations that will be accessible after Owner-supplied equipment is in place.

Verify wall openings are neatly cut, comply with NEC Section 314.21, and will be completely covered by wall plates.

Verify branch circuit wiring installation is completed, tested, and ready for connection to wiring devices.

Clean debris from outlet boxes before installing devices.

INSTALLATION

Install products following manufacturer's instructions. Have the manufacturer’s installation instructions available at the construction site.

Install devices plumb, level, and secure.

Except as otherwise indicated on the Drawings, mount devices flush, with long dimension vertical, and grounding point of receptacles on top. Group adjacent switches and receptacles under single, multi-gang wall plates.

Do not use the duplex/split-wire break-off tabs in receptacles as circuit conductors for connecting downstream devices.

Cover devices and assemblies during painting.

Install wall plates on switch, receptacle, and blank outlets after painting is complete.

Install galvanized steel plates on outlet boxes and junction boxes in unfinished areas, above accessible ceilings, and on surface mounted outlets.

Install Class 2 wiring for occupancy-sensing lighting/receptacle control system in accordance with NEC Article 725.

Install a grounded conductor (neutral) to each switch/controller wall box for each controlled circuit.

Connect the designated neutral terminal/wire on an electronic lighting control device to the grounded (neutral) conductor for the controlled circuit. Do not use the equipment grounding conductor in place of the grounded conductor.

DUAL-LEVEL LIGHTING CONTROL

Provide dual-level lighting control or dimming control in spaces 100 square feet and larger except the following where only full ON-OFF control is required:

Public corridors,

Primary building entrances and lobbies,

Restrooms,

Mechanical, electrical, and telecommunications equipment rooms,

Storage rooms,

Spaces with only one luminaire with rated input power less than 100 W,

Spaces with an ASHRAE/IES Standard 90.1 lighting power allowance of less than 0.6 W/ft2, or

Spaces indicated on the Drawings as requiring 24-hour operation.

Coordinate manual controls with automatic controls so the manual control can reduce the lighting load by at least 50 percent in a reasonably uniform lighting pattern.

Coordinate multi-level lighting controls with daylighting apertures, such as windows.

Coordinate multi-level-lighting controls with luminaire ballasts specified in Section 26 5100, Interior Lighting System.

Stairwell Lighting Control

Install ultrasonic occupancy sensors and control relays and circuit luminaires to reduce stairwell lighting power by 50 percent within 30 minutes of all occupants leaving the controlled zone as required by ASHRAE/IES Standard 90.1.

Mount an occupancy sensor near each stair door. Locate sensors on the side wall of the stairwell above door height to detect opening the stairwell doors.

Connect occupancy sensor auxiliary contacts and control relay normally closed contacts in a “fail on” configuration.

AUTOMATIC RECEPTACLE CONTROL

In private offices, open offices, and computer classrooms connect 120 V receptacles to receptacle circuit controllers so not less than 50 percent of the receptacles will be switched off by occupancy sensing controls within 30 minutes of all occupants leaving the space as required by Chapter 8 of ASHRAE/IES Standard 90.1 (Ch 8 in 2010):

Receptacle control is not required for equipment indicated on the Drawings as requiring 24 hour operation.

Receptacle control is not required in spaces indicated on the Drawings where an automatic shutoff would endanger the safety of the room or building occupants.

Connect general-purpose and PC power receptacles to provide a uniform distribution of controlled receptacles.

Split-wire vertically mounted duplex receptacles so the top receptacle will be controlled and the bottom receptacle will be always on.

Split-wire horizontally mounted duplex receptacles so the left receptacle will be controlled and the right receptacle will be always on.

GROUNDING

Connect wiring device grounding terminal to branch circuit equipment grounding conductor.

Connect isolated ground receptacle grounding terminal to the isolated grounding conductor.

IDENTIFICATION

    - Identify wiring devices with circuit number as required in Section 26 0553, Identification for Electrical Systems.

    - Identify both ends of occupancy-sensing lighting/receptacle control system Class 2 control cables with wire markers indicating “from” and “to” information.

FIELD QUALITY CONTROL

Inspect each wiring device for defects before installing.

Operate each operable device at least six times with circuit energized; verify proper operation.

Test 15 and 20 ampere receptacles for proper polarity and ground continuity using an NRTL listed test device that impresses a momentary current of at least 15 amperes on the branch circuit conductors and equipment grounding path.

Test ground-fault circuit interrupter receptacle operation with both local and remote fault simulations according to manufacturer recommendations.

Verify that GFCI will trip at 5 ±1 mA current

Verify that GFCI does not trip at less than 1.8 mA current.

Replace damaged or defective wiring devices.

CLEANING AND ADJUSTING

Clean devices and wall plates. Replace stained or improperly painted wall plates or devices.

Adjust devices and wall plates to be flush and level.

*************************************************************************************************************

Edit the following article to match Project requirements; delete if not required.

*************************************************************************************************************

Adjust time-out controls each occupancy sensing light switches to the following settings:

Classrooms, private offices, open offices, laboratories, and restrooms: longest time out setting, but not more than 30 minutes.

Break rooms, storage rooms, and copy machine rooms: 5-minute time-out setting.

Conference rooms: 10-minute time-out setting.

Corridors and lobbies: 15-minute time-out setting.

*************************************************************************************************************

Edit the following article to match Project requirements; delete if not required.

*************************************************************************************************************

Adjust ambient light sensor in occupancy sensors to hold off or reduce the electric lighting when daylighting exceeds 80% of the design illuminance at the work area. (For example, in an office with a design illuminance of 50 footcandles, the ambient light sensor should keep the lights off as long as the daylighting exceeds 40 footcandles.

END OF SECTION

*********************************************************

Do not delete the following reference information:

*********************************************************

FOR LANL USE ONLY

This project specification is based on LANL Master Specification 26 2726 Rev. 4, dated November 10, 2011.