SECTION 26 2913

Enclosed Controllers

************************************************************************************************************

LANL MASTER SPECIFICATION

Available online at http://engstandards.lanl.gov.

This template must be edited for each project.  In doing so, specifier must add job-specific requirements.  Brackets are used in the text to indicate designer choices or locations where text must be supplied by the designer.  Once the choice is made or text supplied, remove the brackets.  The specifications must also be edited to delete specification requirements for processes, items, or designs that are not included in the project -- and specifier’s notes such as these.

To seek a variance from requirements in the specifications that are applicable, contact the Engineering Standards Manual Electrical POC. Please contact POC with suggestions for improvement as well.

When assembling a specification package, include applicable specifications from all Divisions, especially Division 1, General requirements.

Specification developed for ML-4 projects.  For ML-1, 2, and 3 applications, additional requirements and independent reviews should be added if increased confidence in procurement or execution is desired; see ESM Chapter 1 Section Z10 Specifications and Quality Sections.

Seismic:  If the enclosed controller isn’t exempt from seismic design per ASCE 7 paragraph 13.1.4 then, prior to attempting to edit this Section to be Project-specific, refer to Sections 26 0548.16, Seismic Controls for Electrical Systems, and 01 8734, Seismic Qualification of Nonstructural Components (IBC), as applicable. Refer to author notes that begin with “Seismic.”  Also, see the Seismic Specification Guide for Electrical (soon-to-be posted on LANL specs webpage) for guidance on properly editing this section.
*************************************************************************************************************

GENERAL

SECTION INCLUDES

AC motor control devices rated 600V and less that are not an integral part of equipment or motor control centers.

*************************************************************************************************************

Edit the following sections to match Project requirements; delete those not applicable to Project.

*************************************************************************************************************

Manual motor controllers for fractional horsepower motors.

Magnetic motor controllers, full-voltage, non-reversing.

Combination magnetic motor controllers, full-voltage, non-reversing.

*************************************************************************************************************

Seismic: If the enclosed controller is exempt from seismic design then delete both of the following subparagraphs.

- Otherwise, see the seismic-portion of the previous author note.

*************************************************************************************************************

RELATED SECTIONS

Section 01 8734, Seismic Qualification of Nonstructural Components (IBC), for requirements.

Section 26 0548.16, Seismic Controls for Electrical Systems, for [seismic-design criteria,] submittal requirements, devices for seismic restraint, and installation requirements for these devices.

ACTION SUBMITTALS

Submit the following:

Catalog data:  Submit manufacturer's technical data for each type of motor controller and starter, including data proving that materials comply with specified requirements. Provide catalog sheets showing voltage, controller size, ratings and size of switching and overcurrent protective devices, short circuit ratings, dimensions, and enclosure details.

Installation instructions:  Indicate application conditions and limitations of use stipulated by Product testing agency specified under Quality Assurance.  Include instructions for storage, handling, protection, examination, preparation, installation, and starting of Product.

Operation and maintenance instructions.

Test and Inspection Records: Submit records of inspections, tests, and adjustments performed under FIELD QUALITY CONTROL.

Wiring diagrams: Submit the following diagrams for each type of enclosed controller supplied:

Wiring diagram showing the relative locations of controller components and terminals.

Elementary diagram with components arranged in a “ladder” format to show sequence of operation of the devices.

QUALITY ASSURANCE

Comply with the National Electrical Code (NEC) for  installation requirements

Provide enclosed controllers listed and labeled by a nationally recognized testing laboratory (NRTL).

Receiving, Storing and Protecting

Receive, store, protect, and handle products according to NECA 1 - Standard Practices for Good Workmanship in Electrical Construction and NECA 230 - Standard for Selecting, Installing, and Maintaining Electric Motors and Motor Controllers.

COORDINATION

Coordinate the features of each enclosed controller with the ratings and characteristics of the supply circuit, the motor, the required control sequence, the duty cycle of the load, the pilot devices, and control circuit affecting controller functions. Provide controllers that are horsepower rated to suit the motor controlled.

SERVICE CONDITIONS

Enclosed controllers shall perform satisfactorily in the following service conditions without mechanical or electrical damage or degradation of operating characteristics:

Operating elevation of 7,500 feet above sea level.

Operating ambient temperature extremes of 32 to 104 degrees F.

Operating relative humidity: 0 to 80 percent, without condensation.

*****************************************************************************************************

Edit the following to match project requirements; use only for outdoor equipment.

*****************************************************************************************************

Maximum solar heat gain: 110 W/sq ft.

EXTRA MATERIALS

Furnish one spare for every five installed fuses, but not less than one set of three of each kind.

PRODUCTS

*************************************************************************************************************

For enclosed controllers that are not exempt from seismic, if Project Spec includes 26 0548.16, and if mounting and/or anchorage devices are to be used that differ from those specified in 26 0548.16, they must be described herein (in PART 2).

*************************************************************************************************************

  - PRODUCT OPTIONS AND SUBSTITUTIONS

Alternate products may be accepted; follow Section 01 2500 - Substitution Procedures.

*************************************************************************************************************

Seismic: Delete 2.2 if enclosed controller is exempt from seismic design.

Otherwise retain the section and edit its content based on the following:

- 	1st paragraph is for a controller that doesn’t have to operate/function post seismic event

- 	2nd paragraph is for a controller that must operate/ function after a seismic event (i.e., it’s a Designated Seismic System, or DSS).

- If paragraph applies, the “E” drawings for the controller shall also state that the controller is a Designated Seismic System

If paragraph applies, edit it in accordance with content of 26 0548.16 and/or 01 8734.

*************************************************************************************************************

SEismic Performance requirements

The enclosed controller shall remain in place without separation of any parts when subjected to the design basis earthquake [per Section 01 8734, Seismic Qualification of Nonstructural Components (IBC)] [as represented by the seismic forces derived from the criteria indicated [on the drawings] [in Section 26 0548.16, Seismic Controls for Electrical Systems]].

The enclosed controller is a Designated Seismic System and, as such, it shall remain in place and be fully operational following the design basis earthquake [per Section 01 8734, Seismic Qualification of Nonstructural Components (IBC)] [as represented by the seismic forces derived from the criteria indicated [on the drawings] [in Section 26 0548.16, Seismic Controls for Electrical Systems]].

  - General

Provide enclosed controllers that are NRTL-listed to UL 508 – Industrial Control Equipment and have a short circuit withstand rating that exceeds the fault current available at the controller line terminals

Provide enclosed controllers that conform to the requirements of NEMA ICS 2 - Industrial Control Devices, Controllers, and Assemblies

Provide enclosures in accordance with ANSI/NEMA ICS 6 - Enclosures for Industrial Controls and Systems with Type as required to meet conditions of installation.

  - FRACTIONAL HORSEPOWER MANUAL MOTOR CONTROLLERS

*************************************************************************************************************

Edit this part to match Project requirements; delete if manual motor starters are not required. Use manual motor starters to control single-phase 120 V fractional horsepower motors where automatic or remote control is not required.

*************************************************************************************************************

Provide general purpose, Class A, manually-operated, full-voltage controllers for AC fractional horsepower motors.

*************************************************************************************************************

Edit the following to match Project requirements.

*************************************************************************************************************

Provide starter with thermal overload unit, red pilot light, and [key] [toggle] operator.

Provide handle guard with provision for locking in the OFF position.

Manufacturers:

Allen-Bradley “Bulletin 600”

Eaton “Type MS”

Siemens “Class SMF”

Square D “Class 2510 Type F”.

  - MAGNETIC MOTOR CONTROLLERS – NON-REVERSING:

*************************************************************************************************************

Edit this part to match Project requirements; delete if magnetic, full-voltage, non-reversing controllers are not required.

*************************************************************************************************************

Provide general purpose, Class A, magnetic, full-voltage, non-reversing controllers for AC induction motors rated in horsepower.

*************************************************************************************************************

Edit the following to match Project requirements. Some special applications use 24 V controls.

*************************************************************************************************************

[Coil shall be of the encapsulated type.  Coil operating voltage shall be [24] [120] volts, 60 Hz.]

Provide controllers of size and number of poles as indicated on the Drawings.

Contacts shall be totally enclosed, double-break, silver-cadmium-oxide power contacts.  Contact inspection and replacement shall be possible without disturbing line or load wiring.

Contacts for 480 volt motor applications shall be rated at 600 volts

Contactor shall be suitable for at least the number of operations indicated in the NEMA AC-3 utilization category load-life profile for the contactor size.

Provide solid-state overload units with the following characteristics for motors rated less than 100 full-load amperes:

*************************************************************************************************************

Edit the following to match Project requirements; some motor/load combinations require a Class 10 (fast trip) or Class 30 (slow trip) start time characteristic instead of the standard Class 20. Consider a schedule of enclosed controllers on the Drawings if different requirements exist for different controllers.

*************************************************************************************************************

NEMA Class [10] [20] [30] tripping characteristics [as scheduled on the Drawings].

Field selectable motor full load current.

Ambient temperature insensitive.

Phase loss protection.

Manual reset after time delay.

Integral current transformers.

*************************************************************************************************************

Edit the following to match Project requirements; delete if no motors on Project are rated from 100 to 300 full-load amperes. Refer to Section D5020 in the LANL Engineering Standards Manual for overload protection for motors rated over 300 full-load amperes.

*************************************************************************************************************

Provide solid-state overload units with the following characteristics for motors rated from 100 to 300 full-load amperes:

*************************************************************************************************************

Edit the following to match Project requirements; some motor/load combinations require a Class 10 start-time characteristic.

*************************************************************************************************************

NEMA Class [10] [20] tripping characteristics [as scheduled on the Drawings].

Field selectable/adjustable overload trip current.

Phase unbalance and phase loss protection.

Manual or electric reset after time delay.

Current sensing using external current transformers with 5 ampere secondary.

*************************************************************************************************************

Edit the following to match Project requirements. Delete if auxiliary contacts are not required.

*************************************************************************************************************

Provide [one][two][  ] sets of NEMA ICS 2 field convertible auxiliary contacts in addition to the seal-in contact [as scheduled on the Drawings].

*************************************************************************************************************

Edit the following to match Project requirements. Delete control devices that are not required, but do not delete all control devices.

*************************************************************************************************************

Provide cover mounted, heavy duty, 22 mm or 30 mm, metal operator, oil tight pilot devices as listed below with NEMA ICS 2, Form Z, A600 rated contacts.

*************************************************************************************************************

Edit the following to match Project requirements. Use a rotary type selector switch on equipment that is required to re-start automatically after a power interruption (e.g., most HVAC equipment).

*************************************************************************************************************

Selector Switches:  Rotary type [as scheduled on the Drawings]

HAND-OFF-AUTO or ON-OFF-AUTO selector switch if controller is connected to automatic control system or may be in the future.

ON-OFF selector switch if controller is not connected to automatic control system.

*************************************************************************************************************

Edit the following to match Project requirements. Use push-button controls on equipment that is required to remain OFF after a power interruption (e.g., equipment requiring operator-assisted startup or having safety issues during startup).

*************************************************************************************************************

Push buttons: [as scheduled on the Drawings]

Flush, momentary-contact START pushbutton.

Flush, momentary-contact STOP pushbutton.

*************************************************************************************************************

Edit to match Project requirements. Delete if not required.

*************************************************************************************************************

Mushroom head, maintained-action, turn-to-release or pull-to-release EMERGENCY STOP pushbutton as indicated on the Drawings.

Push-to-test LED-type indicating lights:

Red RUNNING pilot light.

Green STOPPED pilot light.

Additional pilot lights as indicated on the Drawings.

Provide legend plates for pushbuttons, pilot lights and selector switches.

Provide externally operable manual reset operator.

*************************************************************************************************************

Edit the following to match Project requirements. Some special applications use 24V controls. Some applications may warrant specifying additional future control power transformer capacity.

*************************************************************************************************************

Provide a control power transformer [as scheduled on the Drawings] in each motor starter.  The transformer shall have [24][120] volt secondary and sufficient capacity to operate starter coil and all connected pilot, indicating and control devices, plus [20 percent][100 percent] spare capacity [as scheduled on the Drawings].  Provide fused primary and secondary.  Bond un-fused leg of secondary to enclosure.  Provide fuses or fuse holders with blown fuse indicators.

Manufacturers:

Allen-Bradley “Bulletin 509”

Eaton “A200” or “Freedom Series”

Siemens “Class 14”

Square D “Class 8536 Type S”.

  - CIRCUIT BREAKER TYPE COMBINATION MAGNETIC MOTOR CONTROLLERS - NON-REVERSING

*************************************************************************************************************

Edit this part to match Project requirements; delete if combination magnetic motor controllers are not required.

*************************************************************************************************************

Provide combination magnetic motor controllers with motor circuit protector disconnect and controller in a common enclosure.

Motor circuit protector shall conform to UL 485 and UL 487 – Molded Case Circuit Breakers, with an integral instantaneous magnetic trip in each pole.

Trip units shall be calibrated to coordinate with the actual locked-rotor current of the connected motor and the controller overload relays.

Provide motor circuit protectors that are factory assembled with the controller, interlocked with unit cover or door, and arranged to disconnect the controller.

Motor circuit protector shall have a color coded externally operated handle.  Operating handle shall give positive visual indication of ON-OFF with red and black color coding.  Include provisions for padlocking handle in the OFF position.

Provide motor circuit protectors rated 600 volts when used on 480 volt systems.

Provide general purpose, Class A, magnetic, full-voltage, non-reversing controllers for AC induction motors rated in horsepower.

*************************************************************************************************************

Edit the following to match Project requirements; some special applications use 24V controls. Consider a schedule of enclosed controllers on the Drawings if different requirements exist for different controllers.

*************************************************************************************************************

Coil shall be of the encapsulated type.  Coil operating voltage shall be [24] [120] volts, 60 Hz [as scheduled on the Drawings].

Provide controllers of size and number of poles as indicated on the Drawings.

Contacts shall be totally enclosed, double-break, silver-cadmium-oxide power contacts.  Contact inspection and replacement shall be possible without disturbing line or load wiring.

Contactor shall be rated for at least the number of operations indicated in the NEMA AC-3 utilization category load-life profile for the contactor size.

Wiring shall be “straight-through” with all terminals clearly marked.

Provide solid-state overload units with the following characteristics for motors rated up to 100 full-load amperes:

*************************************************************************************************************

Edit the following to match Project requirements; some motor/load combinations require a Class 10 or Class 30 start-time characteristic.

*************************************************************************************************************

NEMA Class [10] [20] [30] tripping characteristics

Field selectable motor full load current.

Ambient temperature insensitive.

Phase loss and phase unbalance protection.

Manual reset after time delay.

Integral current transformers.

*************************************************************************************************************

Edit the following to match Project requirements; delete if no motors on Project are rated from 100 to 300 full-load amperes. Refer to Section D5020 in the LANL Engineering Standards Manual for overload protection for motors rated over 300 full-load amperes.

*************************************************************************************************************

Provide solid-state overload units with the following characteristics for motors rated from 100 to 300 full-load amperes:

*************************************************************************************************************

Edit the following to match Project requirements; some motor/load combinations require a Class 10 (fast trip) or Class 30 (slow trip) start time characteristic instead of the standard Class 20. Consider a schedule of enclosed controllers on the Drawings if different requirements exist for different controllers.

*************************************************************************************************************

NEMA Class [10] [20] [30] tripping characteristics [as scheduled on the Drawings].

Field selectable/adjustable overload trip current.

Phase unbalance and phase loss protection.

Manual or electric reset after time delay.

Current sensing using external current transformers with 5 ampere secondary.

*************************************************************************************************************

Edit the following to match Project requirements; delete if auxiliary contacts are not required.

*************************************************************************************************************

Provide [one][two][  ] sets of NEMA ICS 2 field convertible auxiliary contacts in addition to the seal-in contact [as scheduled on the Drawings].

*************************************************************************************************************

Edit the following to match Project requirements. Delete control devices that are not required, but do not delete all control devices.

*************************************************************************************************************

Provide cover mounted, heavy duty, 22 mm or 30 mm, metal operator, oil tight pilot devices as listed below with NEMA ICS 2, Form Z, A600 rated contacts

*************************************************************************************************************

Edit the following to match Project requirements. Use a rotary type selector switch on equipment that is required to re-start automatically after a power interruption (e.g., most HVAC equipment).

*************************************************************************************************************

Selector Switches:  Rotary type [as scheduled on the Drawings]

HAND-OFF-AUTO or ON-OFF-AUTO selector switch if controller is connected to automatic control system or may be in the future.

ON-OFF selector switch if controller is not connected to automatic control system.

*************************************************************************************************************

Edit the following to match Project requirements. Use push button controls on equipment that is required to remain OFF after a power interruption (e.g., equipment requiring operator-assisted startup or having safety issues during startup).

*************************************************************************************************************

Push buttons: [as scheduled on the Drawings]

Flush, momentary-contact START pushbutton.

Flush, momentary-contact STOP pushbutton.

Mushroom head, maintained action, turn-to-release or pull-to-release EMERGENCY STOP pushbutton as indicated on the Drawings.

Push-to-test LED type indicating lights:

Red RUNNING pilot light.

Green STOPPED pilot light.

Additional pilot lights as indicated on the Drawings.

Provide legend plates for pushbuttons, pilot lights and selector switches.

Provide externally operable manual reset operator.

*************************************************************************************************************

Edit the following to match Project requirements. Some special applications use 24V controls. Some applications may warrant specifying additional future control power transformer capacity.

*************************************************************************************************************

Provide a control power transformer [as scheduled on the Drawings] in each motor starter.  The transformer shall have [24][120] volt secondary and sufficient capacity to operate starter coil and all connected pilot, indicating and control devices, plus [20][100] percent spare capacity.  Provide fused primary and secondary.  Bond un-fused leg of secondary to enclosure.  Provide fuses or fuse holders with blown fuse indication.

Manufacturer:

Allen-Bradley “Bulletin 513”

Siemens “Class 18”

Square D “Class 8539 Type S”.

EXECUTION

*************************************************************************************************************

For enclosed controllers that are not exempt from seismic, if Project Spec includes 26 0548.16, and if requirements associated with installation, testing, and inspection of mounting and/or anchorage devices differ from those requirements in 26 0548.16, they must be described herein (in PART 3).  Also, if this is applicable, identify special types of seismic-control devices required for each application using the same terminology used for those devices in PART 2.

*************************************************************************************************************

  - EXISTING WORK

*************************************************************************************************************

Delete this article when existing construction is not affected.

*************************************************************************************************************

Maintain access to existing enclosed motor controllers and other installations that are to remain active and to require access. Modify installation or provide access panel.

Clean and repair existing enclosed motor controllers that are to remain or be reinstalled, that are part of the project scope

  - EXAMINATION

Examine surfaces to receive control equipment for compliance with installation tolerances and other conditions affecting performance of the control system.  Do not proceed with installation until unsatisfactory conditions have been corrected.

  - INSTALLATION

Install motor control equipment where indicated on the Drawings and according to NECA 230 and the manufacturer's instructions. Manufacturer’s installation instructions shall be available at the construction site.

Mount with operating mechanism 5' above floor or as indicated on the Drawings.

*************************************************************************************************************

Edit the following to match Project requirements; refer to instructions in Section 26 0548 for a detailed description of the conditions where seismic controls are required.

*************************************************************************************************************

Install enclosed controllers plumb. Provide supports in accordance with the requirements of the following Sections:

Section 26 0529 – Hangers and Supports for Electrical Systems: applies to enclosed controllers that weigh 20 lb or less and have been assigned an importance factor of 1.0.

Section 26 0548.16 – Seismic Controls for Electrical Systems: applies to enclosed controllers that weigh more than 20 lb or have been assigned an importance factor greater than 1.0.

Remove temporary blocking of moving parts from controllers.

Tighten electrical connectors and terminals according to manufacturers published torque values.  Where manufacturer's torque values are not furnished, use those specified in UL 486E - Equipment Wiring Terminals for Use with Aluminum and/or Copper Conductors.

Set overload relays or install overload heater elements in motor controllers to match installed motor characteristics.

Provide neatly typed label inside each motor starter enclosure door identifying motor served, nameplate horsepower, full load amperes, code letter, service factor, and voltage/phase rating. Place label in clear plastic holder.

Connections

Ground and bond motor controllers and control devices as required in Section 25 0526, grounding and Bonding for Electrical Systems.

Install conduit connections to enclosed bus assemblies as required in Section 26 0533, Raceways and Boxes for Electrical Systems.

Install conductors as required in Section 26 0519, Low Voltage Electrical Power Conductors and Cables.

*************************************************************************************************************

Seismic:  Flexible connections (between the controller and other nonstructural components it’s associated with) are one of the requirements for the controller exemption from seismic design.  Ensure such connections are indicated on the drawings in the applicable location(s).

*************************************************************************************************************

Install flexible connections for enclosed controllers where shown on drawings

IDENTIFICATION

Identify enclosed controllers as required in Section 26 0553, Identification for Electrical Systems.

Provide Category I nameplate for each enclosed controller. Refer to Section 26 0553.

At indoor locations, mark floor in front of each enclosed controller to show NEC required working clearances according to Section 26 0553, where shown on approved construction documents.

Provide neatly typed label inside each motor starter enclosure door for each magnetic motor controller and each combination motor controller identifying the motor served, nameplate horsepower, full load amperes, code letter, service factor, and voltage/phase rating.

  - FIELD QUALITY CONTROL

Clean, inspect, test, adjust, and energize enclosed controllers in accordance with the manufacturer’s instructions and NECA 230.

Verify that the proper overloads are installed and set for the motor nameplate full load current and duty.

[Witness torqueing of power conductor terminations].

Verify proper operational response to control devices.

*************************************************************************************************************

Edit the following to match project requirements. Delete if formal electrical acceptance testing is not required; refer to LANL Master Specification Section 26 0813.

*************************************************************************************************************

Coordinate inspections and tests with those required by Section 26 0813, Electrical Acceptance Testing.

After completing installation, cleaning, and testing, re-touch scratches and mars on finish to match original finish.

END OF SECTION

*********************************************************

Do not delete the following reference information:

*********************************************************

THE FOLLOWING STATEMENT IS FOR LANL USE ONLY

This project specification is based on LANL Master Specification Section 26 2913 Rev. 3, dated August 24, 2017.