SECTION 26 2923

VARIABLE Frequency MOTOR Controllers

*************************************************************************************************************

LANL MASTER SPECIFICATION

Word file at http://engstandards.lanl.gov

This template must be edited for each project.  In doing so, specifier must add job-specific requirements.  Brackets are used in the text to indicate designer choices or locations where text must be supplied by the designer.  Once the choice is made or text supplied, remove the brackets.  The specifications must also be edited to delete specification requirements for processes, items, or designs that are not included in the project -- and specifier’s notes such as these.  To seek a variance from requirements in the specifications that are applicable, contact the Engineering Standards Manual Electrical POC. Please contact POC with suggestions for improvement as well.

When assembling a specification package, include applicable specifications from all Divisions, especially Division 1, General requirements.

Specification developed for ML-4 projects.  For ML-1, 2, and 3 applications, additional requirements and independent reviews should be added if increased confidence in procurement or execution is desired; see ESM Chapter 1 Section Z10 Specifications and Quality Sections.
*************************************************************************************************************

- GENERAL

SECTION INCLUDES

Configured adjustable frequency AC controllers (AFCs) for use with NEMA B design AC squirrel-cage induction motors.

LANL Performed Work

None

SUBMITTALS

Submit the following in accordance with project submittal procedures:

Catalog Data: Submit catalog data describing each type of AFC.  Include data substantiating that materials comply with specified requirements.  Provide catalog sheets showing voltage, controller size, ratings and size of switching and overcurrent protective devices, short circuit ratings, dimensions, and enclosure details.

Calculations:

Submit calculations showing de-rating and selection of each AFC for the specified altitude, ambient temperature, and carrier frequency.

If the total connected kVA of AFCs exceeds 15 percent of the self-cooled kVA rating of the facility service transformer submit evaluation of harmonic distortion at the point of common coupling (PCC) using computer simulation of the distribution system and connected AFCs.  The PCC for voltage distortion shall be at the secondary of the utilization voltage service transformers.  The PCC for current distortion shall be at the primary of the utilization voltage service transformers. Use procedures outlined in IEEE 519-1992, IEEE Recommended Practices and Requirements for Harmonic Control in Electric Power Systems.  Assume that all connected AFCs operating at 80% speed.

*************************************************************************************************************

Edit the following article to match Project requirements; delete if no AFC on the Project is designated with an Ip greater than 1.0.

*************************************************************************************************************

Certification: Submit certification and backup information that AFC can perform required functions after a design earthquake as specified in “SERVICE CONDITIONS” below.

AFC designated with Ip greater than 1.0 shall be certified by the manufacturer to withstand the total lateral seismic force and seismic relative displacements specified in the International Building Code (IBC) or ASCE 7, Minimum Design Loads for Buildings and Other Structures.

Certification shall be based on 3-axis shake table testing of similar products.

Required response spectra shall exceed 1.1 times the in-structure spectra determined in accordance with IBC AC156, Acceptance Criteria for Seismic Qualification by Shake-Table Testing of Nonstructural Components and Systems.

Certification: Submit certification by manufacturer’s field technical representative that the subcontractor has installed, adjusted, and tested each AFC according to the manufacturer’s recommendations.

Shop Drawings: Submit shop drawings for each AFC including dimensioned plans and elevations and component lists. Include front and side views of enclosure showing overall dimensions, enclosure type, enclosure finish, unit locations, and conduit entrances.

Installation Instructions: Indicate application conditions and limitations of use stipulated by Product testing agency specified under Regulatory Requirements. Include instructions for storage, handling, protection, examination, installation, and starting of Product.

Operation and Maintenance Instructions: Submit operation and maintenance instructions.

Test Reports: Submit results of required factory tests.

Warranty: Provide a 3-year parts warranty, on materials and workmanship, and 1-year labor warranty from the date of field certification by manufacturer’s representative of satisfactory operation.

QUALITY ASSURANCE

Comply with the National Electrical Code (NEC) for components and installation.

Provide products that are listed and labeled by a Nationally Recognized Testing Laboratory (NRTL) for the application, installation condition, and the environment in which installed.

Comply with the applicable requirement of the latest NEMA ICS 3.1 – Safety Standards for Construction and Guide for Selection, Installation and Operation of Adjustable Speed Drive Systems, IEEE 519, and FCC Part 15 Subpart J.

The manufacturer of the AFC shall be a certified ISO 9001 facility.

The manufacturer’s turn around period to repair or replace the AFC shall be no more than 36 hours.

Perform the following factory tests on each AFC:

Test every power converter (a component of the AFC) with an actual AC induction motor 100% loaded and temperature cycled to the full range of the AFC.  Monitor the power converter for correct phase current, phase voltages, and motor speed. Verify current limit operation by simulating a motor overload.

Verify proper factory presets by scrolling through all parameters to ensure proper microprocessor settings.  Verify proper functioning of all input and output ports.

Test all AFC door mounted pilot devices to verify proper function.

Functionally test all options including operation of a motor in the bypass mode if supplied.  Verify proper setting of motor overload protection.

Test the AFC wiring for continuity, shorts, and unintended grounds with all enclosed devices mounted and wired.

COORDINATION

Coordinate the features of each AFC with the ratings and characteristics of the supply circuit, the motor, the required control sequence, the duty cycle of the motor, drive, load, the pilot device, and control circuit affecting controller functions.  Furnish AFCs rated to suit the motor controlled in the specified conditions.

Coordinate the communications protocol with the building automation system; refer to Section 25 5000 – Integrated Automated Facility Controls.

SERVICE CONDITIONS

AFCs shall perform satisfactorily in the following service conditions without mechanical or electrical damage or degradation of operating characteristics:

Operating elevation of 7500 feet above sea level.

Operating ambient temperature extremes of 32 to 104 degrees F.

24-hour average operating ambient temperature not exceeding 86 °F.

Operating relative humidity: 0 to 95 percent, without condensation.

International Building Code seismic criteria:

      - Seismic Design Category = D

      - SDS = spectral acceleration, short period = 0.75g

      - SD1 = spectral acceleration, 1-second period = 0.64g

      - ap = component amplification factor = 2.5

      - Rp = component response modification factor = 6.0

*****************************************************************************************************

Edit the following article to match project requirements; indicate the applicable importance factor. If more than one applies, indicate specific AFCs that have an importance factor greater than 1.0.

*****************************************************************************************************

      - Ip = component importance factor
Ip = 1.5 for life safety related components such as emergency system AFCs
Ip = 1.5 for safety class or safety significant system AFCs.
Ip = 1.0 for all other AFC applications

*****************************************************************************************************

Edit the following article to match project requirements; use only for outdoor equipment.

*****************************************************************************************************

Maximum solar heat gain: 110 W/sq ft.

Receiving, Storing and Protecting

Receive, store, and protect, and handle products according to NECA 1—Standard Practices for Good Workmanship in Electrical Construction.

EXTRA MATERIALS

Furnish six spares of each size and type fuse required.

*****************************************************************************************************

Edit the following article to match project requirements; use only for AFCs on life safety, safety systems, safety significant systems, or mission critical systems where the load is not suitable for operation at full speed through a bypass contactor. Coordinate with the ES-DE Process and Automation team. Delete if not applicable to the project.

*****************************************************************************************************

Provide one spare AFC to match the size and type required for each of the AFCs listed below:

___________________________

___________________________

___________________________

Project record Documents

Submit the following in accordance with Section 01 7839, Project record Documents:

Parameter Settings: For each AFC provide a listing of all drive parameter settings that were changed from the manufacturer’s default settings.

Test reports and certifications indicated in FIELD QUALITY CONTROL article.

PRODUCTS

  - PRODUCT OPTIONS AND SUBSTITUTIONS

Alternate products may be accepted; follow Section 01 2500, Substitution Procedures.

  - Adjustable FREQUENCY AC CONTROLLER

Provide UL508C listed and labeled configured adjustable frequency AC controller(s) (AFCs) as indicated on the Drawings and specified in this Section. NEMA 1 enclosed AFCs shall be UL-1995 listed for mounting in plenums and compartments handling conditioned air.

*************************************************************************************************************

Edit the following article to match project requirements. Use the 3-contactor bypass only for critical loads (e.g. ML-2, ML-3, safety significant, process critical, life safety) that are suitable for operation at full speed.

*************************************************************************************************************

Each configured AFC shall be an integrated assembly with an externally operated disconnect device, transient voltage surge suppression, current-limiting fuses, line input reactor, power converter, cooling fans, operator interface, control system interface, control power transformer, [3-contactor bypass system,] and a suitable enclosure.

Provide fusible switch type externally operable disconnect.  Disconnect handle shall have provisions for locking in the OFF position with up to 3 padlocks.  Mechanical interlocks shall prevent opening the enclosure door with disconnect in the ON position and shall prevent moving disconnect to the ON position with enclosure door open.

Provide current-limiting drive branch circuit fuses in the disconnect switch.  Select fuses to protect the input rectification circuit.  Use Class J fuses with interrupting rating of 200,000 AIC.  The series interrupting rating of the AFC and fuses shall be a minimum of 30,000 AIC and shall be stated in the AFC Instruction Manual as required by UL

Provide a three phase 3% minimum impedance input line reactor in the AFC cabinet to minimize drive harmonics on the AC line and protect the drive from damaging electrical system transients.  Provide additional input filtering as required to limit line current total harmonic distortion (THD) to less than 10 percent.

Provide power converter that is microprocessor based using insulated gate bipolar transistors and pulse width modulation (PWM) technology and is suitable for low-noise operation of adjustable torque loads such as centrifugal pumps and fans.

Input voltage shall be either 200-230 or 380-480 Vac as indicated on the drawings.

Power converter shall be able to withstand voltage variations of -15 percent to +10 percent and imbalance of 3 percent without tripping or affecting drive performance.

Power converter shall operate with input frequency of 60 Hz and shall withstand a frequency variation of +5 percent to -5 percent.

Power converter displacement power factor shall be not less than 0.95 lagging under any speed or load condition.

The efficiency of the power converter shall be not less than 96 percent at full speed and full load.

Line notches, transients, and harmonics on incoming line shall not affect power converter performance.

Power converter shall include provisions for a DC link inductor.  Power converters 100 HP and above shall be supplied with DC link inductor in addition to the input line reactor.

Power converter output shall be capable of continuously operating the connected variable torque motor load over the complete speed range at an elevation of 7500 feet in an ambient temperature of +40 degrees C operating at the specified carrier frequency.

Current rating of the power converter shall be based on a carrier frequency of 8 kHz for AFCs 1-75 HP and 4 kHz for AFCs 100-400 HP.  All HP ratings shall meet or exceed Table 430.150 of the National Electric Code.  Rated three-phase motor full load current, HP, maximum current and rated voltage shall appear on the power converter nameplate.

Power converter output voltage shall vary with frequency to maintain a constant volts/hertz ratio up to 60 Hz output.  Constant or linear voltage output shall be provided above 60 Hz.

Power converter rated output voltage shall be programmable to match motor nameplate voltage.

The power converter one-minute overload rating shall be not less than 120 percent of rated current, adjusted for altitude.

The power converter shall be able to operate with its output disconnected for troubleshooting and startup.

PWM carrier frequency shall be field adjustable with a minimum range of 2 kHz to 6 kHz to minimize the level of audible motor noise.

Motor acceleration and deceleration shall be programmable from one second to not less than 60 seconds.

For fan service, provide controller with not less than 3 programmable critical frequencies that can be skipped to avoid mechanical resonances.

Power converter shall not generate damaging voltage pulses at the motor terminals when located within 200 feet of the motor.  Power converter shall comply with NEMA MG1 section 30.40.4.2.

Supply the power converter with interface modules as required to provide the following control functions and external signals:

*************************************************************************************************************

Edit the following article to match project requirements. Select the protocol that will be compatible with the building automation system or process control system. Coordinate with Section 25 5000 and the LANL ES-DE Process and Automation Team.

*************************************************************************************************************

Automatic control using [ModBus RTU compatible] [ANSI/ASHRAE Standard 135, ISO 16484-5 approved BACnet compatible] network protocol over an RS-485 communications system from the building automation system.  This communications port shall provide direct communication between the drive microprocessor and the building automation system.  All configuration and control functions shall be accessible through this port and fault diagnostics, start/stop, speed commands, and all drive feedback variables shall be available.  Discrete signals such as Bypass Run or Interlock Open shall also be mapped through the drive terminal strip to the system for unitary control.  The communications port shall have the ability to be used in a "monitor only" mode where control shall be from a digital controller directly wired to the drive.

Six configurable digital inputs, factory pre-set for common HVAC control interface to minimize customization at start up.

*************************************************************************************************************

Edit the following article to match project requirements. Coordinate with the ES-DE Process and Automation Team.

*************************************************************************************************************

Two isolated analog inputs with 0-20 mA, 4-20 mA or 0-4 V, 0-8 V, and 0-10 V selectable parameters.  Both shall be capable of providing speed feedback for internal PI setpoint control loop.  Either may be mapped to communication port for unitary control of temperature, pressure, or other analog control functions.

Isolated 0-10 V output signal proportional to speed or load as required to interface with control system

Not less than two sets of NEMA ICS 2 field-convertible auxiliary contacts to signal the following conditions:

Drive run.

Drive fault.

Provide the power converter with the following protective features:

Class 10 or 20 electronic overload circuit designed to protect AC motor operated by the AFC output from extended overload operation.  No additional hardware such as motor overload relays or motor thermostats shall be required.

Output phase-to-phase short circuit protection.

Output ground fault protection.

High input line voltage.

Low input line voltage.

Loss of input or output phase.

Drive overcurrent.

Drive over-temperature.

Stall protection.

Transient voltage surge suppression up to 6000 volts peak per IEEE C62.41.

The AFC shall have the capability of riding though power dips up to 10 seconds without a controller trip depending on load and operating condition. The AFC shall automatically restart after a longer power interruption.

Provide the following operator interfaces mounted on the cover of:

Touch keypad and LCD screen that digitally indicates:

Frequency output

Voltage output

Current output

Motor RPM

Motor kW

Elapsed Time

Time Stamped Fault Indication

DC Bus Volts

Faults

PI running, PI setpoint

Parameter settings

Heavy duty, 22 mm or 30 mm, metal operator, oil tight pilot devices as listed below with NEMA ICS 2, Form Z, A600 rated contacts:

Push buttons: Mushroom head, maintained action, turn-to-release emergency STOP pushbutton.

Push-to-test LED type indicating lights:

          - White POWER ON pilot light.

          - Yellow FAULT pilot light.

          - Red RUNNING pilot light.

          - Green STOPPED pilot light.

Speed Control Selector Switch: Rotary type LOCAL - OFF - REMOTE.

Provide legend plates for pushbuttons, pilot lights, potentiometer, and selector switch.

Provide labeled terminal block connections for safety interlocks, fault contacts, normal operational functions such as run/stop, remote references, mode control, external emergency stop, and external emergency full-speed.

*************************************************************************************************************

Edit the following article to match project requirements. Specify the 3-contactor bypass only for systems serving critical loads (e.g. ML-2, ML-3, safety significant, process critical, life safety) that are suitable for operation at full speed. Specify spare AFCs for systems serving critical loads that are not suitable for operation at full speed. Coordinate with the ES-DE Process and Automation Team.

*************************************************************************************************************

Provide the AFC with 3-contactor isolation and bypass system.

Provide interlocked isolation and bypass contactors, electronic overload relay, fused disconnect interlocked with the door, motor flux decay timer and AFC-TEST-BYPASS selector switch.

In the AFC position the power converter shall provide adjustable frequency speed control of the motor under non-fault conditions.  When the power converter is under a fault condition the contactors shall be automatically energized upon power converter shutdown (Drive fault contact operation) to isolate the power converter and operate the motor, across the line, on 60 Hertz line power through the overload relay.

In Drive Test mode, the drive-input contactor shall be closed to keep the power on to the drive, and the drive-output contactor open.  This shall enable the user to test the drive before running the motor.  A jumper shall be added to test the drive while bypass is running the motor and must be field installed to alert operators of this condition.

In bypass mode, the drive-input and the drive-output contactor will be open to isolate the drive.  The bypass contactor will be open to allow the motor to run directly from the AC line.  Bypass motor overload protection shall be provided by electronic Class 20 adjustable overload relay.

Provide relay control logic within the AFC enclosure to allow the same "START/STOP" and “emergency stop” commands to operate the motor in either the AFC or BYPASS mode.

Provide push-to-test LED indicator lights to annunciate bypass status and alarms.

Provide a control power transformer in each enclosed AFC.  The transformer shall have 120-volt secondary and sufficient capacity to operate all connected cooling fans, pilot, indicating and control devices, plus 100 percent spare capacity.  Provide fused primary and secondary.  Bond un-fused leg of secondary to enclosure.  Provide fuse blown indicating fuses.

Provide auxiliary control relays where required to accomplish interlocks and control sequences.  Relays shall be heavy-duty general-purpose type, having 115 volt 60 Hertz operating coils.

Provide the AFC with cooling air fan(s) and/or heat sink construction as required for maintaining the temperature of components within operating limits.  Provide filtration for cooling air as required for the installation and operating environment.

Provide AFC enclosure in accordance with ANSI/NEMA ICS 6 - Enclosures for Industrial Controls and Systems as required to meet conditions of installation and operation.

AFCs shall meet the radio frequency energy emission limits of FCC Part Class A and also the IEC 61800-3 – EMC Product Standard for Power Drive Systems emission limits for Restricted Distribution and installation in the First Environment.  Installation manual shall include instructions for installing the drive equipment so that it meets the specified emission limits as installed.

Manufacturer: Allen-Bradley “1336 Plus II”, ABB “ACH 550” or “ACS 550”, P11”, Square D “ATV66”.

EXECUTION

  - EXISTING WORK

*************************************************************************************************************

Delete this article when existing construction is not affected.

*************************************************************************************************************

Disconnect and remove abandoned AFCs.

Maintain access to existing AFCs and other installations that are to remain active and to require access. Modify installation or provide access panel.

Clean and repair existing AFCs that are to remain or be reinstalled.

  - EXAMINATION

Examine surfaces to receive control equipment for compliance with installation tolerances and other conditions affecting performance of the control system.  Do not proceed with installation until unsatisfactory conditions have been corrected.

  - INSTALLATION

Install AFCs indicated on the Drawings and according to manufacturer's instructions.  Manufacturer’s installation instructions shall be available at the construction site.

Mount with digital display panel 5'-0" above floor or as indicated on the Drawings.

Install enclosed controllers plumb.  Provide supports in accordance with the requirements of Section 26 0529 – Hangers and Supports for Electrical Systems, Section 26 0548 – Vibration and Seismic Controls for Electrical Equipment, and the NEC.

Ground and bond motor controllers and control devices as required in Section 26 0526 – Grounding and Bonding for Electrical Systems.

Identify motor controllers and install warning signs as required in Section 26 0553 – Identification for Electrical Systems.

Tighten electrical connectors and terminals according to manufacturer's published torque-tightening values. Where manufacturer's torque values are not furnished, use those specified in UL Standard 486A-486B.

Set overload relays or install overload heater elements in motor controllers to match installed motor characteristics.

Provide neatly typed label inside each motor starter enclosure door identifying motor served, nameplate horsepower, full load amperes, code letter, service factor, and voltage/phase rating.  Place label in clear plastic holder.

  - FIELD QUALITY CONTROL

Clean, inspect, test, adjust, and energize AFCs in accordance with the manufacturer’s instructions.

      - Inspect each AFC for physical damage, proper alignment, and proper anchorage.

      - Configure AFC parameters to match requirements of the served system.

      - Keep records of inspections, tests, configurations, and adjustments for each AFC; submit them to the LANL STR.

*****************************************************************************************************

Edit the following article to match project requirements. Delete if formal electrical acceptance testing is not required; refer to LANL Master Specification Section 26 0813.

*****************************************************************************************************

Coordinate inspections and tests with those required by Section 26 0813 – Electrical Acceptance Testing.

After completing installation, cleaning, and testing, touch-up scratches and mars on finish to match original finish.

  - MANUFACTURER'S FIELD SERVICE

Provide the services of a factory trained representative from the AFC manufacturer to inspect and certify the installation and to oversee energizing and testing.

Manufacturer’s representative shall certify in writing that each AFC has been installed, adjusted, and tested in accordance with the manufacturer’s recommendations.

Provide one full work day of training for up to three owner’s representatives at the project site.  A manufacturer’s qualified representative shall conduct training session.  The training program shall consist of instruction on the operation and maintenance of the AFC.

END OF SECTION

****************************************************************************************************

Do not delete the following reference information.

****************************************************************************************************

FOR LANL USE ONLY

This project specification is based on LANL Master Specification 26 2923 Rev. 2 dated January 12, 2010.