SECTION 26 4300

Surge Protective Devices

************************************************************************************************************

LANL MASTER SPECIFICATION

Available online at http://engstandards.lanl.gov.

This template must be edited for each project. In doing so, specifier must add job-specific requirements. Brackets are used in the text to indicate designer choices or locations where text must be supplied by the designer. Once the choice is made or text supplied, remove the brackets. The specifications must also be edited to delete specification requirements for processes, items, or designs that are not included in the project -- and specifier’s notes such as these. To seek a variance from requirements in the specifications that are applicable, contact the Engineering Standards Manual Electrical POC. Please contact POC with suggestions for improvement as well.

When assembling a specification package, include applicable specifications from all Divisions, especially Division 1, General requirements.

Specification developed for ML-4 projects. For ML-1, 2, and 3 applications, additional requirements and independent reviews should be added if increased confidence in procurement or execution is desired; see ESM Chapter 1 Section Z10 Specifications and Quality Sections.
***********************************************************************************************************

***********************************************************************************************************

This Section supersedes both LMS Section 26 4123 – Lightning Protection Surge Arresters and Suppressors and LMS Section 26 4313 - Transient-Voltage Suppression for Low-Voltage 
Electrical Power Circuits. This revision is to correlate with ANSI/UL 1449 – UL Standard for Safety for Surge Protective Devices, 4th Edition and Article 285 in the National Electrical Code.

Type 1 SPDs are designed to be used on the line side of a service disconnect, directly connected to the transformer secondary conductors.

Type 2 SPDs are designed to be used on the load side of a circuit breaker.

***********************************************************************************************************

GENERAL

***********************************************************************************************************

Edit the following section to match Project requirements. Delete materials not applicable to Project.

***********************************************************************************************************

SECTION INCLUDES

General requirements for both type 1 and type 2 surge protective devices (SPDs) for the protection of electrical power circuits not exceeding 1000 V.

Type 1 surge protective devices (SPD’s) for the protection of electrical power circuits not exceeding 1000 V.

SPDs for the protection of signal, data, antenna, and control lines.

ACTION SUBMITTALS

Submit the following:

Catalog Data: Submit catalog data describing SPDs. Include data substantiating that proposed products comply with specified requirements.

Installation Instructions: manufacturer’s manual.

QUALITY ASSURANCE

Comply with the National Electrical Code (NEC), and NFPA 780 – Standard for the Installation of Lightning Protection Systems for installation requirements, where applicable.

Provide SPDs that are listed by a Nationally Recognized Testing Laboratory (NRTL). Listing standard shall be the following, as applicable:

ANSI/UL 1449 – Standard for Safety for Surge Protective Devices

UL 497B – Standard for Safety for Protectors for Data Communications and Fire Alarm Circuits.

UL 497C – Standard for Safety for Protectors for Coaxial Communications Circuits.

Provide SPDs suitable for use at a nominal altitude of 7500 ft.

Receiving, Storing and Protecting

Receive, store, protect, and handle products according to the manufacturer’s instructions and NECA 1 Standard Practices for Good Workmanship in Electrical Construction.

PRODUCTS

  - PRODUCT OPTIONS AND SUBSTITUTIONS

Alternate products may be accepted; follow Section 01 2500.

***********************************************************************************************************

Edit the following section to match Project requirements. Delete materials and systems not applicable to Project.

***********************************************************************************************************

  - general spd requirements for power applications

NRTL listed to UL 1449.

SPD shall provide surge current paths for at least the following modes of protection:

L-N, L-G, and N-G for wye-connected systems;

L-L, L-G in delta-connected systems.

Provide each individual SPD intended for mounting external to the electrical assembly with a NEMA enclosure suitable for the installation location and environment.

NEMA 1, 12, 3R, and 4 enclosures: powder-coated steel.

NEMA 4X enclosures: polycarbonate or Type 304 stainless steel.

Each SPD shall pass the manufacturing and production line tests required in UL 1449 latest Edition.

  - Type 1 SPD

AC Power SPDs shall have a UL 1449 Short Circuit Current Rating (SCCR) not less than the following:

System Voltage	Circuit Size	Minimum SCCR

480Y/277	Any	200 kA,

480 Delta	Any	200 kA,

208Y/120	Greater than 400 A	200 kA,

208Y/120	400 A and less	100 kA,

120/240	Any	100 kA.

SPD shall be suitable for use without external or supplemental overcurrent protection.  Every suppression component of every mode shall be protected by internal overcurrent and thermal over-temperature controls.  SPDs relying upon external or supplementary overcurrent protection will not be considered.

SPD shall have a UL 1449 nominal discharge current rating (In) of not less than 20 kA.

Suppression components shall be thermally-protected 32 mm or larger metal-oxide varistors (MOVs).

AC Power SPDs minimum surge current capability (single pulse rated) per phase shall be as indicated for the following applications:

Service Equipment or Transfer Switch:

System Voltage	Equipment Size	Minimum Surge Current Capability

480Y/277	Any	240 kA,

480 (ungrounded)	Any	240 kA,

208Y/120	Greater than 400 A	240 kA,

208Y/120	400 A and less	100 kA,

120/240	Any	100 kA.

Panelboards and MCCs that supply  one or more electrical circuits that leave the structure to supply another structure and the conductors extend more than 100 feet:

System Voltage	Minimum Surge Current Capability

480Y/277	150 kA,

480 (ungrounded)	150 kA,

208Y/120	100 kA,

120/240	100 kA.

Panelboards and MCCs that supply  one or more electrical circuits that leave the structure to supply equipment that is exposed to lightning (e.g. roof mounted HVAC equipment, parking lot lighting):

System Voltage	Minimum Surge Current Capability

480Y/277	150 kA,

480 (ungrounded)	150 kA,

208Y/120	100 kA,

120/240	100 kA.

AC Power SPDs UL 1449 Voltage Protection Rating (VPR) shall not exceed the following:

System Voltage	  L-N	  L-G	  L-L	  N-G

480Y/277	1200V	1200V	2000V	1200V

480 (ungrounded)	   ---	1800V	2000V	   ---

208Y/120	 700V	 700V	1200V	 700V

120/240	 700V	 800V	1200V	 700V

UL 1449 Maximum Continuous Operating Voltage (MCOV) rating shall be not less than the following:

System Voltage	Allowable System Voltage Fluctuation (%)	MCOV

480Y/277	15%	320V

480 (ungrounded)	15%	550V

208Y/120	25%	150V

120/240	25%	150V

AC Power SPDs shall include not less than the following monitoring and diagnostic features that report the protection status of the SPD:

One green LED (protected) indicator per phase and one red (not protected) LED.

For SPDs with a surge current capacity greater than 100 kA provide an audible alarm with on/off silence function, and one set of NO/NC contacts that change state under any fault condition.

***********************************************************************************************************

Edit the following section to match Project requirements; delete section if not applicable. SPDs that are integrated within the protected electrical equipment (e.g. switchgear, switchboards, panelboards, motor control centers, busway plugs, and automatic transfer switches) will usually exhibit better performance and reliability than externally mounted SPDs. However, such integration requires coordination of this Section with the specification sections for the particular equipment items.

***********************************************************************************************************

Where indicated on the Drawings or specified in other Sections, provide SPDs that are factory installed and integrated within the protected electrical [switchgear,] [switchboards,] [panelboards,] [motor control centers,] [busway plugs,] [and] [automatic transfer switches], and indicate if SPD is Type 1 or Type 2.

***********************************************************************************************************

Edit the following section to match Project requirements; delete section if not applicable. SPDs that are mounting external to the protected electrical assembly will usually exhibit degraded performance compared to SPDs that are integrated within electrical equipment. This is due to the added impedance of the longer interconnecting conductors. In addition, the design must provide space immediately adjacent to the enclosure of each protected equipment item so the length of the interconnecting conductors will be the proper length, as specified by the manufacturer.

***********************************************************************************************************

Manufacturers:

Advanced Protection Technologies:

- Surge Current Capability over 100 KA: “XAS” series,

- Surge Current Capability 100 KA or less: “XDS” series.

Eaton:

- Surge Current Capability over 100 KA: “SPD” series,

- Surge Current Capability 100 KA or less: “CVX100” series.

Siemens:

- Surge Current Capability over 100 KA:  “TPS3 01,” TPS3 05”, “TPS3 06,” “TPS3 12.”

- Surge Current Capability 100 KA or less: “TPS3 11.”

Square D:

- Surge Current Capability over 100 KA: “IMA” and “EMA” series.

- Surge Current Capability 100 KA or less: “IMA” and “EMA” series.

*************************************************************************************************************

Edit the following section to match Project requirements. Delete materials not applicable to Project.

*************************************************************************************************************

SPD FOR signal, data, Antenna, and control lines

Provide SPDs suitable for the protection of signal, data, antenna, and control lines.

Select SPDs with consideration for aspects such as the frequency, bandwidth, voltage, and current of the signal, data, antenna, or other communications lines and to ensure that insertion losses introduced by the surge protective devices are within acceptable operational limits.

Coordinate selection of SPDs for signal, data, antenna, and control lines with owner of equipment that is served by the lines.

Provide SPDs for of signal, data, and control lines that provide both common mode and differential mode protection.

Provide SPDs for signal, data, control, and alarm lines.

Provide devices with ratings and connectors as required by the application.

Manufacturer: Phoenix Contact, EDCO, MCG Electronics

Provide coaxial SPDs for antenna and RF signal lines.

Devices shall be listed in accordance with UL 497C.

Provide devices with ratings and connectors as required by the application.

Provide bulkhead plates and low-impedance paths to ground where antenna cables enter the structure.

Manufacturers: TII Network Technologies, Inc., Cable Innovations, PolyPhaser

EXECUTION

  - EXAMINATION

Verify mounting area is ready for SPDs.

Verify that circuit rough-in is at correct location.

INSTALLATION

Install SPDs as specified below, according to the manufacturer's instructions, NFPA 780, and the National Electrical Code. Have the manufacturer’s installation instructions available at the construction site.

**********************************************************************************************************

Edit section to match Project requirements. Delete materials or systems not applicable to Project.  For weapons areas, the SPD must be connected on the line side and section 2 must be edited to match.

**********************************************************************************************************

Service Equipment:

Install a [Type 1][Type 2] SPD that is [factory installed and integrated into] [individually mounted immediately adjacent to] each low-voltage service equipment.

Connect SPD on the [line side] [load side] of the service disconnecting means.

Provide a means of connection for the SPD, as recommended by the manufacturer.  This might be a sub-feed connection block, or it might by a dedicated circuit breaker.

**********************************************************************************************************

Edit section to match Project requirements. Delete materials or systems not applicable to Project.

**********************************************************************************************************

Automatic Transfer Switch:

Install an individual [Type 1][Type 2] SPD mounted immediately adjacent to each automatic transfer switch that is connected to an outdoor generator.

Connect SPD on the alternate source side of the automatic transfer switch.

**********************************************************************************************************

Edit section to match Project requirements. Delete materials or systems not applicable to Project.

**********************************************************************************************************

Power Panelboard or Motor Control Center:

Install a Type 2 SPD that is [factory installed and integrated into] [individually mounted immediately adjacent to] each power panelboard or motor control center that supplies electronic equipment (e.g. computers, adjustable frequency drives, and laboratory equipment).

Install a Type 2 SPD that is [factory installed and integrated into] [individually mounted immediately adjacent to] each power panelboard or motor control center that supplies  one or more electrical circuits that leaves the structure to supply another structure and the conductors extend more than 100 feet.

Install a Type 2 SPD that is [factory installed and integrated into] [individually mounted immediately adjacent to] each power panelboard or motor control center that serves one or more electrical circuits that leaves the structure to supply equipment that is exposed to lightning (e.g. roof mounted HVAC equipment, parking lot lighting).

Provide a dedicated 3-pole circuit breaker, sized as per manufacturer’s instructions, in the panelboard or MCC as the SPD interface device.

Connect SPDs to protect each ungrounded (line) and grounded (neutral) conductor.

**********************************************************************************************************

Edit section to match Project requirements. Delete materials or systems not applicable to Project.

**********************************************************************************************************

Install listed SPD for each for signal, data, control, and alarm line that enters the structure or exits the structure to serve external detached equipment or other detached structures. Where such signal, data, control, and alarm circuits are longer than 100 ft. install listed SPD at both ends of the circuit.

**********************************************************************************************************

Edit section to match Project requirements. Delete materials or systems not applicable to Project.

**********************************************************************************************************

Install listed coaxial SPD for each for antenna and RF signal line that enters the structure or exits the structure to serve external detached equipment or other detached structures. Where such antenna and RF signal circuits are longer than 100 ft. install listed coaxial SPD at both ends of the circuit.

Install each SPD so it will be accessible for inspection and maintenance.

Install SPDs in a manner that will not limit the use of through-feed lugs, sub-feed lugs, or sub-feeder circuit breakers in panelboards.

Install each SPD with conductor length according to the manufacturer’s instructions.

Twist conductors tightly together and keep runs as straight as possible with no sharp bends or kinks.

For facilities in explosive areas:

SPDs in these areas are required to be connected to the line side of the main, or service, disconnect.  The ground connection of the SPD shall be made to the ground bar that is in the panel directly downstream of the SPD.  If this requires an extension to the ground lead of the SPD, the manufacturer shall be contacted for instructions on how to extend the lead.

  - Field Quality Control

Provide final protection and maintain conditions to ensure that coatings and finishes are without damage or deterioration at final inspection.

Repair damage to paint finishes with matching touch-up coating recommended by the manufacturer.

Verify that each SPD is correctly connected and that all condition monitoring indicators operate properly.

Verify mechanical integrity of each conductor connection.

END OF SECTION

**********************************************************

Do not delete the following reference information.

**********************************************************

THE FOLLOWING STATEMENT IS FOR LANL USE ONLY

This project specification is based on LANL Master Specification Section 26 4300 Rev. 2, dated September 2, 2020.