SECTION 26 5200

Emergency lIGHTING

*************************************************************************************************************

LANL MASTER SPECIFICATION

This template must be edited for each project.  In doing so, specifier must add job-specific requirements.  Brackets are used in the text to indicate designer choices or locations where text must be supplied by the designer.  Once the choice is made or text supplied, remove the brackets.  The specifications must also be edited to delete specification requirements for processes, items, or designs that are not included in the project -- and specifier’s notes such as these.  To seek a variance from requirements in the specifications that are applicable, contact the Engineering Standards Manual Electrical POC. Please contact POC with suggestions for improvement as well.

When assembling a specification package, include applicable specifications from all Divisions, especially Division 1, General requirements.

Specification developed for ML-4 projects.  For ML-1, 2, and 3 applications, additional requirements and independent reviews should be added if increased confidence in procurement or execution is desired; see ESM Chapter 1 Section Z10 Specifications and Quality Sections.
*************************************************************************************************************

GENERAL

Section Includes

Unit emergency lights.

Fluorescent emergency ballasts.

Emergency exit signs.

SUBMITTALS

Submit the following in accordance with Section 01 3300, Submittal Procedures:

Catalog Data: Submit catalog data describing emergency lighting. Include data substantiating that materials comply with specified requirements.  Arrange data for luminaires in the order of fixture designation.

Performance Curves/Data: Submit certified photometric data for emergency lighting units.

Warranty:  Submit warranties for emergency lighting units and exit signs.

Maintenance Instructions: Submit maintenance instructions for inclusion in the operating and maintenance manuals.

ENVIRONMENTAL REQUIREMENTS

Provide emergency lighting products that are suitable for operation at an altitude of 7500 feet above sea level.

For ambient temperature limits, refer to the specific products in Part 2.

SPARE MATERIALS

Furnish the following extra materials matching products installed.  Package the extra materials with protective covering for storage and identify with labels describing contents.

Lamps:  Provide 10 percent of quantity of lamps of each type, but no fewer than two lamps of each type.

QUALITY ASSURANCE

Comply with ANSI/NFPA 70 - National Electrical Code (NEC), NFPA 101 - Life Safety Code, and the Uniform Building Code (UBC) for components and installation.

Provide emergency lighting units and exit signs that are NRTL-listed and labeled for their indicated use and location on this project by a Nationally Recognized Testing Laboratory (NRTL) in accordance with UL 924 – Emergency Lighting and Power Equipment.

Use manufacturers that are experienced in manufacturing emergency lighting units similar to those indicated for this Project and have a record of successful in-service performance.

WARRANTY

Submit warranties, mutually executed by the manufacturer and the Subcontractor, agreeing to replace emergency lighting products that fail in materials or workmanship within the period specified for each product, beginning on the date of acceptance by LANL. This warranty is in addition to, and not a limitation of, other rights and remedies LANL may have under the Subcontract Documents.

Receiving, Storing and Protecting

Receive, store, and protect, and handle products according to NECA 1 – Standard Practices for Good Workmanship in Electrical Construction, NECA/IESNA 500 – Standard for Installing Indoor Commercial Lighting Systems, and NECA/IESNA 502 – Standard for Installing Industrial Lighting Systems.

PRODUCTS

  - PRODUCT OPTIONS AND SUBSTITUTIONS

Refer to Section 01 2500, Substitution Procedures.

Provide emergency lighting products that meet the requirements of the “Buy American Act” (Title 41 of the U.S. Code, Chapter 1, §10a – 10d).

Fluorescent Emergency Ballast

*************************************************************************************************************

NOTE:  Use fluorescent emergency ballast for indoor dry locations with a temperature range of 32 to 130 degrees F.  Do not use in supply-air luminaires that provide heating. Do not use in wet, damp, or hazardous locations. Fluorescent emergency ballasts may used instead of wall-mounted emergency lighting units in most areas with fluorescent luminaires. Delete this article if the project does not require any fluorescent emergency lighting ballasts.

*************************************************************************************************************

Furnish an NRTL-listed, self-diagnostic, fully automatic, fluorescent emergency ballast in each luminaire indicated on the Drawings.

The normal fluorescent luminaire ballast will operate the lamps during normal conditions; during emergency conditions the fluorescent emergency ballast shall operate one or two of the lamps in the luminaire.

Provide fluorescent emergency ballast that is connectable for operation at either 120 or 277 volts and suitable for indoor dry locations with a temperature range of 32 to 130 degrees F.

Provide fluorescent emergency ballast that contains a maintenance-free, sealed high-temperature nickel-cadmium or nickel-metal hydride battery with an expected service life of not less than 7 years.

Upon interruption of normal AC power, the internal controller shall automatically switch the emergency lighting load to the battery. The battery shall supply the ballast with power to produce 1100 to 1400 lumens of emergency light output for a minimum of 90 minutes.

Provide fluorescent emergency ballast with a self-diagnostic system that meets the requirements of NFPA 101 and includes the following features:

Automatically perform a self-test of battery and lamps for at least 30 seconds at intervals not exceeding 30 days.

Automatically perform a self-test of battery and lamps for at least 90 minutes once per year.

Any failure shall be indicated by a status indicator.

Provide fluorescent emergency ballast with an LED charging indicator lamp and a push to test switch for installation on the luminaire at locations and positions that will be visible from the floor and operable without removing or opening luminaire lenses or covers.

Provide not less than a 5 year full warranty on the fluorescent emergency ballasts.

Manufacturer: Bodine “B50ST” or approved equal.

Wall-Mounted EMERGENCY LIGHTING UNIT

*************************************************************************************************************

NOTE:  Use wall-mounted emergency lighting units for indoor dry locations with a temperature range of 68 to 86 degrees F. Delete this article if the project does not require any wall-mounted emergency lighting units.

*************************************************************************************************************

Furnish an NRTL-listed, self-diagnostic, fully automatic, wall-mounted emergency lighting unit at each location indicated on the Drawings.

Provide emergency lighting unit that is connectable for operation at either 120 or 277 volts and suitable for indoor dry locations with a temperature range of 68 to 86 degrees F.

Provide emergency lighting unit that contains a 6-volt maintenance-free battery, either sealed lead-calcium or sealed lead-acid. Battery shall be field-replaceable and shall have an expected service life of not less than 5 years.

Upon interruption of normal AC power, or brownout conditions exceeding a 20% drop from nominal voltage, the internal controller shall automatically switch on the emergency lighting. The unit shall be rated to supply not less than 25 watts for a minimum of 1.5 hours to 87.5 percent of rated battery voltage. During emergency operation, the battery shall be protected from deep discharge by a low-voltage battery disconnect circuit.

The unit shall include a voltage-regulated, automatic, solid-state battery charger to maintain the battery in a fully charged state under normal conditions. After a battery discharge, the charger shall automatically re-charge the battery to a fully charged state within the time limit set by UL 924.

Provide emergency lighting unit light source consisting of two top or side mounted adjustable heads each with either a 7.2 watt (minimum) wedge base T-5 lamp or a 7.2 watt (minimum) PAR-36 sealed beam lamp.

Provide emergency lighting unit with housing that is fabricated from either white UV stabilized high impact UL 94 V-0 5VA thermoplastic or corrosion-resistant steel with white powder coat finish.

Provide emergency lighting unit with a self-diagnostic system that meets the requirements of NFPA 101 and includes the following features:

Automatically perform a self-test of battery and lamps for at least 30 seconds at intervals not exceeding 30 days.

Any failure shall be indicated by a status indicator.

Provide emergency lighting unit that will perform self-timed tests that are manually initiated through the test button, including:

Lamps and battery for at least 30 seconds.

Lamps and battery for at least 90 minutes.

Emergency lighting unit shall provide exterior visual indication of AC power status, all self-diagnostic test cycles, and unit malfunctions including:

Battery fault

Charger fault

Lamp fault

Provide at least a 3-year full warranty on unit emergency lighting equipment and at least a 1-year full warranty plus additional 4-year pro-rata warranty on the battery.

Provide a wall-mounting plate or bracket, plus other seismic protection mounting accessories required for each installation location.

Manufacturers:  Chloride “6MF25WJ762-AD” or approved equal.

Furnish cord with suitable strain relief and plug for emergency lighting unit as follows:

120 volt systems: white or gray 3-foot, SJT or SJTO, 3-conductor cord with a NEMA 15-5P plug.

277 volt systems: white or gray 3-foot, SJT or SJTO, 3-conductor cord with a NEMA L7-20P twist lock plug.

SEVERE-DUTY Wall-Mounted EMERGENCY LIGHTING UNIT

*************************************************************************************************************

NOTE:  Use severe-duty emergency lighting units for wet, corrosive, or very dusty locations with a temperature range of 32 to 104 degrees F. This product is NOT suitable for use in hazardous locations defined by NEC Article 500. Delete this article if the project does not require any severe duty, wall-mounted emergency lighting units. NOTE: Severe-duty emergency lighting units are available for lower temperatures; consult manufacturer for more information.

*************************************************************************************************************

Furnish an NRTL-listed, self-diagnostic, fully automatic, severe-duty, wall-mounted emergency lighting unit at each location indicated on the Drawings.

Provide a severe-duty emergency lighting unit that is suitable for operation in a dusty, wet, or corrosive environment with an ambient temperature of 32 to 104 degrees F.

Provide severe-duty emergency lighting unit that is connectable for operation at either 120 or 277 volts.

Provide emergency lighting unit that contains a 6-volt maintenance-free battery, either sealed lead-calcium or lead-acid.

Battery charger shall automatically adjust charging parameters based on ambient temperature to maximize battery life.

Battery shall be field-replaceable and shall have an expected service life of not less than 5 years.

Upon interruption of normal AC power, or brownout conditions exceeding a 20% drop from nominal voltage, the internal controller shall automatically switch on the emergency lighting. The unit shall be rated to supply not less than 50 watts for a minimum of 1.5 hours to 87.5 percent of rated battery voltage at the lowest rated temperature. During emergency operation, the battery shall be protected from deep discharge by a low-voltage battery disconnect circuit.

The unit shall include a voltage-regulated, automatic, solid-state battery charger to maintain the battery in a fully charged state under normal conditions. After a battery discharge, the charger shall automatically re-charge the battery to a fully charged state within the time limit set by UL 924.

Provide severe-duty emergency lighting unit light source consisting of two adjustable lamp heads each with a 9-watt (minimum) PAR-36 sealed beam halogen lamp.

Provide severe-duty emergency lighting unit housing that is fully gasketed, gray polycarbonate or fiberglass-reinforced polyester that meets NEMA 4X requirements.

Provide severe-duty emergency lighting unit with a self-diagnostic system that meets the requirements of NFPA 101 and includes the following features:

Automatically perform a self-test of battery and lamps for at least 30 seconds at intervals not exceeding 30 days.

Any failure shall be indicated by a status indicator.

Provide severe-duty emergency lighting unit that will perform self-timed tests that are manually initiated through the test button, including:

Lamps and battery for at least 30 seconds.

Lamps and battery for at least 90 minutes.

Emergency lighting unit shall provide exterior visual indication of AC power status, all self-diagnostic test cycles, and unit malfunctions including:

Battery fault

Charger fault

Lamp fault

Provide at least a 3-year full warranty on unit emergency lighting equipment and a 1-year full warranty plus additional 4-year pro-rata warranty on the battery.

Manufacturer: Chloride “RN5PJ2IC-T” or approved equal.

LED emergency Exit Sign

*************************************************************************************************************

NOTE:  Use LED emergency exit sign for indoor dry locations with a temperature range of 68 to 86 degrees F. Delete this article if the project does not require any emergency exit signs.

*************************************************************************************************************

Furnish an NRTL-listed, self-diagnostic, fully automatic, LED illuminated emergency exit sign at each location indicated on the Drawings.

Provide LED emergency exit sign that is connectable for operation at either 120 or 277 volts and suitable for indoor dry locations with a temperature range of 68 to 86 degrees F.

Provide exit sign with die cast aluminum housing, white finish, green stencil face letters, and universal mounting capability. Provide all necessary components for each wall, ceiling, or end mounting application.

Provide single face or double face exit sign with arrows as indicated on the Drawings or as required for each location.

Provide exit sign with a maintenance-free battery, either nickel-cadmium or nickel-metal hydride. Battery shall be field-replaceable and shall have an expected service life of not less than 7 years.

Upon interruption of normal AC power, or brownout conditions exceeding a 20% drop from nominal voltage, the internal controller shall automatically switch the emergency exit sign lighting load to the battery. Emergency power will be provided for a minimum of 90 minutes. During emergency operation, the battery shall be protected from deep discharge by a low-voltage battery disconnect circuit.

Visibility of exit sign during normal or emergency operation shall be not less than that required in UL 924.

Provide exit sign with a self-diagnostic system that meets the requirements of NFPA 101 and includes the following features:

Automatically perform a self-test of battery and lamps for at least 30 seconds at intervals not exceeding 30 days.

Any failure shall be indicated by a status indicator.

Provide emergency exit sign that will perform self-timed tests that are manually initiated through the test button, including:

Lamps and battery for at least 30 seconds.

Lamps and battery for at least 90 minutes.

Exit sign shall provide exterior visual indication of AC power status, all self-diagnostic test cycles, and unit malfunctions including:

Battery fault

Charger fault

Lamp fault

Provide at least a 5-year full warranty on LED illuminated emergency exit sign electronics and a 5-year full warranty plus additional 5-year pro-rata warranty on the battery.

Manufacturers: Chloride “CXLN[1 or 2]GW-AD” or approved equal.

Severe-Duty LED emergency Exit Sign

*************************************************************************************************************

NOTE:  Use severe-duty LED emergency exit signs for wet, corrosive, or very dusty locations with a temperature range of 20 to 95 degrees F. This product is NOT suitable for use in hazardous locations defined by NEC Article 500. Delete this article if the project does not require any severe duty, emergency exit signs. NOTE: Severe-duty emergency exit signs are available for lower temperatures; consult manufacturer for more information. NOTE: This product does not have self-diagnostics available in a Buy American Act compliant unit.

*************************************************************************************************************

Furnish an NRTL listed, fully automatic, severe-duty LED illuminated emergency exit sign at each location indicated on the Drawings.

Provide a severe-duty LED illuminated emergency exit sign that is suitable for operation in a dusty, wet, or corrosive environment with an ambient temperature of 20 to 95 degrees F.

Provide severe-duty LED illuminated emergency exit sign that is connectable for operation at either 120 or 277 volts.

Provide exit sign with corrosion-resistant polycarbonate exterior housing, white finish, and green stencil face letters.

Provide exit sign with arrows as indicated on the Drawings or as required for each location.

Provide exit sign with a maintenance-free battery, either nickel-cadmium or nickel-metal hydride. Battery shall be field-replaceable and shall have an expected service life of not less than 10 years.

Upon interruption of normal AC power, or brownout conditions exceeding a 20% drop from nominal voltage, the internal controller shall automatically switch the emergency exit sign load to the battery. Emergency power will be provided for a minimum of 90 minutes. During emergency operation, the battery shall be protected from deep discharge by a low-voltage battery disconnect circuit.

Visibility of exit sign during normal or emergency operation shall be not less than that required in UL 924.

Provide emergency exit sign unit that will perform self-timed tests that are manually initiated through the test button, including:

Lamps and battery for at least 30 seconds.

Lamps and battery for at least 60 minutes.

Provide at least a 3-year full warranty on severe-duty LED illuminated emergency exit sign and a 5-year full warranty plus additional 5-year pro-rata warranty on the battery.

Manufacturers: Chloride “NSPL1G” plus “EMF” external mounting feet, or approved equal.

SELF-LUMINOUS EXIT SIGN

*************************************************************************************************************

NOTE:  Use self-luminous exit signs only in special circumstances such as hazardous areas, very hot or cold locations, or in structures that do not have electricity but require exit signs. Delete this article if the project does not require any self-luminous exit signs.

*************************************************************************************************************

Furnish an NRTL-listed self-luminous exit sign at each location indicated on the Drawings.

Provide self-luminous exit sign that meets the following contrast and luminance requirements:

Contrast Ratio: Not less than 0.5.

Letters: A minimum luminance of 0.06 foot-lambert as measured by a color-corrected photometer.

Furnish self-luminous exit sign rated to maintain the required minimum luminance for not less than 20 years.

Illumination:   Caused by the interaction of tritium and phosphors contained in sealed Pyrex glass tubes.

Color of Emitted Light:  Yellow-green.

Meets applicable Nuclear Regulatory Commission requirements.

Provide single or double face self-luminous exit sign and directional arrows as indicated on the Drawings.

Provide self-luminous exit sign with black plastic housing, green vinyl face, white letter strokes, and transparent polycarbonate cover.

Provide mounting accessories suitable for each installation location.

Manufacturers: Safety Light Corporation 2040-XX-20, Chloride C3-G-U-20-X-BK-PW, or approved equal.

PART 3  EXECUTION

  - EXISTING WORK

*************************************************************************************************************

Edit to suit project requirements

*************************************************************************************************************

Disconnect and remove abandoned emergency lighting units, exit signs, lamps, and accessories as indicated on the Drawings.

Extend existing emergency lighting and exit sign installations using materials and installation methods as specified.

Clean and repair existing emergency lighting units and exit signs that are indicated as remaining or are to be reinstalled.

Dispose of batteries in accordance with applicable LANL procedures. Arrange disposal of self-luminous exit signs with original unit manufacturer.

  - INSTALLATION

Install emergency lighting system in accordance with NECA/IESNA 500, Recommended Practice for Installing Indoor Commercial Lighting Systems (ANSI), the NEC, manufacturer's instructions, and approved shop drawings. Have the manufacturer’s installation instructions available at the construction site.

Mount exit signs and unit emergency lights with bottom of fixture not less than 6'-8" or more than 12'-0" above finished floor.

*************************************************************************************************************

Edit the following article to match available LANL Master Specifications. It is anticipated that in the fullness of time Section 25 0548 will be added to the LANL Master Specifications to address seismic protection for electrical components.

*************************************************************************************************************

Provide seismic protection for emergency lighting equipment in accordance with the Uniform Building Code and Specification Section [26 0529 Hangers and Supports for Electrical Systems][26 0548 Seismic Controls for Electrical Equipment].

Connect fluorescent emergency ballasts to operate two lamps in multi-lamp emergency luminaires.

Connect luminaires to a branch circuit that serves the general lighting in the area and ahead of any local or remote switches.  Self-luminous exit signs do not require an electrical circuit.

For 120 volt wall-mounted emergency lights install a NEMA L15-5R single receptacle within 12 inches of the emergency light fixture location.  Refer to Section 16140 - Wiring Devices.

For 277 volt wall-mounted emergency lights install a NEMA L7-20R single receptacle within 12 inches of the emergency light fixture location.  Refer to Section 16140 - Wiring Devices.

Connect severe-duty wall-mounted emergency lights to lighting circuits using a raceway system suitable for the installation environment: refer to Section 26 0533 Raceways and Boxes for Electrical Systems.

  - ADJUSTING

Aim lamps on wall-mounted emergency lighting units to obtain the following illumination of exit pathway:

1 ft-candle average

0.1 ft-candle minimum

Maximum-to-minimum uniformity ratio not exceeding 40 to 1.

Test emergency lighting equipment in accordance with the manufacturer’s instructions and NECA/IESNA 500.

*************************************************************************************************************

NOTE TO DESIGNER: The luminaire schedule on the Drawings should contain the following information:

1. Fixture type designation (e.g. “X”).

2. Description of fixture (e.g. “LED stencil-face emergency exit sign”).

3. Description of finish (e.g. “Baked white enamel finish”).

4. Description of lens or louver (e.g. “Green plastic lens”).

5. Description of ballast if applicable (e.g. "277V electronic ballast").

6. Description and quantity of lamps (e.g. “Green LED lamps”).

7. Description of accessories: (e.g. 3 foot white cord with “NEMA L7-20P plug”).

8. Manufacturer and catalog number (e.g. “XYZ #123456-7890”).

*************************************************************************************************************

END OF SECTION

*********************************************************

Do not delete the following reference information:

*********************************************************

FOR LANL USE ONLY

This project specification is based on LANL Master Specification 26 5200, Rev. 3, dated August 5, 2008.