SECTION 31 2323.33

FLOWABLE FILL

*************************************************************************************************************

LANL MASTER SPECIFICATION

Word file at http://engstandards.lanl.gov

This template must be edited for each project.  In doing so, specifier must add job-specific requirements.  Brackets are used in the text to indicate designer choices or locations where text must be supplied by the designer.  Once the choice is made or text supplied, remove the brackets.  The specifications must also be edited to delete specification requirements for processes, items, or designs that are not included in the project -- and specifier’s notes such as these.  To seek a variance from requirements in the specifications that are applicable, contact the Engineering Standards Manual Civil POC. Please contact POC with suggestions for improvement as well.

When assembling a specification package, include applicable specifications from all Divisions, especially Division 1, General requirements.

Specification developed for ML-4 projects.  For ML-1, 2, and 3 applications, additional requirements and independent reviews should be added if increased confidence in procurement or execution is desired; see ESM Chapter 1 Section Z10 Specifications and Quality sections.
*************************************************************************************************************

GENERAL

SECTION INCLUDES

Flowable fill (cement stabilized backfill).

RELATED SECTIONS

31 2000 - Earth Moving

03 3001 - Reinforced Concrete

ACTION SUBMITTALS

Submit the following:

Material certifications.  A complete list of materials including type; brand; source and amount of cement, fly ash, pozzolans, [silica fume], ground slag, and admixtures; and applicable reference specifications shall be included in the mix design submittal. Provide design mixes and test reports.

Batch tickets.

Field test reports (if required per 3.5)

DESCRIPTION

Flowable fill is a self-leveling slurry of cement, fly ash, aggregates, admixtures, and water with low final strength that can be hand dug later.

Flowable fill may be used for trenches, pipe structures, fill for abandoned water and sewer lines, and other works where cavities exist and firm support is required.

The use of flowable fill around or adjacent to utility lines or structures shall be reviewed and approved by the appropriate LANL Utilities and Infrastructure system representative.  Flowable fill shall not be around or adjacent to utility lines that have requirements for movement.

QUALITY ASSURANCE

When work or portions of work of this section are completed and require testing, notify the LANL Subcontract Technical Representative (STR).

Ensure all required cast-in-place concrete, embedment items, and utility work has been completed prior to placing flowable fill.

Job conditions

- Perform concrete washout, trucks and mixers, in a designated and controlled area to prevent the runoff of washout material and the co-mingling of unset concrete with storm water. Properly dispose of all hardened excess concrete.

PRODUCTS

  - MATERIALS

Cement: ASTM C 150, Type I or Type II.

Fine and Coarse Aggregates: Conform to ASTM C 33.  Provide a uniform mixture of fine aggregate or fine and course aggregate, as determined by ASTM D 422.

Aggregate Mixture Gradation Requirements

Sieve Size                        Percent Passing

1 inch                               		100

3/8 inch                                		95 – 100

No. 4                                     		80 – 100

No. 8                                  		60 – 95

No. 16                                    		45 – 80

No. 30                                     		25 – 60

No.50                                       	 5 – 45

No. 100                                     	5 – 35

No. 200                                     	0 - 30

Water: Potable water that is clean and not detrimental to concrete.

Fly Ash: Conform to ASTM C 618, Class C or Class F.

Air Entrainment: Conform to ASTM C260.  Air entrainment may be between 6 and 25 percent.  Air entraining is not required for below grade installation in areas not subject to freeze/thaw cycles.

Proportioning and Physical Property Requirements

- Provide a flowable fill mix design in accordance with the following limits:

- Cement, maximum 50 lbs/yd3

- Fly ash, from 150 lbs/yd3 to 300 lbs/yd3

- Air content, optional

- Slump, from 6 to 11 inches

- Water/Cement ratio, proportioned by weight to produce a slump within limits.

- Consistent aggregate throughtout the concrete mixture

- Compressive strength will not exceed 150 psi at 28 days.

FLOWABLE FILL

Mix and deliver flowable fill in accordance with ASTM C94.

Use accelerating admixtures in cold weather only when approved by LANL STR.  Use of admixtures will not relax cold weather placement requirements.

Use set retarding admixtures during hot weather only when approved by LANL STR.

Do not use calcium chloride as an admixture.

Add air-entraining agent if required to produce a flowable mix.

EXECUTION

- EXAMINATION

Verify that all items of cast-in-place concrete, grading, trenching, and all utilities and other embedded items are in place prior to placing flowable fill.

Utilities that are subject to required movement (e.g., steam and condensate lines), shall not be embedded in flowable fill or otherwise have restricted movement.

Flowable fill shall not be used as a substitute for sand bedding or earth backfill for primary utilities unless approved by the LANL Utilities and Infrastructure system representative.

- preparation

  - Remove all loose material from the uneven tuff and the concrete structures.

  - Set elevation marks or otherwise determine the proper top elevation for the flowable fill.

- PLACEMENT OF FLOWABLE FILL

- Notify LANL STR a minimum of 48 hours prior to placement of flowable fill.

- Flowable fill may be placed by direct discharge from the truck, by pumping, or by other approved methods.

- The flowable fill shall be placed in a uniform manner that will prevent voids or segregation of the bedding and filling material.  If required, the flowable fill shall be consolidated with internal vibrators.

- Pipes, reinforcement, inserts, or other embedded parts shall be placed, supported, and secured in a manner that shall prevent the flowable fill from displacing, sagging, or from floating embedded items.

- Flowable fill shall be brought up uniformly to the fill line shown on the plans.  Formed walls or other bulkheads shall be constructed to withstand the exerted hydrostatic pressure and confine the material within a dedicated space.

- Placement of flowable fill shall start only when weather conditions are favorable.  The temperature shall be at least 35 degrees F and rising.  Flowable fill shall not be placed on frozen ground or when it is raining.

- CURING AND PROTECTION

- Immediately after placement, protect flowable fill from premature drying, excessively hot or cold temperatures and mechanical injury.

- The flowable fill shall not be subjected to load and shall remain undisturbed by construction activities for at least 24 hours after placement.

- FIELD QUALITY CONTROL

    - Testing of flowable fill is not necessarily required.  If testing is required, the Subcontractor shall employ an independent testing agency to perform compressive strength test cylinders.  Testing laboratory certification may be provided by Cement and Concrete Reference Lab (CCRL).

    - For field testing use a standard (15 lb) T-post driver to drive a #6 reinforcing bar with a flat end into the flowable fill material 24 hours after placement. Lift the driver until the bottom of the driver is even with a mark located 6 inches below the top of the rebar and then allow it to fall under its own weight. Remove and replace the flowable fill if fewer than 6 blows or more than 25 blows are required to drive the rebar 12 inches into the fill.

    - Provide unobstructed access to work and cooperate with appointed firm.

- DEFECTIVE FLOWABLE FILL

- Do not accept or place defective flowable fill that is not in conformance with acceptance criteria.  Return the fresh flowable fill to the supplier.

- Defective flowable fill is material having excessive honeycomb, embedded debris, higher than maximum compressive strength, or not conforming to required lines, details, dimensions, tolerances or specified requirements. Repair or replace defective flowable fill as directed by the LANL STR.

- Replace flowable fill not in conformance with details, tolerances, and other construction requirements at Contractor’s expense.

END OF SECTION

************************************************************

Do not delete the following reference information:

************************************************************

FOR LANL USE ONLY

This project specification is based on LANL Master Specification 31 2323.33, Rev. 5, dated August 27, 2012.