SECTION 33 1000

WATER UTILITIES

*************************************************************************************************************

LANL MASTER SPECIFICATION

Word file at http://engstandards.lanl.gov

This template must be edited for each project.  In doing so, specifier must add job-specific requirements.  Brackets are used in the text to indicate designer choices or locations where text must be supplied by the designer.  Once the choice is made or text supplied, remove the brackets.  The specifications must also be edited to delete specification requirements for processes, items, or designs that are not included in the project -- and specifier’s notes such as these.  To seek a variance from requirements in the specifications that are applicable, contact the Engineering Standards Manual Civil POC. Please contact POC with suggestions for improvement as well.

When assembling a specification package, include applicable specifications from all Divisions, especially Division 1, General Requirements.

Specification developed for ML-4 projects.  For ML-1, 2, and 3 applications, additional requirements and independent reviews should be added if increased confidence in procurement or execution is desired; see ESM Chapter 1 Section Z10 Specifications and Quality sections.

*****************************************************************************************************************

GENERAL

SECTION INCLUDES

Site water distribution piping system (potable and fire water) beyond the building wall.

LANL-PERFORMED WORK

LANL Utilities and Institutional Facilities (U&I) will perform final tie-in into existing water piping systems using Subcontractor-supplied material.

### LANL FURNISHED AND INSTALLED EQUIPMENT

### lanl will furnish and install post indicator valve padlocks.

ACTION SUBMITTALS

Submit the following:

Catalog data on pipe materials, pipe fittings, valves, and accessories and directional drilling pull (weak link) device and casing seals.

Installation instructions for valves and accessories.

Existing system pressure calculations to support new water pipe design and selection.

Certification of welders and qualified welding procedure.

[Submittals for the Horizontal Direction Drilling.]

Tracing wire continuity test report.

Catalog data on identification tape and tracing wire.

QUALITY ASSURANCE

Welders Certifications, Qualified Procedure Standards, and Weld Inspection/Testing.

      - Plastic Pipe: Comply with LANL ESM, Chapter 13 – Welding, Joining & NDE.

        - On-site and joining welding shall comply with LANL ESM, Chapter 13 – Welding, Joining & NDE; and Master Specification 01 4455, Onsite Welding & Joining Requirements.

- Use LANL Welding Procedures.

- Welders shall be qualified at LANL by LANL.

        - Off-site welding and joining shall comply with ESM, Chapter 13 – Welding, Joining & NDE; and Master Specification 01 4444, Offsite Welding & Joining Requirements.

Weld Inspection: Comply with ESM, Chapter 13 – Welding, Joining & NDE for PE pipe.

B.	LANL Subcontract Technical Representative (STR) shall submit the approved material and accessory catalog data, and certification of welders and qualified welding procedure to the LANL U&I water system engineer and the LANL construction inspector for verification of construction items and certifications during field quality assurance.

PRODUCTS

  - PRODUCT OPTIONS AND SUBSTITUTIONS

Alternate products may be accepted; follow Section 01 2500, Substitution Procedures.

  - Water BEyond building wall

******************************************************************************************************************

Consult with the LANL U&I Group water system representative for approval when selecting buried piping beyond the building wall and under roads.  Provide permanent buildings with a minimum pipe size of 4 inches for potable water supply line.

AWWA C151 Available Pipe Size: 4-64 inches.

Designer shall account for the diminished interior diameter of polyethylene pipe when designing for facility volume and velocity requirements.

******************************************************************************************************************

Ductile Iron Pipe: AWWA C151.

Joints: Bell and spigot, AWWA C111 rubber gaskets.

Fittings: AWWA C110, Ductile-Iron or Gray-Iron, Class 350 or AWWA C153, Ductile-Iron Compact Fittings, Class 350.

Pipe and Fittings: Cement mortar lined with bituminous outside coating.

Copper Tubing: ASTM B88, Type K, hard drawn or annealed.

Joints: AWS A5.8, BCuP silver braze.

Fittings: ANSI/ASME B16.22, wrought copper and copper alloy solder-joint.

**********************************************************************************************************

For PVC, AWWA C900 available pipe size is 4-12 inches.  Use ductile iron if static pressure is greater than 200 psig; system is dedicated, pumped fire protection pipeline; or pipeline is routed too close to an active steam line.  See minimum utility line clearances in ESM Civil Chapter.

**********************************************************************************************************

PVC Pipe: AWWA C900, DR18, pressure class 235.

Joints: Bell and spigot joint ASTM D3139 rubber gaskets ASTM F477.

Fittings: AWWA C110, Ductile-Iron or Gray-Iron, Class 350 or AWWA C153, Ductile-Iron Compact Fittings, Class 350.

Polyethylene Pipe and Fittings: AWWA C901 and ASTM D 3035 (3 inch or less) and AWWA C906 and ASTM F714 (4 inch to 63 inch), [Class 150, pressure rating 150] [Class 200, pressure rating 200]

Manufacturer: Performance Pipe – DriscoPlex 4000 FM, Ductile Iron Pipe Size (or as approved by LANL UI Water System Engineer).

Pipe: Polyethylene, high density, AWWA (C901), (C906), PPI-PE 4710, ASTM D3350 cell classification number PE 445574C.  Certifications by Factory Mutual Approvals Standard (FMA) Class Number 1613 and National Sanitation Foundation (NSF).

Fittings: Polyethylene, high density, AWWA (C901), (C906), ASTM D3261, PPI-PE 4710, ASTM D3350 cell classification number PE 445574C.  Certifications by Factory Mutual Approvals (FMA) and National Sanitation Foundation (NSF) NSF/ANSI 61.  The pipe manufacturer shall supply fittings and adapters.

Joints: Heat fusion per ASTM D2657 and manufacturer’s written instruction.

FLANGES, UNIONS, AND COUPLINGS

Copper Tubing:

Class 150 bronze unions with soldered joints.

Mechanical or Push-On Type Pipe, and Fittings Below Grade.

UL listed or FM approved.

Ductile Iron Pipe: Megalug Series 1100, malleable/ductile iron joint retainer/restraint gland with polymer, epoxy or bituminous outside coating and 1/2 inch minimum diameter asphalt coated tie rods.

PVC Pipe: for ductile iron joint use a compression connection and restraint system or retainer/restraint gland, Mueller AquaGrip System, Megalug Series 2000PV.

HDPE Pipe: for ductile iron joint use restraint devices designed to resist pull out forces. Internal pipe wall stiffeners must be used when restraining HDPE. Megalug Series 2000PV.

High Density Polyethylene

Flanges: Flanged joints shall be standard manufacturers flange adaptor that is butt fused to the pipe. Backup ring shall be ductile iron. Flange gaskets shall be installed.

Transitions: MJ Adaptors shall be standard manufacturers adaptor that is butt fused to the pipe for connecting to mechanical joint pipe, fittings, and appurtenances.  Manufacturers’ complete assembly shall be supplied; including stainless steel stiffener, extended gland bolts and nuts, gland and gasket.

VALVES, ABOVE GRADE

Ball Valves up to 2 inches:

Manufacturer: Nibco, Series 585-70.

MSS SP-110, 600 psi CWP, bronze, two piece body, chrome plated brass ball, full port, teflon seats and stuffing box ring, blowout proof stem, lever handle, solder or threaded ends.

Butterfly Valves over 2 inches:

Manufacturer: Nibco, Series LD 2000.

MSS SP-67, 200 psi CWP, ductile iron body, aluminum bronze disc, resilient replaceable EPDM seat, lug style, extended neck, lever handle, for use between ANSI Class 125/150 flanges.

Globe Valves up to 2 inches:

Manufacturer: Nibco, Series 211.

MSS SP-80, Class 125 bronze body, bronze trim, hand wheel, bronze disc, solder or threaded ends.

Gate Valves up to 2 inches:

Manufacturer: Nibco, Series 111.

MSS SP-80, Class 125 bronze body, bronze trim, rising stem, hand wheel, inside screw, solid wedge disc, solders or threaded ends.

VALVES, BELOW GRADE

**********************************************************************************************************

Comply with Civil Standard Drawings, ST-G3010-2 and ST-G3010-3 for below grade shut-off valve piping details.

**********************************************************************************************************

Gate Valves less than 2 inches:

Manufacturer: Nibco, Series T-176-A.

MSS SP-80, Class 300 bronze body, bronze trim, non-rising stem, hand wheel, inside screw, solid wedge disc, threaded ends.

Gate Valves 2 inches and over:

Manufacturer: Mueller, No. A-2360-8, 2 through 3 inch threaded, 2 inch square wrench nut or No.  A-2361-20 with accessories, use No. A-2361-23 when using retainer/restraint gland, or A-2361-77 AquaGrip System for PVC pipe, 4 inch and larger, 2 inch square wrench nut.

AWWA C509 for 2 and 3 inch, AWWA C515 for 4 through 12 inch, 250 psig and 350 psig pressure, UL listed or FM approved, non-rising stem, open left, threaded inlet and threaded outlet or mechanical joint inlet and outlet with mechanical joint with accessories unassembled, less accessories, or with appropriate transition gasket.

Tapping Valves 2 inches and over:

Manufacturer: Mueller, No. T-2360-16 with accessories, use No. T-2360-19 when using retainer/restraint gland, 2 through 3 inch, 2 inch square wrench nut or Mueller, No. T-2361-16 with accessories, use No. T-2361-19 when using retainer/restraint gland, 4 inch and larger.  No substitution.

AWWA C509 for 2 and 3 inch, AWWA C515 for 4 through 12 inch, 250 psig and 350 psig pressure, UL listed or FM approved, resilient wedge, non-rising stem, open left, ANSI Class 125/150 inlet flange, mechanical joint outlet with mechanical joint with accessories or less accessories, 2 inch square wrench nut.

Gate Valve (Post Indicator):

Manufacturer: Mueller, No. P-2361-20, with accessories, use No. P-2361-23 when using retainer/restraint gland, No Substitution.

UL listed and FM approved, 350 psig, non-rising stem with post indicator flange, open left, mechanical joint inlet and outlet with mechanical joint with accessories or less accessories.

### WATER PRESSURE REDUCING VALVES (PRV)

### ******************************************************************************************************************

Install PRV(s) in appropriately sized concrete vaults allowing full access for maintenance.  A LANL U&I Group water system representative shall approve design and installation of site PRVs and required PRV optional features.  Comply with the ESM Mechanical Chapter for building PRVs.

******************************************************************************************************************

Manufacturer: CLA-VAL, No. 90-01, No Substitution.

Single seated, hydraulically operated, pilot controlled, diaphragm type valve, 175 psi pressure rating, 180 degree F maximum water temperature and 15 to 75 psi adjustment range.  Pilot control; direct acting, adjustable, spring loaded, and normally open.  Valve construction; globe, ductile iron main valve body and cover, bronze main valve trim, and cast bronze pilot control with stainless steel trim. Repairs must be done without removing valve from line.

Optional Features:  [CV Flow Control (opening), CV Flow Control (closing), CK2 (Isolation Valve)].

Capacity/Size:

Flow: [     ] gpm

Size: [     ] inches with female NPT union ends or ANSI Class 150 flanged ends.

WATER PRESSURE REDUCING VALVE (PRV)

Manufacturer: CLA-VAL, No. 90-48, Low Flow Bypass, No Substitution.

Single seated, hydraulically operated, pilot controlled, diaphragm type valve, 175 psi pressure rating, 180 degree F maximum water temperature and 15 to 75 psi adjustment range.  Pilot control; direct acting, adjustable, spring loaded, and normally open.  Valve construction; globe, ductile iron main valve body and cover, bronze main valve trim, and cast bronze pilot control with stainless steel trim.  Repairs must be done without removing valve from line.

Optional Features: [  CV Flow Control (opening), CV  Flow Control (closing), CK2 (Isolation Valve ) ].

Capacity/Size:

Flow: [     ] gpm

Size: [     ] inches with ANSI Class 150 flanged ends.

WATER PRESSURE REDUCING VALVE (PRV)

Manufacturers:

CLA-VAL, No. 990

Watts Regulator Company, No. 25AUB or No. U5B.

Balanced single seat with bronze valve body and cover, stainless steel trim, integral strainer, 175 psi maximum water pressure, and standard adjustment range 8-80 psi. Repairs must be done without removing valve from line.

Capacity/Size:

Flow: [     ] gpm

Size: [     ] inches with NPT union ends.

FIRE HYDRANTS

********************************************************************************************************

Comply with Civil Standard Drawings ST-G3010-4 for fire hydrant piping detail.

********************************************************************************************************

Manufacturer: Mueller, Super Centurion 250, Style A423.  No Substitution.

UL listed or FM approved, dry barrel, 5 1/4 inch main valve opening, 3-way with 4 1/2 inch pumper nozzle and two 2 1/2 inch hose nozzles, ground level break flange, and mechanical joint inlet connection or Mueller AquaGrip System.  Hydrant factory painted yellow.

POST INDICATORS

********************************************************************************************************

Comply with Civil Standard Drawings ST-G3010-3 for PIV piping detail.

********************************************************************************************************

Manufacturer: Mueller, No. A20806.  No Substitution.

UL listed or FM approved, adjustable type, open left, complete with lower barrel sized for appropriate bury depth.

BACKFLOW PREVENTER, THREADED ENDS (Sizes up to 2 inches)

********************************************************************************************************

A LANL U&I Group water system representative shall approve design and installation of backflow preventers installed outside the building.  Do not install backflow preventer below grade.

********************************************************************************************************

Manufacturer: Watts Regulator Series 909 or models listed in the latest edition of Approved Backflow Prevention Assemblies by the University of Southern California Foundation for Cross Connection Control and Hydraulic Research.

Assembly, reduced-pressure, bronze body, with ball-type shut-off valves, FNPT ends, test cocks for in-line field testing, integral unions between body and shut-off valves, water temperature range 33 to 140 degrees F, rated working pressure 175 psi, meeting AWWA C511 and ASSE 1013.  Provide matching air gap drain.

Size: [     ] inch.

BACKFLOW PREVENTER, FLANGED ENDS (2 ½ inches and larger)

Manufacturer: Watts Regulator Series 909RPDA or models listed in the latest edition of Approved Backflow Prevention Assemblies by the University of Southern California Foundation for Cross Connection Control and Hydraulic Research.

Assembly, reduced-pressure, ductile or cast iron body epoxy coated internal and external, with UL approved OS & Y resilient wedge gate shut-off valves, flanged ends, test cocks for in-line field testing.  Water temperature range 33 to 140 degrees F, working pressure 175 psi, meeting AWWA C511 and ASSE 1013 and/or ASSE 1047.  Provide matching air gap drain.

Size: [     ] inch.

PRESSURE GAUGE

*****************************************************************************************************************

Refer to manufacturer’s recommendation for gauge pressure ranges.  Generally, a pressure range of twice the working pressure is recommended, with maximum working pressure not exceeding 75 percent of the range.  If pulsation occurs, working pressure should not exceed 65 percent of the pressure range.

*****************************************************************************************************************

Manufacturer: Reotemp Instruments.

ANSI B40.1, Grade A, 1 percent full scale accuracy, minimum 2 1/2 inch dial, phenolic or steel case, phosphor bronze bourdon tube and 1/4 inch NPT brass bottom connection. Furnish with brass ball valve.

Range: [     ] psi or [See drawings]

SERVICE SADDLE

*****************************************************************************************************************

A LANL U&I Group water system representative shall approve the design and installation of proposed taps on asbestos-cement water lines.  Asbestos-cement lines cannot be tapped directly; portion of main line will be replaced by LANL U&I group.

*****************************************************************************************************************

Manufacturer: Mueller, DR1A & S Series and DR2A & S Series for A-C and plastic.

Ductile iron, stainless steel strap, iron pipe outlet thread, and o-ring gasket.

Strap shape to be per manufacture recommendation for the existing pipe material.

TAPPING SLEEVE

*****************************************************************************************************************

A LANL U&I Group water system representative shall approve the design and installation of proposed taps on asbestos-cement water lines.  Asbestos-cement lines cannot be tapped directly; portion of main line will be replaced by LANL U&I group.

*****************************************************************************************************************

Manufacturer: Romac Industries, No. FTS 419, No Substitution.

Fabricated steel, ANSI Class 150 outlet flange, suitable for PVC, steel, ductile iron, and cast iron pipe, outlet flange size and sleeve O.D. to suit piping system, 4 inch and larger.

COUPLING

Manufacturer: Tyler Union, American Cast Iron Pipe Company, Star Pipe Products, solid sleeves, long style, MJ x MJ with appropriate sized gasket material.  AWWA C153, Ductile-Iron Compact Fittings, Class 350.

Steel, size suitable for pipeline material and diameter.

VALVE BOX

*****************************************************************************************************************

Comply with Civil Standard Drawing ST-G3010-1 for valve box detail.

*****************************************************************************************************************

Manufacturer: Tyler, Series 6860.

Cast iron, 5 1/4 inch shaft, screw type, lid marked “water”.

EXECUTION

  - EXAMINATION

Do not install underground piping when bedding is wet or frozen.

Verify that excavations are to required grade.

PREPARATION

Ream pipe and tube ends.  Remove burrs.

Remove scale and dirt on inside and outside of piping before assembly.

Keep open ends of pipe free from scale and dirt.  Whenever work is suspended during construction, or at the end of each workday, protect open ends with temporary plugs or caps.

PIPING TIE-IN

*****************************************************************************************************************

Refer to Civil Standard Drawings ST-G3010-2 for water piping tie-in details.

*****************************************************************************************************************

Tie-in to existing piping systems will be performed by LANL U&I group.  Excavation, backfill, and materials required for tie-in shall be provided by Subcontractor.  The tie-in will be inspected by the LANL STR and the LANL U&I Group water system representative.

New tie-ins shall be a minimum size of 2 inches when tying into existing piping systems that are 4 inches and larger.  If required, a pipe size reduction shall be made after the valve.

New tie-ins to existing piping systems 4 inches and larger shall be made by using a tee cut into the existing pipe and a valve on the new service line.  If the existing line cannot be removed from service a tapping tee and tapping valve can be used.

LANL STR will notify LANL U&I group at least 15 working days in advance to schedule tie-in.

Before tie-ins are scheduled, the LANL STR will ensure materials required for tie-in are on site, service lines have been tested and disinfected, material submittals and all test reports have been approved by LANL U&I Group, and bell hole excavation meets access and OSHA requirements.

BURIED PIPING

*****************************************************************************************************************

Tracer wire and test stations are required when specifying cast iron, ductile iron, and non-metallic piping. Comply with Civil Standard Drawings ST-G30GEN-3 for tracer wire/test station details and ST-G30GEN-4 for trenching detail.

Refer to the LANL Engineering Standards Manual, Civil Chapter 3, Section G30, for required minimum utility line clearances.

# Refer to Civil Standard Drawing ST-G30GEN-4 for trench width and piping burial depth.

*****************************************************************************************************************

Refer to Drawings and Section 31 2000, Earth Moving, for earth cover, bedding, tracer wire, wire continuity test, warning tape, documenting new or exposed existing utility location, etc., requirements.

Minimum cover over pipe shall be 48 inches measured from finish grade to top of pipe.

INSTALLATION

Comply with Uniform Plumbing Code (IAMPO) and applicable AWWA publications.

Provide non-conducting dielectric connections wherever jointing dissimilar metals.

Route piping in a straight line, in an orderly manner, and maintain gradient.

Set hydrants plumb and locate pumper nozzle perpendicular to and facing roadway.

Install piping to allow for expansion and contraction without stressing pipe, joints, or connected equipment.

Sleeve and caulk pipes penetrating exterior walls below grade to provide a waterproof installation.

*****************************************************************************************************************

Disinfecting solutions containing chlorine shall not exceed 12% active chlorine, greater concentrations can chemically attack and degrade polyethylene.

*****************************************************************************************************************

Disinfect water distribution system per Section [22 0816 or 33 1300].

Pressure test piping system per Section [22 0813].

*****************************************************************************************************************

Consult with a LANL Fire Protection Group representative and a LANL U&I Group water system representative for sites with dedicated non-potable water fire lines.

*****************************************************************************************************************

Fire hydrants tied into a non-potable dedicated fire loop shall have the hydrant bonnet painted black, and labeled “Non-Potable Water, Do Not Drink” per Section 22 0554, Identification for Plumbing, HVAC, and Fire Piping and Equipment.  Refer to Drawings for hydrant location.

Comply with AWWA M23, PVC Pipe Design Installation, for installation of PVC piping under roads.

POLYETHYLENE PIPING INSTALLATION

*************************************************************************************************************

Use metallic pipe if water line is installed less than 20 feet from steam and condensate lines.

*************************************************************************************************************

Lay coiled and small diameter piping on trench bottom in such a manner as to snake piping (“S” curves) in trench along the piping run.  This will insure that sufficient piping material is available for expansion and contraction.  Lay piping in trench and allow for temperature stabilization to minimize thermal expansion and contraction.

Cold (field) bending allowable bend radius is determined by pipe diameter and dimension ratio.  Minimum bend radius shall be per manufacturers written instructions.  Bends shall not be made where fittings are in the bend.

Provide minimum of 5 feet of cover over piping installed under any roadways and vehicle parking areas.

Perform butt heat-fusion joining in accordance with ASTM D2657 and the manufacturer’s written instructions.  See PART 1, Quality Assurance article.

Make connections to PE-to-DI or PVC pipe and mechanical connections, valves, and appurtenances with transition fittings that are butt fused onto the PE pipe. Provide complete assemblies and install per manufacturers written instruction.

Thrust blocks and restraint shall be installed at fire hydrants, tees and change in direction per the manufacturer’s written instructions.

Horizontal Directional Drilling or Pipe Bursting

Crossing of paved streets or roadways or other areas, if approved by LANL U&I group representative, may be accomplished by horizontal directional drilling (HDD) or pipe bursting, whenever practical. The HDD bore shall be kept to a maximum of 2 inches larger than the pipe. Care shall be exercised to ensure the paved surface is not damaged during the drilling operation.

Top of HDD shall have a minimum below grade bury depth of 48 inches and a minimum bury depth of 60 inches below any paved surface. Depth shall not exceed excavation by standard, conventional means and shall be approved by LANL U&I group representative.

When pulling in pipe the pulling force shall be monitored and kept below the Allowable Tensile Load (ATL) value of the pipe size and material per manufacturer’s recommendation. Both pipe ends shall be monitored for continuous, smooth movement. Pulling load from the equipment shall be monitored and the pipe lead end shall be equipped with a weak link device to disengage at the ATL or below. Manufacturer’s procedures and design parameters shall be followed, in addition to ASTM F1962.

Polyethylene pipe shall extend 3-5 percent of the pulled-in length past the termination points to allow for contraction. Polyethylene pipe shall be allowed 24 hours to recover from the pulling stress and contract to original pre-pull length and allowed to stabilize to buried soil temperature before final tie-ins are accomplished. A minimum of five (5) feet of pipe shall extend beyond the drilling entrance/exit hole to allow for pipe damage assessment. Tracing wire shall be pulled in with the polyethylene pipe.

END OF SECTION

************************************************************

Do not delete the following reference information:

************************************************************

THE FOLLOWING STATEMENT IS FOR LANL USE ONLY

This project specification is based on LANL Master Specification 33 1000 Rev. 8, dated January 23, 2018.