# SECTION 33 5100

# NATURAL GAS DISTRIBUTION

*************************************************************************************************************

LANL MASTER SPECIFICATION SECTION

Word file at https://engstandards.lanl.gov/specs.shtml

Rev. 11 Summary of changes Added 8400 BlackStripe and new WPS table. Various updates and clarifications to text and authors notes.

The designer is cautioned that the piping design of the distribution system to the exit of the service meter assembly (or, where no meter is provided, the outlet of the service regulator or service shutoff valve) is governed by ASME B31.8 AND 49CFR192.  The most stringent code or CFR shall apply.  While ASME codes are issued at discrete intervals, the CFR may change at any time.  The design should check the CFR website for the most current requirements ()

After the service point (above), the governing code is NFPA 54, National Fuel Gas Code (replacing ASME B31.2, ANSI Z21.3, and ANSI Z83.1) and should follow 23 1123, Facility Natural-Gas Piping.  Other codes may apply for safety features of the gas train.  See ESM Chapter 17 for information on those requirements

This template must be edited for each project.  In doing so, specifier must add job-specific requirements.  Brackets are used in the text to indicate designer choices or locations where text must be supplied by the designer.  Once the choice is made or text supplied, remove the brackets.  Section must also be edited to add or delete requirements for processes, items, or designs that are not included in the project -- and specifier’s notes such as these.  To seek a variance from requirements that are applicable, contact the Engineering Standards Manual Pressure Safety POC, Civil POC, and/or Natural Gas SME. Please contact POC with suggestions for improvement as well.

When assembling a specification package, include applicable sections from all Divisions, especially Division 1, General requirements.

Section developed for ML-4 projects.  For ML-1, 2, and 3 applications, additional requirements and independent reviews should be added if increased confidence in procurement or execution is desired; see ESM Chapter 1 Section Z10 Specifications and Quality sections.

*************************************************************************************************************

# PART 1 	GENERAL

SECTION INCLUDES

Site distribution gas piping system including above and below grade piping and appurtenances upstream of and including the low pressure regulator station.

Design requirements

Most widely or uniquely used at LANL applications are listed. The code of record is:

ASME B31.8–[2020 or state year], Gas Transmission and Distribution Piping Systems

CFR TITLE 49—Transportation; Part 192—Transportation of Natural and Other Gas by Pipeline: Minimum Federal Safety Standards (as of [12/16/2022]).

The design requirements for this system are as shown below:

*************************************************************************************************************
Total connected natural gas load in BTUs per hour, heat input requirement for each connected device in BTUs per hour, and pressure (psig) requirement at building wall.  As part of the design, provide the total connected natural gas load in BTUs per hour, input requirement for each connected device in BTUs per hour with device room location, and pressure (IWC or PSIG) requirement at building wall.

Pipe shall be limited in design to less than 20 percent of SMYS.

Design pressure is 100 psig for wall thickness and testing.

Operating pressure is 60 psig for piping capacity.

Maximum actual operating pressure is 60 psig.

*************************************************************************************************************

Design Pressure Distribution System:  100 psig

Design Temperature:  600 F buried pipe

Design temperatures for above ground pipe are

Winter: 5 degrees F dry bulb B.

Summer: 89 degrees F dry bulb, 60 degrees F wet bulb

Specified minimum yield strength (SMYS) of system:  [19%]

Class location unit:  4 (mandatory)

Total Demand for facility:  [ xx ]BTU/Hr [minimum 100,000 BTU/Hr]

Total Design Pressure for Facility [1, 2, 3, 4, …]:  [XX psig or XX inches water column]

Design Temperature:  600 F

Device [1, 2, 3, 4, ….]: BTU/Hr : [Facility and Room Location]

Total Required Natural Gas   [5,000,000] BTU/Hr

*************************************************************************************************************

Submittals shall be approved by the LANL U&I Group gas system representative and the LANL Construction Inspector

*************************************************************************************************************

ACTION SUBMITTALS

Submit the following for material, equipment, worker certifications & inspection reports:

      - Catalog data on regulators, pipe materials, pipe fittings, valves, pipe coating, pipe pig, accessories, directional drilling pull (weak link) device, special tooling (e.g., Lycofit fittings), and casing seals.

      - Certified Material Test Reports (CMTR) for metallic piping and components required by the code of record ASTM A269.

      - Certificate of Compliance (CoC) to show compliance to the applicable codes and standards as identified in this specification, specifically nonmetallic materials.

      - Per the requirements of 01 4444 Offsite Welding and Joining Requirements and/or 01 4455 Onsite Welding and Joining Requirements, submit:

******************************************************************************************************

Welding fabrications are typically “onsite” and therefore fall under the requirements of 01 4455. In the event of Offsite only, delete submittals below regarding Onsite welding and other mentions of onsite work including Part 3 (and, if all onsite, delete all section wording on offsite). For high risk applications such as ML-1 or ML-2, add submittals for “Weld Filler Material Control Procedures” and “Filler Material Certified Material Test Reports (CMTRs)” when required.  Add “Post-Weld Heat Treatment Procedures” when required.

*******************************************************************************************************

      - Welding Procedure Specification (WPS) and supporting Procedure Qualification Record (PQR).  [Note:  For Onsite welding use of LANL WPS/PQR is the default; coordinate usage with the LANL CWI; no submittal required]

      - Welder Performance Qualification Records (WPQR) including continuity [Note: For Onsite, welders are tested by LANL who will produce WPQR and track continuity; this includes brazing, bonding and fusing; no submittal required]

      - Inspector qualification records

      - Inspection procedures

      - Weld inspection report(s) and weld map(s)

      - [Submittals for the Horizontal Directional Drilling. Include calculations showing that proposed pipe can withstand all installation and in use stressors]

      - [Pipe pigging inspection report for 4-inch diameter and larger pipe and for all piping sizes with lengths greater than 500 feet.]

      - [Tracer wire catalog data. Installed with non-metallic pipe]

      - [Tracing wire continuity test report.]

      - Catalog data on identification tape.

    - Action Submittals - Fabrication

      - Qualifications

        - Installer Qualifications

          - Documented OQ program per 49 CFR 192 Subpart “N” for all covered tasks

          - Special training required for mechanical fitting installation (e.g., Lycofit fittings).

      - Installation Instructions

      - Procedures

        - Prior to receiving materials submit the Material Control Procedure.

        - Before fabrication, submit the following procedures:

          - Code leak testing

          - Cleaning

      - Certified Factory Acceptance Test Report

        - Indicate codes under which all inspections and tests were conducted at the factory, include inspection and testing forms and logs.

        - Instrument Calibration Certificates for equipment used during the Factory Acceptance Test.

      - Field Test Reports

        - Field Test and Inspection Report providing evidence that the applicable code or standard was met.

Note:  Commissioning activities are the responsibility of LANL Utilities. The Constructor shall coordinate and provide all records necessary for LANL Utilities to complete the commissioning activities.

      - Commissioning (ASME B31.8, 841)

        - The following commissioning records shall be maintained as permanent records:

          - cleaning and drying procedures

          - cleaning and drying results

          - function-testing records of pipeline monitoring

          - control equipment systems

      - [Submittals for the Horizontal Directional Drilling.]

      - [Pipe pigging inspection report for 4-inch diameter and larger pipe and for all piping sizes with lengths greater than 500 feet.]

      - [Tracing wire continuity test report, install with non-metallic pipe.]

      - Certifications

        - Instrument Calibration Certificates for equipment used during the Factory Acceptance Test

  - QUALITY ASSURANCE

    - WPS, WPQR, and Weld Inspection/Testing

      - Exterior Steel Pipe: API Standard 1104

        - For pipe diameters up to 2.375” O.D., use LANL WPS API 1000-2

        - For pipe diameters greater than 2.375” O.D. and up to 12.75” O.D., use LANL WPS API 1000-1.

        - On-site and joining welding shall comply with LANL ESM, Chapter 13 – Welding, Joining & NDE; and Master Specification Section 01 4455, Onsite Welding & Joining Requirements.

          - Use LANL Welding Procedures

          - Welders shall be qualified at LANL by LANL

        - Off-site welding and joining shall comply with ESM, Chapter 13 – Welding, Joining & NDE; and Master Specification 01 4444, Offsite Welding & Joining Requirements.

        - Weld Inspection: Weld inspection acceptance shall be in accordance with API Standard 1104, Section 9, for steel pipe and LANL ESM Chapter 13, Volume 6 – Welding, Joining & NDE.  Cracks shall not be accepted. Certified Weld Inspector (CWI) shall visually inspect 100% of the completed welds. Inspector should visually inspect base metal, filler metal, weld joint prep, temperature, and inter-pass temperature, weld fit up, root and subsequent passes when on-site.

      - Plastic Pipe: Comply with ESM Chapter 13, Volume 6 – Welding, Joining & NDE and 49 CFR 192.287.

        - LANL WPS to use for joining HDPE Performance Pipe

|  | Pipe “B” Downstream |
| --- | --- |
| Pipe “A” (Upstream) | 8100 Yellow | 8300 Blk w/ Yellow stripes | 8400 Yellow w/ Blk stripes |
| 8100 | 7000-Gasx-PPE2 | 7000-Gasx-PPE2 | 7000-Gasx-PPE3 |
| 8300 | 7000-Gasx-PPE2 | 7000-Gasx-PPE3 (or PPE2) | 7000-Gasx-PPE3 |
| 8400 | 7000-Gasx-PPE3 | 7000-Gasx-PPE3 | 7000-Gasx-PPE3 |

Table Notes:

8100 Driscopipe:   The original, yellow outside/black inside, exists both as installed and limited stock on hand

8300 Yellowstripe:  Black with 4 yellow stripes, exists both as installed and limited stock on hand

8400 BlackStripe:    Yellow with 3 black stripes

        - On-site and joining welding shall comply with LANL ESM, Chapter 13 – Welding, Joining, & NDE; and Master Specification 01 4455, Onsite Welding & Joining Requirements.

          - Use LANL Welding Procedures

          - Welders shall be qualified at LANL by LANL

        - Off-site welding and joining shall comply with ESM, Chapter 13 – Welding, Joining & NDE; and Master Specification 01 4444, Offsite Welding & Joining Requirements.

        - Installation and inspection of each PE heat fusion joints, except for electrofusion, shall comply with ASTM F2620-12.

        - Electrofusion joints shall be made in accordance to user’s written procedures and the fitting manufacturer’s installation instructions.

      - ASME B31.8 WELD INSPECTION REQUIREMENTS

        - Inspection of Welds on Piping Systems Intended to Operate at Hoop Stress Levels of Less Than 20% of the Specified Minimum Yield Strength:

          - The quality of welds shall be checked visually on a sampling basis, and defective welds shall be repaired or removed from the line.

        - Plastic pipe and tubing shall be carefully inspected for cuts, scratches, gouges, and other imperfections before use, and any pipe or tubing containing harmful imperfections shall be rejected.  Each installation shall be field inspected to detect harmful imperfections. Any such imperfections found shall be eliminated.

        - If damage (e.g., scratches, gouges, etc.) exceeds 10% of the nominal wall thickness, then the pipe shall be replaced in its entirety

    - Clean and pig piping 4-inch diameter and larger, and all piping sizes with lengths greater than 500 feet.

LANL-PERFORMED WORK

LANL Utilities and Institutional Facilities Engineering (U&I) will tie into existing gas piping system.

LANL U&I will install regulator station and adjust outlet pressure of gas regulators.

Related SECtions

Section 01 2500, Substitution Procedures

Section 01 3300, Submittal Procedures

Section 01 4000, Quality Requirements

Section 01 4115, Pressure Safety Submittals

[Section 01 4444, Offsite Welding and Joining Requirements]

Section 01 4455, Onsite Welding and Joining Requirements

Section 01 4631, Welding of B31 Piping

Section 01 4731, Flange Assembly for B31 Systems

Section 09 9100, Painting

Section 22 0529, Hangers for Supports for Plumbing Piping and Equipment

Section 22 0548.23, Vibration and Seismic Controls for Mechanical Systems

Section 22 0713, Plumbing and HVAC Insulation

Section 22 0813, Testing Piping Systems

Section 31 2000, Earth Moving

  - References

    - API

- API Specification 5L, Specification for Line Pipe, [46th Edition, 2018, effective 5/1/2019]

    - ASME

- ASME B1.20.1 – [2013], Pipe Threads, General Purpose (Inch)

- ASME B16.3 – [2016], Malleable Iron Threaded Fittings

- ASME B16.5 – [2017], Pipe Flanges and Flanged Fittings NPS 1/2 Through NPS 24 Metric/Inch Standard

- ASME B16.9 - [2018], Factory-Made Wrought Butt-welding Fittings

- ASME B16.11 - [2016], Forged Fittings, Socket-Welding and Threaded

- ASME B16.21 – [2011], Nonmetallic Flat Gaskets for Pipe Flanges

- ASME B16.34 – [2017], Valves – Flanged, Threaded, and Welded End

- ASME B16.40 – [2019], Manually Operated Thermoplastic Gas Shutoffs and  Valves in Gas Distribution

- ASME B18.2.1 – [], Square, Hex, Heavy Hex, and Askew Head Bolts and Hex, Heavy Hex, Hex Flange, Lobed Head, and Lag Screws (Inch Series)

- ASME B18.2.2 – [], Nuts for General Applications: Machine Screw Nuts, Hex, Square, Hex Flange, and Coupling Nuts (Inch Series)

- ASME B18.21.1 –[year], Washers: Helical Spring-Lock, Tooth Lock, and Plain Washers (Inch Series)

- ASME B31.8 – [2018], Gas Transmission and Distribution Piping Systems

- ASME PCC-2, Repair of Pressure Equipment and Piping

    - ASTM

- ASTM A53/A53M - [2018], Standard Specification for Pipe, Steel, Black and Hot-Dipped, Zinc-Coated, Welded and Seamless

- ASTM A105/A105M – [2018] Carbon Steel Forgings for Piping Applications.

- A106/A106M – [2019] Standard Specification for Seamless Carbon Steel Pipe for High-Temperature Service

- ASTM A234/A234M REV A [2019] Standard Specification for Piping Fittings of Wrought Carbon Steel and Alloy Steel for Moderate and High Temperature Service

- ASTM D2513 – [2019], Standard Specification for Polyethylene (PE) Gas Pressure Pipe, Tubing, and Fittings

- ASTM D3350-2014, Standard Specification for Polyethylene Plastics Pipe and Fittings Materials (not listed)

- ASTM F1962 – [2011], Standard Guide for Use of Maxi-Horizontal Directional Drilling for Placement of Polyethylene Pipe or Conduit Under Obstacles, Including River Crossings

- ASTM F1973 – [2013] “Standard Specification for Factory Assembled Anodeless Risers and Transition Fittings in Polyethylene (PE) and Polyamide 11 (PA 11) and Polyamide 12 (PA 12) Fuel Gas Distribution Systems”

- ASTM F2620 – 2012, Standard Practice for Heat Fusion Joining of Polyethylene Pipe and Fittings

- ASTM G62 – [2014], Standard Test Method for Holiday Detection in Pipeline Coatings

    - MSS

- MSS SP-97 – [2012], Integrally Reinforced Forged Branch Outlet Fittings – Socket Welding, Threaded, and Buttwelding Ends

PRODUCTS

  - PRODUCT OPTIONS AND SUBSTITUTIONS

Alternate products may be accepted; follow Section 01 2500, Substitution Procedures except those item marked “No Substitution”..

POLYETHYLENE PIPING, BELOW GRADE

*************************************************************************************************************

Do not use polyethylene piping when design pressure exceeds gauge pressure of 100 psig 
(49 CFR 192.123). Provide 1-inch, 1-1/4 inch, 2-inch, or 3-inch PE service line and 2-inch-minimum PE main line as required for capacity and to integrate with the existing piping.

No not use electrofusion fittings without contacting a LANL U&I Group gas system representative.

Provide calculations for performing Horizontal Directional Drilling (HDD) or other pipe pulling operations to ensure the piping will handle all stresses experienced during and after construction. Minimum SDR is SDR11 for HDD.

*************************************************************************************************************

Manufacturer: Chevron-Phillips Performance Pipe (Driscopipe 8100 or Yellowstripe 8300 or Blackstripe 8400), No Substitution.

      - Pipe: Polyethylene, high density, ASTM D2513, PPI-PE4710, SDR 11 iron pipe size, ASTM D3350 cell classification number 445574C.

        - Nominal Pipe Size: [2, 3, 4, 5, 6, 8, 10, 12] inch

      - Fusion Fittings: Polyethylene, high density, butt heat fusion type, ASTM D2513, PE4710, SDR 11, ASTM D3350 cell classification number 445574C

        - Nominal Pipe Size Fittings: [2, 3, 4, 5, 6, 8, 10, 12] inch

************************************************************************************************************

Do not use electrofusion fittings without contacting a LANL U&I Group gas system representative.

************************************************************************************************************

      - [Electro-Fusion Fittings: Polyethylene, high density, butt heat fusion type, ASTM D2513, PE4710, SDR 11, ASTM D3350 cell classification number 445574C

        - Nominal Pipe Size Fittings: [2, 3, 4, 5, 6, 8, 10, 12] inch]

Mechanical Fittings: Required for tie in to Drisco 8000-series HDPE piping, No Substitutions.

      - R.W. LYALL, LYCOFIT Coupling, ASTM D 2513, PPI-PE 4710 (PE 3408), SDR11, iron pipe size 1 inch through 2 inch.

- Nominal Pipe Size Fittings: [1, 1 ¼, 1 ½, 1 ¾, 2] inch

      - Elster Permaset XL Coupling, ASTM D 2513, PPI-PE 4710 (PE 3408), SDR11, iron pipe size 3 inch through 8 inch.

- Nominal Pipe Size Fittings: [3, 4, 5, 6, 8] inch

STEEL PIPING, BELOW GRADE

*************************************************************************************************************

Contact a LANL U&I Group gas system representative for approval to use steel piping below grade. Provide minimum 2-inch steel service line.

*************************************************************************************************************

Pipe: Standard wall, black steel, ASTM A53, Type E, Grade B or API 5L, EW, Grade B or ASTM A106, Grade B.

- Nominal Pipe Size: [1, 2, 3, 4, 5, 6, 8, 10, 12] inch

- Schedule: [40,80,160, standard]

Fittings: Standard wall, black steel, butt-welding type, ASME B16.9, ASTM A234, Grade WPB.

- Nominal Pipe Size: [1, 2, 3, 4, 5, 6, 8, 10, 12] inch

- Fitting type: [elbow, short radius elbow, reducing elbow, etc.]

Coating: Factory applied fused system consisting of; an adhesive primer layer, with minimum 10 mil thermoplastic elastomer layer and minimum 40 mil polyolefin top layer containing UV protection; or alternate of an epoxy primer layer with minimum 50 mil high density polyethylene top layer; or an approved equal by the LANL U&I Group gas system representative.

Manufacturers:

- Tyco Adhesives, Synergy Plant Coating System

- Tyco Adhesives, VANGUARD Plant Coating System

Product marking shall be in accordance with ASTM A53, Section 21. Product marking shall be transferred to and stenciled to the outside of the pipe coating. Minimum transferred information shall include; pipe specification, grade, size, type, and heat number in accordance with the certified material test report and the product marking.

STEEL PIPING, ABOVE GRADE

Pipe: Standard wall, black steel, ASTM A53, Type E, Grade B or API 5L EW, Grade B or ASTM A106, Grade B.  Welded for pipe sizes above 2 inches, threaded for pipe sizes 2 inches or less.

- Nominal Pipe Size: [1, 2, 3, 4, 5, 6, 8, 10, 12] inch

- Schedule: [40, standard]

Fittings 2” or less: Malleable iron, threaded type, ANSI B16.3, Class 150

- Nominal Pipe Size: [1, 1 ¼, 1 ½, 1 ¾, 2] inch

- Fitting type:  [elbow, tee, cross, coupling, etc…]

Fittings greater than 2”: Standard wall, black steel, butt welding type, ASME B16.9, ASTM A234, Grade WPB.

- Nominal Pipe Size: [3, 4, 5, 6, 8, 10, 12] inch

- Fitting type: [elbow, short radius elbow, reducing elbow, etc.]

Flanges: Forged steel, ASTM A105, ANSI Class 150, weld neck, raised face, concentric serrations dimensions per ANSI B16.5.

- Nominal Pipe Size: [3, 4, 5, 6, 8, 10, 12] inch

Gasket ASME B16.21, Type “F”, 1/8” thickness, Gasket type: Flat Ring Material: Neoprene, durometer range A, hardness 50-65.

- Nominal Pipe Size: [3, 4, 5, 6, 8, 10, 12] inch

Flange bolts ASME B18.2.1, ASTM A307 Grade B, UNC threads; hex nuts ASME B18.2.2 ASTM A563 Grade A, UNC threads; and Type A plain washers ASME B18.21.1 Hardened Plain Carbon Steel Washer (ASTM F436 Washers), Bolt or stud number, diameter, and lengths as required by ASME B16.5 Class 150.

- [Machine Bolt, Stud Bolt diameter and thread: ½ inch UNC]

- [Machine Bolt, Stud Bolt length:  2 inch or 2.25 inch respectively]

- [Nut quantity: 4]

- Nut Size and type: hex nut, ½ inch UNC

- Nut quantity: 8

- [Washer size: Type A Series N plain carbon steel washer ½ inch]

- Washer quantity:  8

PRESSURE REGULATOR STATION

*************************************************************************************************************

Regulator stations are limited to the stations and regulators identified in the Civil Standard Drawings ST-G3060-2.  Specific regulator part numbers will need to be determined based on delivery requirements.

For parameters outside Civil Drawings ST-G3060-2, contact the ES-UI system engineer for regulator station design.

*************************************************************************************************************

Regulator station and regulator shall meet Civil Standard Drawing ST-G3060-2 sheet [1, 2, 3, 4], No Substitutions.

LANL's U&I group will install, and adjust outlet pressure of gas regulator station in conjunction with the subcontractor.

SHUT-OFF VALVE, ABOVE GRADE, THREADED ENDS, 1 & 2 inch

Manufacturer: Balon Series S, No Substitution.

      - Valve: Ductile iron body, threaded ends, non-lubricated full port opening ball valve, lever-operated, 1000 psig working pressure, size [ 1 ], [ 2 ] inch.

    - [1” valve Part # 1F-S42-SE]

    - [2” valve Part # 2F-S42-SE]

SHUT-OFF VALVE, ABOVE GRADE, FLANGED ENDS, 3 through 12 inch

Manufacturer: Balon Series F, No Substitution.

      - Steel body, flanged ends, non-lubricated full port opening ball valve, lever-operated, Class 150, size [ 2 ], [ 3 ], [ 4 ] inch. Balon Series F,  No Substitution

- [2” valve Part # 2F-F13-RF]

- [3” valve Part # 3F- F13-RF]

- [4” valve Part # 4F- F13-RF]

      - Steel body, flanged ends, non-lubricated full port opening ball valve, gear-operated, Class 150, size [ 6 ], [ 8 ] inch. Balon Series F,  No Substitution

- [6” valve Part # 6F-F13-RF]

- [8” valve Part # 8F-F13-RF]

Manufacturer: Balon Series T, No Substitution.

      - Steel body, flanged ends, non-lubricated full port opening ball valve, gear-operated, Class 150, size [ 10 ], [ 12 ] inch. Balon Series T,  No Substitution

- [10” valve Part # 10F-T13-RF]

- [12” valve Part # 12F-T13-RF]

SHUT-OFF VALVE, ABOVE AND BELOW GRADE, WELDED ENDS

Manufacturer: Balon US Series Weld X Weld,  No Substitution.

      - Valve: Steel body, butt welded ends, non-lubricated full port opening ball valve, Drive nut operated, Class 150, size [ 2 ], [ 3 ], [ 4 ], [6] inch.

[2” valve Part # 2F-US13-BW]

[3” valve Part # 3F-US13-BW]

[4” valve Part # 4F-US13-BW]

[6” valve Part # 6F-US13-BW]

SHUT-OFF VALVE, BELOW GRADE, POLYETHYLENE

Manufacturer: Nordstrom Poly-Gas,  No Substitution.

Ball Valve for natural gas service ASME B16.40, ASTM D 2513, material PPI-PE 4710 (PE 3408), for use with Performance Pipe (Driscopipe 8100 or Yellowstripe 8300 or BlackStripe 8400 designation), SDR11, iron pipe size 100 psig service pressure, butt fusion end connections.  Full bore when available.

- Valve Size: [ 1 ], [ 1 1/4 ], [ 2 ], [ 3 ] , [ 4 ] inch

    - [1” valve Part # 1-89111]

    - [1-1/4” valve Part # 1.25-89111]

    - [2” valve Part # 2-89111]

    - [3” valve Part # 3-89111]

    - [4” valve Part # 4-89111]

ANODELESS RISER

Manufacturer: R.W. Lyall and Company, Inc.,  No Substitution

Prebent, 30-inch-radius minimum, ASTM F1973, ASTM D 2513, PPI-PE 4710 (PE 3408), SDR11, iron pipe size NPT steel end by HDPE butt fusion, size to match piping system.  Steel pipe shall be standard wall, black steel, API 5L EW, Grade A or ASTM A53, Type E, Grade A for 1 1/2 inch and less, Grade B for 2 inch and larger.  The mechanical joint shall be provided with a tamper proof, gas tight connection and seal per ASTM D2513, Category 1.

Required size:  [1, 1 ½, 2, 4, 5, 8] inch

TRANSITION FITTING

Manufacturer: R.W. Lyall and Company, Inc.,  No Substitution

Preformed steel pipe to HDPE pipe, ASTM D 2513, PPI-PE 4710 (PE 3408), SDR11, iron pipe size beveled steel end for welding by PE butt fusion, size to match piping system.  Steel pipe shall be standard wall, black steel, API 5L EW, Grade A or ASTM A53, Type E, Grade A for 1 1/2 inch and less, Grade B for 2 inch through 8 inch.  The mechanical joint shall be provided with a tamper proof, gas tight connection and seal per ASTM D2513, Category 1.

Required size:  [2, 4, 6, 8] inch

Branch Connection

Manufacturer: Bonney Forge or approved alternative

MSS SP-97, or ASME B16.11 paragraph 1.1.2 Special Fittings, Branch connection style is a Weld-o-let.    Run to branch ratio must be 4:1 or greater.  Material shall comply with ASTM A105.

      - Run size:  [4, 6, 8, 10] inch

      - Run schedule:  [40, 80, 160]

      - Branch Weldolet size:  [1], [1-1/4], [2], [3], [4], [6] inch

      - Branch Weldolet schedule:  [40, 80, 160]

VALVE BOX

Manufacturer: Tyler, Series 6860

      - Valve Box: Cast iron, 5 1/4 inch shaft screw type, with lid marked GAS, length to suit burial depth.

Test lead stations

Below Grade Test Station

      - Manufacturer: C.P services, Glenn Test station, Non-locking lid

Above Grade Test Station

      - Rhino Tri-view Test Station 72”

TEST PLUG (PETE’s PLUG II or equal)

1/4 inch NPT, brass body, neoprene core, rated for 1,000 psig, complete with sealing cap and gasket, to receive 1/8 inch O.D. probe.

      - Pete’s Plug II Product Number 100

carrier pipe spacers and seal

GPT nonmetallic spacers model PE.

GPT Link-Seal® Modular seal- model “O”.

      - [2” pipe and 4” carrier pipe- Link-Seal® LS-300-C with 6 links.]

      - [3” pipe and 5” carrier pipe- Link-Seal® LS-300-C with 8 links.]

      - [4” pipe and 6” carrier pipe- Link-Seal® LS-300-C with 10 links.]

      - [6” pipe and 10” carrier pipe- Link-Seal® LS-475-C with 10 links.]

      - [8” pipe and 12” carrier pipe- Link-Seal® LS-475-C with 12 links.]

      - [10” pipe and 14” carrier pipe- Link-Seal® LS-410-C with 15 links.]

      - [12” pipe and 16” carrier pipe- Link-Seal® LS-475-C with 17 links.]

EXECUTION

  - preparation

Square and ream pipe ends and remove burrs.

Remove scale and dirt on inside and outside of piping before assembly.

Keep open ends of pipe free from scale and dirt.  Whenever work is suspended during construction, or at the end of each workday, protect open ends with temporary plugs or caps.

# *************************************************************************************************************

Butt weld ends shall meet ASME B31.8 Mandatory Appendix I, End Preparations For Buttwelding, including transitions.  Joint details shall be provided in drawings or sketches issued by Engineer of Record.

# *************************************************************************************************************

  - GENERAL INSTALLATION

Furnish and install gas piping in accordance with ASME B31.8 Gas Transmission and Distribution Piping Systems, and 49 CFR 192 Code of Federal Regulations.

Do not run gas piping below buildings, structures, or in crawl spaces.

Do not run gas piping under walks and equipment pads adjacent to building.  If unavoidable, sleeve line with non-metallic piping.

Flange installation shall be in accordance with Section 01 4731, Flange Assembly for B31 Systems.

Steel slip-on flanges, socket welds, and weld-o-lets shall be welded to the dimensions provided in Section 01 4631, Welding of B31 Piping.

Paint outside gas regulator piping, valves, and appurtenances above ground. Gas piping color should be Forest Green and valves should be Slate Grey. Refer to Section 09 9100, Painting.

Support piping in accordance with Section 22 0529, Hangers and Supports for Plumbing Piping and Equipment.

Minimum cover over pipe shall be measured from finish grade to top of pipe.

Butt weld ends shall be in accordance with ASME B31.8 Mandatory Appendix I, End Preparations for Buttwelding.

Meet the requirements of 49CFR192.627 Tapping Pipelines Under Pressure, 49CFR192.629 Purging of Pipelines, B31.8 841.2.7 Precautions to Avoid Explosions of Gas–Air Mixtures or Uncontrolled Fires During Construction Operations, and B31.8 831.4.2 Special Requirements (j).

cleaning of natural gas piping interior

Use a pipeline pig to clean the interior of natural gas piping.  The pipeline pig used shall be of a type and configuration to provide optimum cleaning of scale, debris, and moisture from the pipeline interior.

      - Soft pigs shall be used with polyethylene pipe to avoid damage to the pipe.

A pressuring system shall be used to provide sufficient energy to drive the pig but to not overpressure the pipeline, the pressure to drive the pig shall not exceed the final test pressure.

A pig catcher of a design to provide a safe and effective means to receive the pig as it discharges from the line shall be used.

POLYETHYLENE PIPING INSTALLATION

# *************************************************************************************************************

# Refer to Civil Standard Drawing ST-G30GEN-4 for trench width and piping burial depth.

# *************************************************************************************************************

Lay piping on trench bottom in such a manner as to snake piping from one side of trench to the other with one cycle approximately every 40 feet.  This will insure that sufficient piping material is available for expansion and contraction.

Provide minimum of 5 feet of cover over piping installed under any roadways and vehicle parking areas.  Minimum cover over pipe shall be from finish grade to top of pipe.

*************************************************************************************************************

Use steel pipe if gas line is installed less than 20 feet from steam and condensate lines.

*************************************************************************************************************

Perform butt heat-fusion joining in accordance with ASTM F2620 and manufacturer’s written instructions.  See PART 1, Quality Assurance article, including acceptable LANL Welding Procedures.

*************************************************************************************************************

Refer to Civil Standard Drawings ST-G30GEN-3 and ST-G30GEN-4 for trenching, piping burial depth, warning tape, and tracer wire details.

Refer to the Engineering Standards Manual, Civil Chapter, Section G30, for required minimum utility line clearances.

*************************************************************************************************************

Refer to Drawings and Section 31 2000, Grading, Earth Moving, for earth cover, bedding, tracer wire, wire continuity test, warning tape, documenting new or exposed existing utility location, etc., requirements.

Make plastic-to-steel connection with transition fitting that is butt fused on plastic end and welded on steel end.

Mechanical fittings required for tie-in to Drisco 8000-series HDPE piping shall be installed as required by the fitting manufacturer using trained personnel, for example the Lycofit fittings and tooling.

horizontal directional drilling or cased boring

Crossing of paved streets or roadways or other areas, (if approved by LANL U&I group representative), will be accomplished by horizontal directional drilling (HDD) or cased boring, whenever practical. Casings for steel carrier pipe are not allowed. Care shall be exercised to ensure the paved surface is not damaged during the boring operation.

Directional Drill Bore Diameter:  [4, 6, 8, 10, 12] inch

Top of HDD or casing shall have a minimum burial depth of [36, 60, xxx] inches.

Casing

      - Manufacturer:  Pittsburgh Pipe

      - Material [A106]

      - Size:  [4, 6, 8, 10, 12, 14] inch

When pulling in pipe the pulling force shall be monitored and kept below the Allowable Tensile Load (ATL) value of the pipe size and material per manufacturer’s recommendation. Both pipe ends shall be monitored for continuous, smooth movement. Pulling load from the equipment shall be monitored and the pipe lead end shall be equipped with a weak link device to disengage at the ATL or below. Manufacturer’s procedures and design parameters shall be followed, in addition to ASTM F1962.

The pipe shall be inserted into the casing in such a manner that the pipe and the casing insulators will not be damaged. Polyethylene pipe shall extend 3-5% of the pulled-in length past the termination points to allow for contraction. Polyethylene pipe shall be allowed 24 hours to recover from the pulling stress and contract to original pre-pull length and allowed to stabilize to buried soil temperature before final tie-ins are accomplished. A minimum of five (5) feet of pipe shall extend beyond the borehole or casing to allow for pipe damage assessment. Tracing wire shall be pulled in with the polyethylene pipe.

The annulus between the casing and the pipe shall be sealed with a waterproof mechanical seal, e.g., a Link-Seal.

Polyethylene pipe shall be allowed to snake in the casing and centering spacers are not required.

STEEL PIPING INSTALLATION

Butt weld underground steel piping.  See Quality Assurance in PART 1.

Use ASME B1.20.1  threaded joints for above grade piping 2 inches and smaller and butt-welded joints for piping above 2 inches.

Apply Polyken primer 1019 or 1027 to underground joints, fittings, and valves, and spiral wrap with a double layer, half lapped, 35 mil tape, Polyken 934 system.  Follow manufacturer’s instructions.

Perform holiday test in accordance with the following procedure:

      - After pipe has been welded, joints wrapped, and pipe is ready for lowering into trench, test coating for flaws (holidays). Test coated piping system throughout its length for flaws in coating system by means of a high-potential flaw detector that can impress a maximum of 8,000 volts across coating.  One electrode of tester shall maintain complete circumferential contact with coating while transversing entire length of coating system and other electrode shall be the underlying metal pipe.  An electrical discharge through coating detected visually or by instrument, shall constitute failure of this test.

Actual working voltage of detector on pipe will depend upon thickness of coating and size of pipe.  A thin coating on a large pipe will offer a capacitive load to the detector that will drop the working voltage several thousand volts below the "no-load" voltage.  Detector output may also have to be increased to overcome conditions such as extremely dry rock, or sandy soil.

Important!  Do not cut ground cable to a shorter length.  The length supplied is important to proper operation of the detector.  Keep as much of the cable as possible in contact with the earth.  Straighten out kinks where possible and do not let it ride up over skids.  In dry areas it will help to drag the cable in the ditch where there is more moisture.  The pipe should be grounded.

      - Mark holidays as they are found and repair prior to lowering pipe into trench.  Repair holidays in factory coating by removing initial coating and undercoating for a minimum of 4 inches on each side of holiday.  Remove coating around holiday and feather edge to pipe wall for sufficient distance to make a satisfactory repair.  Apply primer (Polyken 1027) to the holiday to form a bond over the entire surface of the holiday and then spirally wrap pipe with a double layer of half-lapped 35 mil polyethylene tape (Polyken 934) for a minimum of 2 inches on each side of the holiday.

Repair holidays in joint wrappings by removing field applied coating in area of holiday and rewrapping.  LANL STR or designated representative will approve all areas of joint coating.

*************************************************************************************************************

Refer to Civil Standard Drawings ST-G30GEN-3 and ST-G30GEN-4 for trenching, warning tape, and tracer wire details.

Refer to the Engineering Standards Manual, Civil Chapter, Section G30, for required minimum utility line clearances

*************************************************************************************************************

Refer to Drawings and Section 31 2000, Earth Moving, for earth cover, bedding, tracer wire, wire continuity test, warning tape, documenting new or exposed existing utility location, etc., requirements.

Pressure testing

When pneumatically testing piping, the test area shall be cleared of unauthorized personnel due to contained energy.  The area to be cleared for the pneumatic test shall be [XXX feet per ASME PCC-2 or other method].

All piping systems shall be tested after construction except for pre-tested fabricated assemblies and welded tie-in connections where post construction tie-in testing is not practical.

When all joints are accessible the soap bubble test will be used to locate leaks.

The circumferential welds associated with connecting pretested assemblies, pretested repair pipe lengths or sections, and welded tie-in connections not pressure tested after construction shall be inspected by radiographic or visual inspection with visual aids.

Nonwelded tie-in connections not pressure tested after construction shall be leak tested at not less than the pressure available when the tie-in is placed into service

Pressure test piping in accordance with Section 22 0813, Testing Piping Systems and as follows:

      - Sufficient time for joints to “set” properly or “cool” must be allowed before the test is initiated.

      - Do not test HDPE above 100 °F (38 °C).

      - Test with inert gas at 160 psig for not less than 1/2 hour for each 500 ft3 (14m3) of pipe volume or fraction thereof. Minimum duration of pressure test shall be 1 hour. The duration of the test shall not exceed 8 hours.  Bring pressure to 160 psig and equalize to ambient temperature before starting pressure test; re-pressure as necessary to attain 160 psig prior to beginning test.  Record test with calibrated testing equipment, calibrated and certified per LANL requirements prior to each pressure test.  Recorded pressure line shall be continuous, even, and virtually “straight” without abrupt glitches, jogs or changes.  The test pressure shall return to within five (5) percent of the starting position pressure at end of testing period.  Do not use oxygen, acetylene, or other flammable/combustible gases or gas mixtures for leak testing.

Pressure test tie-in joints to existing system

      - Because it is sometimes necessary to divide a pipeline or main into sections for testing, and to install test heads, connecting piping, and other necessary appurtenances, it is not required that the tie-in sections of piping be tested.  The tie-in joints, however, shall be tested for leaks at line pressure.  The test procedure used, including the duration of the test, shall be capable of disclosing all leaks in the section being tested and shall be selected after giving due consideration to the volumetric content of the section and its location.  In this case, the soap bubble test will be used to locate leaks if the tie-in joint is accessible during the test.

piping TIE-IN

*************************************************************************************************************

Refer to Civil Standard Drawings ST-G3060-1 for gas piping tie-in details.  https://engstandards.lanl.gov/Dwgs_Details.shtml#civil

If the natural gas distribution system requires a hot-tap operation, LANL UI qualified personnel shall perform the operation.  A specific civil drawing will be issued for the installation. A specific list of the tools, materials, and PPE will be created for the operation.  Either the manufacturer’s specific procedure covering the specific tooling and parts will be followed or LANL will create a specific procedure for the specific tooling and parts for the operation.

The requirements of 49CFR192.627 Tapping Pipelines Under Pressure, 49CFR192.629 Purging of Pipelines, B31.8 841.2.7 Precautions to Avoid Explosions of Gas–Air Mixtures or Uncontrolled Fires During Construction Operations, and B31.8 831.4.2 Special Requirements (j) will be met.

*************************************************************************************************************

Tie-in to existing system will be performed by LANL U&I.  Excavation, backfill, and materials required for tie-in shall be provided by Subcontractor.  Tie-in will be inspected by LANL STR and the LANL U&I Group gas system representative.

LANL STR will notify LANL U&I group at least 15 working days in advance to schedule tie-in.

Before tie-ins are scheduled the LANL STR will ensure materials required for tie-in are on site, service lines have been tested, material submittals and all test reports have been approved by LANL U&I Group and bell hole excavation meets access and OSHA requirements.

CORROSION CONTROL (STEEL PIPING BELOW GRADE)

*************************************************************************************************************

Contact LANL U&I Corrosion Specialist or the LANL U&I Group Gas System Representative for cathodic protection requirements.  Also refer to the ESM Electrical Chapter, Section G4040. *************************************************************************************************************

Repairs and retesting

Defective welds shall be repaired or removed

Weld repairs will be accomplished in accordance with 49 CFR 192 192.245.

Indications of leakage are not acceptable. If leakage is observed during testing reduce pressure to zero, repair leak, and then complete pressure testing.

If leakage is observed during testing with flammable gas the repair will be in accordance with a written procedure to vent the system safely, make the line non-flammable if possible and, if not possible, what compensatory methods are needed, repair the leak, and then complete pressure testing.

Repair of non-standard mechanical joints shall be in accordance with a written procedure that vents the system to zero pressure, repairs the joint as defined by the manufacturer’s documentation, and then complete pressure testing.

END OF SECTION

************************************************************

Do not delete the following reference information:

************************************************************

THE FOLLOWING STATEMENT IS FOR LANL USE ONLY

This project specification section is based on LANL Master Specification 33 5100 Rev. 11, dated December 22, 2022.