SECTION 33 7119

ELECTRICAL UNDERGROUND DUCTs AND MANHOLES

*************************************************************************************************************

LANL MASTER SPECIFICATION SECTION

Word file at https://engstandards.lanl.gov

Rev. 6 Summary of Changes Corrected reference to Utilities and Infrastructure. Removed requirement for NRTL listing. Removed references to NFPA 70. Removed requirement for underground warning tape. Corrected usage of conductor vs. cable.

This template must be edited for each project.  In doing so, specifier must add job-specific requirements.  Brackets are used in the text to indicate designer choices or locations where text must be supplied by the designer.  Once the choice is made or text supplied, remove the brackets.  This document must also be edited to delete specification requirements for processes, items, or designs that are not included in the project -- and specifier’s notes such as these.  To seek a variance from requirements that are applicable, contact the Engineering Standards Manual Electrical POC. Please contact POC with suggestions for improvement as well.

When assembling a specification package, include applicable Sections from all Divisions, especially Division 1, General requirements.

Section developed for ML-4 projects.  For ML-1, 2, and 3 applications, additional requirements and independent reviews should be added if increased confidence in procurement or execution is desired; see ESM Chapter 1 Section Z10 Specifications and Quality sections.

*************************************************************************************************************

GENERAL

SECTION INCLUDES

*************************************************************************************************************

Edit the following articles to match Project requirements. Delete systems not applicable to Project.

*************************************************************************************************************

Underground ductbanks for medium-voltage power utility systems

Manholes for medium-voltage power utility systems

LANL-Performed Work

*************************************************************************************************************

Edit the following articles to match Project requirements. Delete systems not applicable to Project.

*************************************************************************************************************

LANL Utilities and Infrastructure (U&I) will furnish, install, and test medium-voltage power cables. At electrical manholes containing energized cables, LANL U&I will pull cables and make penetrations into manholes and will install the last 5 ft of duct into the manhole using materials furnished by Subcontractor.

SUBMITTALS

Action Submittals

*************************************************************************************************************

Delete the following paragraph if manholes are not needed.

*************************************************************************************************************

Catalog Data: Describing pre-cast manhole(s), manhole frame(s) and lid(s), ladders, and cable racks.

Test Reports: Report of duct blockage tests.

Closeout Submittals

Project Record Documents: Record GPS-based survey locations of ductbanks, new and existing manholes, and places where ductbanks cross other underground systems.

QUALITY ASSURANCE

Comply with IEEE C2 – National Electrical Safety Code (NESC) for components and installation.

Receiving, Storing and Protecting

Receive, store, protect, and handle products according to NECA 1 – Standard Practices for Good Workmanship in Electrical Construction and NECA/NEMA 605 – Recommended Practice for Installing Underground Nonmetallic Utility Duct.

SEQUENCING AND SCHEDULING

Notify LANL Subcontract Technical Representative (STR) to schedule inspection of each ductbank or ductbank segment before concrete is placed.

Notify LANL STR 10 days before duct tests.

PRODUCTS

  - PRODUCT OPTIONS AND SUBSTITUTIONS

Alternate products may be accepted; follow Section 01 2500 – Substitution Procedures.

  - RIGID NON-METALLIC CONDUIT AND FITTINGS

Conduit:  PVC per UL651 – Schedule 40 and 80 Rigid PVC Conduit and NEMA TC 2 – Electrical Plastic Tubing and Conduit, ANSI C80.3.

Fittings: Solvent-welded socket fittings meeting UL514C – Non-Metallic Fittings for Conduit and Outlet Boxes, and NEMA TC 3 – PVC Fittings for Use with Rigid PVC Conduit and Tubing.

  - UTILITIES DUCT AND FITTINGS

PVC type EB, 90 degree C rated, utilities duct for concrete encasement per NEMA TC 6 – Plastic Utilities Duct for Underground Installation, ANSI C130.2, ASTM F-512 – Standard Specification for Smooth-Wall PVC Conduit and Fittings for Underground Installation, and UL-651A – Type EB and A Rigid PVC Conduit and HDPE Conduit.

PVC fittings per NEMA TC 9 – Fittings for Plastic Utilities Duct for Underground Installation and ASTM F-512 – Standard Specification for Smooth-Wall PVC Conduit and Fittings for Underground Installation.

  - DUCT SPACERS

Duct spacers must provide 3-inch separations between ducts and minimum 3-inch concrete coverage on bottom sides and top.

  - GROUND Conductor

Use 4/0 AWG bare-stranded, soft-temper, copper conductor per ASTM B 8, Standard Specification for Concentric-Lay Stranded Copper Conductors.

*************************************************************************************************************

Edit the following article to match Project requirements.

*************************************************************************************************************

  - Raceway MEASURING/Pulling TAPE

Raceway measuring/pulling tape shall have permanently printed measurements in one-foot increments and minimum 1,200 lb average breaking strength.

Manufacturer: Greenlee “39243”

*************************************************************************************************************

Edit the following article to match Project requirements. Delete if not applicable to Project.

*************************************************************************************************************

  - DUCT PLUGS

Soft, expansible gasket material compressed with non-metallic plates and bolts to produce a positive seal against water and gas in unused ducts.

Manufacturer: Condux, Jackmoon USA, Inc.

*************************************************************************************************************Edit the following article to match Project requirements. Delete if not applicable to Project.

*************************************************************************************************************

  - DUCT SEALANT

Expandable foam duct sealant kits to prevent water and gas from entering manholes, vaults, or structures.

Manufacturer:  3M “Scotchcast 4416 Duct Sealing Kit”

*************************************************************************************************************

Edit manhole size(s) to match Project requirements. Delete article if manholes are not needed. Refer to LANL ESM Drawings ST-G4010-35, ST-G4010-36, and ST-G4010-37. Provide manhole plans and details in the Drawings.

*************************************************************************************************************

  - PRE-CAST MANHOLES

Per ASTM C858 – Standard Specification for Underground Precast Concrete Utility Structures.

Electrical manholes shall have the following minimum inside dimensions: 12'-0" long, 6'-0" wide, 7'-0" high or as shown on the drawings. Coordinate with LANL U&I through the LANL Subcontract Technical Representative (STR).

Minimum thickness of floor, walls and roof shall be 6 inches.

Minimum design loading shall be in accordance with ASTM C857 – Standard Practice for Minimum Structural Design Loading for Underground Precast Concrete Utility Structures

Design live loading for manholes not subject to vehicle traffic shall be not less than 300 lb/sq ft.

Design live loading shall be AASHTO HS-20 per AASHTO HB-17 where manhole is installed in a street or paved parking area.

Manhole floor shall be cast integral with walls to form the bottom ring.

Furnish a keyed joint between the bottom ring and top ring.

*************************************************************************************************************

Edit knockout sizes and locations to match Project requirements.

*************************************************************************************************************

Position six 30 inches X 30 inches knockout panels, one in each end wall and two in each side wall of each power manhole.  Position a 12-inch diameter sump hole with cast iron cover in the floor near a corner.

Locate a 36-inch diameter access opening centered in the roof of the manhole.

Furnish pre-cast concrete grade rings as required to place top of manhole flush with paving or 2 to 4 inches above finished grade.  Grade rings shall have a minimum inside diameter of 36 inches.  Furnish cast iron manhole steps at 16 inches on-centers.

Furnish lifting inserts in each manhole section for unloading and positioning.

Position one hot dip galvanized steel pulling iron under each knockout panel, two along each side wall and one under the manhole access opening (total of seven).  Pulling iron shall have a capacity of 8000 lb. with a safety factor of 2.

Embed 1-5/8 inches X 1-5/8 inches hot dip galvanized steel continuous pre-set inserts in each side wall of manhole.

Orient inserts horizontally and space 20 inches apart with bottom insert 12 inches above the floor.

Extend inserts to within 6 inches of end walls.

Manufacturer: Unistrut, P3200 series.

Manufacturers:  ARCO Concrete, Inc.; AMCOR Pre-cast; Pre-Cast Manufacturing, Co.; 4-Corners Pre-Cast; Vaughn Concrete Products, Inc.

*************************************************************************************************************

Delete the following article if manholes are not needed.

*************************************************************************************************************

  - PREMOLDED JOINT FILLER

Closed cell expanded neoprene joint filler conforming to ASTM D1056 – Standard Specification for Flexible Cellular Materials - Sponge or Expanded Rubber.

Manufacturer: Williams Products, Inc., Type NN-1

*************************************************************************************************************

Delete the following article if manholes are not needed.

*************************************************************************************************************

  - MANHOLE ACCESSORIES

Heavy duty cast iron manhole frame with solid lid.

Material shall conform to ASTM A48 – Standard Specification for Gray Iron Castings, Class 35B.

Frame and lid shall be suitable for AASHTO HS-20 wheel loads.

Minimum clear opening through the frame will be 30 inches.

Furnish lid lettering "ELECTRIC" for power manhole.

Manufacturer: Neenah Foundry Company, Model R-1640-C1 (power)

Furnish hooked manhole ladder that complies with OSHA 29 CFR 1910.27 and ANSI A14.3 – Safety Code for Fixed Ladders.

Ladder shall be fabricated from steel conforming to ASTM A36 – Standard Specification for Structural Steel.

Paint manhole ladder as follows: One coat of rust inhibiting primer, 2 - 3 mil minimum wet thickness.  Two finish coats of water based alkyd enamel, 3 mil minimum wet thickness, and safety yellow color.

Manufacturer: Condux, Inwesco.

Furnish hot dip galvanized steel telescoping ladder safety post in manholes with two or more grade ring steps. Manufacturer: Bilco LU-2.

Furnish heavy duty non-metallic cable racks and arms for manholes.

Each member shall be molded in one piece from UL listed glass reinforced nylon that can be field cut to length.

Furnish 14-inch-long and 3-inch-long saddle arms.  Coordinate quantity and types with the LANL STR.

Manufacturer: Underground Devices, Inc., #CR36-B 36-inch rack, #RA14 arm, and 3HDS arm (saddle arm).

Use hot dip galvanized, electro-galvanized or stainless-steel fasteners and hardware in manholes.

EXECUTION

  - PREPARATION

Install underground ductbank systems according to the NESC, NECA/NEMA 605 – Recommended Practice for installing Underground Nonmetallic Utility Duct, and the requirements in this Section.

Duct bank system routing shown on Drawings is in approximate locations unless dimensioned. Route as required to complete the system.

Coordinate underground ductbank system work to avoid interference with other trades and existing utilities.

Verify routing and termination locations of duct banks before excavation for rough-in.

Verify that field measurements are as shown on Drawings.

Position trench so concrete envelope of ductbanks will meet or exceed the minimum horizontal and vertical separations from parallel or perpendicular runs other utility pipes or conduits shown on the Drawings.

*************************************************************************************************************

The Drawings should contain detail(s) reflecting the requirements in LANL design standard drawings ST-G30GEN-4 and ST-G30GEN-5 as well as minimum separations shown in the ESM.  If a separations table in this section is desired, copy/adapt from LMS Section 33 8126’s table if present.

*************************************************************************************************************

  - EXCAVATION AND BACKFILL

Make excavation for manholes and underground ductbanks to depth required and to provide solid bearing.

Set excavation so top of power ductbank concrete encasement will be not less than 24 inches below finished grade or paving.

Set excavation so top of telephone ductbank concrete encasement will be not less than 24 inches below finished grade or paving.

Grade trenches for underground ductbanks to a minimum of 4 inches per 100 ft. toward manholes.

Keep excavation dry during installation of work.

Make trenches of sufficient width to receive work to be installed and provide specified concrete coverage on sides.

Backfill excavations for ductbanks and manholes in 6-inch layers; use soil excavated; remove roots, rocks and sharp objects.  Furnish coarse sand as required for additional backfill material.

Moisture condition backfill soil and compact in accordance with ASTM D 1557 to 95% of maximum density under paved areas and 90% of maximum density under unpaved areas.

Overfill excavations to allow for settlement.

Refer to Section 31 2000 – Earth Moving for additional requirements.

*************************************************************************************************************

Edit the following article to match Project requirements. Refer to LANL Standard Detail ST-G4010-32.  Provide ductbank plans and details in the Drawings.

*************************************************************************************************************

  - UNDERGROUND DUCTBANK INSTALLATION

Install the number and size of ducts as indicated on the Drawings.

Use the following duct materials:

*************************************************************************************************************

Edit 1 through 4 to match Project requirements.

*************************************************************************************************************

Use Schedule 40 rigid non-metallic conduit, Type EB utility duct, for utility level medium voltage power ducts.

Use schedule 40 rigid non-metallic conduit, Type EB utility duct for horizontal and vertical elbows, risers, and stub-ups.

Grade ducts to drain a minimum of 4 inches per 100 ft to manholes, hand-holes, or drainage point.

Align and support ducts to prevent trapping moisture at any point.

Use the smooth earth walls of trenches as forms for concrete encasement of ducts.

If a manhole is not indicated, make horizontal changes in direction of duct runs using long sweep bends with a minimum radius of 35 feet unless otherwise noted on the Drawings.

Where ducts turn up into the surface, use elbows with minimum 36 inches radius; terminate in a coupling 4 inches above the surface or equipment pad.  Install pipe plug in each unused duct stub-up.

Support ducts with duct spacers placed at intervals not exceeding 5 ft.  Provide method to prevent duct movement or flotation.  Stagger supports as necessary to prevent any discontinuity in the concrete encasement.

Terminate power ducts in manholes, vaults and building walls using bell end fittings.

At each existing electrical manhole that contains energized cables, terminate ducts 5 ft from the manhole wall. LANL U&I will make penetrations into the manhole and will install the last 5 ft of duct into the manhole. Furnish all ductbank materials required for this work.

For ducts installed through holes cut by the subcontractor in existing building, vault, or manhole walls, pack opening with non-shrink grout. Feather the edge of the grout around each bell and conform to the curvature of the bell end.  Remove sharp edges and projections and fill voids within 6 inches of bell ends.

For concrete-encased ducts installed in new manholes through a knockout panel, after removing forms from the end of the ductbank, rub the exposed concrete surface smooth.  Feather the edge of the concrete around each bell and conform to the curvature of the bell end.  Remove sharp edges and projections and fill voids within 6 inches of bell ends.

Install a 4/0 AWG bare copper ground conductor centered within each power ductbank.

Connect to ground conductor in manholes and at riser poles using exothermic welds or IEEE 837 certified compression connectors.

Connect to ground point in switchgear and transformers using IEEE 837 certified compression connectors.

Make-up joints in underground ducts to be tight, driven home on both sides and thoroughly waterproof.  Use manufacturer's recommended solvent-cement.

Schedule inspection of each ductbank or ductbank segment before concrete is placed.

Test each duct for blockage or deformation after concrete has cured for 24 hours.

Use a flexible mandrel/scraper not less than 12 inches long with a diameter approximately 1/4 inch less than the inside diameter of the duct.

Pull a mandrel behind a brush with stiff bristles.

Replace any duct section found blocked.

Notify LANL STR not less than 2 working days before duct tests; submit written reports of tests to STR.

After ducts have been successfully inspected and tested:

Backfill the trench as described in the “Excavation and Backfill” article above, and

Install measuring and pulling tape in each duct. Leave not less than 12 inches of slack at each end of the tape.  Secure each end of tape.

Stub-Up Connections:

Where ducts turn up into a stub-out, use elbows with minimum 36 inches radius.  Extend conduits through concrete pad or floor for connection to freestanding equipment with an adjustable top or coupling threaded inside for plugs; set flush with the finished floor or equipment pad.

Where equipment connections are not made under this Subcontract, install threaded insert plugs set flush with the floor.

  - CONCRETE ENCASEMENT

Concrete-encase underground ductbanks to provide not less than 3 inches of coverage on all sides.

Refer to Section 03 3053 – Miscellaneous Cast-in-Place Concrete or 03 3001 – Reinforced Concrete for basic material and installation requirements. Neither concrete reinforcing nor concrete testing is required for this application.

Use a pre-approved concrete mix design that is suitable for exterior use exposed to freezing and thawing.

Use red-colored concrete to encase ductbanks for medium voltage cables.

        - Use 2.0 lb. of pigment per 94 lb. sack of cement.

        - Manufacturer: Rockwood Industries/Davis Colors, No. 1117.

Place concrete using deflecting trough directing concrete through the duct assembly.

Place concrete envelope as one monolithic pour where possible; taper any joints with a 10:1 slope.

Allow for expansion/contraction of ducts; place concrete starting at one end of ductbank allowing the free end to move.

*************************************************************************************************************

Delete the following article if manholes are not needed. Refer to LANL ESM Drawings ST-G4010-35, ST-G4010-36, and ST-G4010-37. Provide manhole plans and details in the Drawings.

*************************************************************************************************************

  - MANHOLE INSTALLATION

Install manholes at locations indicated on the Drawings.

Install manholes in accordance with ASTM C891 – Standard Practice for Installation of Underground Precast Concrete Utility Structures.

Make excavation of suitable dimensions so ducts enter manhole at proper elevation. Refer to Section 31 2000 – Earth Moving for additional requirements.

Install at least 6 inches sand bedding under manholes; level and compact to 95% maximum density accordance with ASTM D 1557.

Install a 2 ft. X 2 ft. X 2 ft. sump of 3/4 inch gravel below the drain sump opening in the bottom ring of the manhole.

Place pre-molded joint filler in joints between bottom ring, top ring, grade rings and manhole frame.  Install following manufacturer's instructions.

Install a continuous loop of 4/0 AWG bare copper ground conductor around inside walls of manholes at floor level.

Attach to walls using copper or cast bronze cable holders and masonry anchors.

Connect to duct bank ground conductor using exothermic welds or approved non-reversible compression fittings.

Ground metal cable racks and permanent ladders using exothermic welds or approved non-reversible compression fittings.

Install cable racks as required to support cables at intervals not exceeding 3 ft.  Coordinate quantity and types of racks and arms with the LANL U&I POC and the LANL NIE POC.

For manholes in unpaved areas install an 8 ft by 8 ft by 6-inch concrete apron around manhole frame and cover.  Taper the concrete one inch away from the frame to the edge of the apron for drainage.

Stamp manhole structure number on north edge of manhole ring. Use steel dies with 3/8 inch or larger characters.

  - DUCT PLUGGING AND SEALING

Install duct plugs in both ends of all unused ducts that cross any natural gas line.

Install duct sealant in both ends of all ducts containing cables that cross any natural gas line.

FIELD QUALITY CONTROL

    - Provide final protection and maintain conditions to ensure that coatings and finishes are without damage or deterioration at final inspection.

*************************************************************************************************************

Edit the following article to match Project requirements: delete inspection points that are not applicable to the Project.

*************************************************************************************************************

    - Inspection Points – Provide not less than 2 working days advance notice to the LANL STR for the following inspection points. In the notice identify the particular areas of the Project for which inspection is requested. Correct deficiencies identified during inspections. If the requested inspection does not occur within 1 working day of the inspection point, work may proceed.

Underground ducts: After ducts have been installed but before concrete-encasement or trench backfilling commences. Inspections may be scheduled for one or more segments.  Inspection may include but is not limited to:

        - Correct duct material, quantity, and size,

        - Proper duct spacing and supports,

        - Proper anchoring of support spacers,

        - Proper depth and grading of ducts,

        - Correct duct stub-up locations,

        - Duct connection and coupling integrity,

        - Ground conductor material and size,

        - Ground conductor connection integrity.

Mandrel testing of underground ducts: After concrete-encasement has cured for 24 hours but before trench backfilling commences.  LANL witnessing of subcontractor-performed tests may be scheduled for one or more segments.

Manholes: After manholes have been installed but before concrete- backfilling commences. Inspections may be scheduled for one or more manholes.  Inspection may include but is not limited to:

        - Correct manhole material and size,

        - Proper manhole location, orientation, leveling, and depth,

        - Proper installation of pre-molded joint filler between sections.

END OF SECTION

************************************************************

Do not delete the following reference information:

************************************************************

THE FOLLOWING STATEMENT IS FOR LANL USE ONLY

This project specification section is based on LANL Master Specifications Section 33 7119, Rev. 6, dated July 14, 2022.