## TIP Template Explanation
Purpose: | This template facilitates development of a Project Test and Inspection Plan (TIP) per the Project Specification's 01 4000 Quality Requirements section. When required by 01 4000 or otherwise, producing the TIP is the constructor's responsibility. A TIP must identify the testing, inspection, and quality control requirements per LANL's ESM Chapter 16 (e.g., Sections IBC-GEN, IBC-IP, and IBC-TIA). When present, Special Inspection tasks are captured and controlled by the SSI; they are summarized on TIP template code-based tab and should be expanded there as appropriate to fully convey the tasks.
Legend
CONSTRUCTOR OR CONSTRUCTOR-HIRED UNLESS OTHERWISE INDICATED
CO | Constructor
QC | Quality Control representative -- Constructor's QC inspector (e.g., IQPA-QC for LANL self-perform)
TA | Testing Agency (LANL-approved per Ch. 16 IBC-TIA)
LANL or LANL-HIRED
CEIO | Chief Electrical Inspector's Office (LANL OSH-ISH)
Cx | Commissioning Agent (per ESM Ch. 15)
FE | Field Engineer
FPO | Fire Protection Office
LCA | LANL Commissioning Authority (STUPCOMM; per ESM Ch. 15)
NIE | Network and Infrastructure Engineering Representative (LANL telecom)
OBI | Owners Building Inspector (LANL; per Ch. 16 IBC-IP)
SI | Special Inspector (LANL)
DEFINITIONS
Hold Point | A mandatory verification that cannot be passed without being specifically released by the LANL entity that established the Hold Point in the template. Default notification lead time needed is 48 hours.
Witness Point | Similar to a Hold Point; however, work may proceed once the required notification lead-time to the inspecting organization has passed (e.g., 48 hours) if they are not present.
QC Verification | An in-process formal documentation for adherence to quality assurance standards identified in the Specification. QC Verifications typically correspond to a Hold Point or Witness Point.
QC Submittal | Formal documentation of quality control process results generated by the constructor. Typically documents a process perfomed without QC witnessing after confidence has been established through a QC verification process
Testing | A formal testing process performed by an LBO-approved testing agency
Basic Approach | This is multi-tabbed Excel workbook. On the Spec-Based Tasks tab (at the bottom), the requirements from LANL's master guide specifications are summarized by spec section. The requirements are organized into three categories (see legend above for definitions): 1) Inspections 2) QC Verifications 3) QC Submittals The party responsible for the oversight or administration of each inspection or QC verification is indicated (Owner column). Refer to the legend for definitions of responsible parties. On the Code-Based Inspections tab, code and standard requirements that often span multiple spec section tasks are listed.
Editing the Template/ Creating the Project TIP | A compliant and effective Test and Inspection Plan, per the Project Specification's Section 01 4000, shall include inspections required by specifications, applicable codes, and applicable standards in tabular form and be integrated with a Work Breakdown Structure (WBS) or construction schedule to identify milestones/prerequisites for each test and inspection. This template shall be modified to only include construction systems applicable to the scope of work within the project. Note that this template already contains the necessary information for each inspection, QC verification, or other task to satisfy the five points listed above. The TIP shall list the various systems being installed throughout the project and the corresponding Test and Inspection tasks associated with each system, irrespective of overall construction sequencing. The completed TIP must be submitted to LANL as an action submittal and reviewed by LANL AHJs and Owner's Representatives in accordance with Sections 01 4000 and 01 3300 of the Specification. The plan shall indicate: 1. Test or Inspection ID. 2. Brief description of the test or inspection. 3. Identify if Inspection or Test is a Witness or Hold Point. 4. Entity responsible for performing each test and inspection (e.g., Subcontractor qualified personnel, 3rd Party Inspector, LANL Building Inspector, LBO-approved Special Inspector, or Structural Engineer-of-Record) 5. Reference to code, standard, or specification requiring the test or inspection. Template refers to most LANL office master spec sections present (both revision and paragraphs), but these must be edited to match the rev of the Project Spec section, rows added or deleted to correspond with the Sections and parapgraphs in the Project Spec, and paragraph references verified/upated. The final TIP information shall be integrated within a Work Breakdown Structure or Construction Schedule. This can be performed in Excel, or scheduling software like MS Projects or P6.
Guidance: The LANL 01 3300 Submittal Log template xls has features and instructions that facilitate tailoring and printing multiple workbook tabs, and these might be considered by the constructor's TIP developer.
TIP Template Summary of Revisions | Rev. 0: Initial issuance, 9/24/2013
Rev. 1, March 22, 2023: Complete revision and update, simplified/streamlined. Addition of code-based inspections and instructions on separate tabs. Incorporates VAR-10564 (constructor develops, not design agency). 2021 IBC, IFC, UMC, and UPC and 2020 NEC compliant.

## Spec-Based Tasks
Sec Div | Sort Seq. | Discipline | Section No. | Sec Rev | Section Title | Task | Task Type | Witness Point | Hold Point | Owner | Requirement Reference | Spec Reference (correct as needed)
01 | 1 | General | 01 3300 | 6 | Submittal Procedures | Submittal Schedule | QC Submittal | No | Yes | CO |  | 1.4.A
01 | 2 | General | 01 4000 | 8 | Quality Requirements [Non-nuclear] | [Project Quality Assurance Plan] | QC Submittal | No | Yes | CO |  | 01 4000 1.4.A
01 | 3 | General | 01 4000 | 8 | Quality Requirements [Non-nuclear] | Construction Schedule | QC Submittal | No | Yes | CO |  | 01 4000 1.4.C
01 | 4 | General | 01 4000 | 8 | Quality Requirements [Non-nuclear] | Test and Inspection Plan | QC Submittal | No | Yes | CO |  | 01 4000 1.4.D
01 | 5 | General | 01 4000 | 8 | Quality Requirements [Non-nuclear] | Verification of System Completion | QC Verification | No | Yes | OBI |  | 01 4000 1.6.A.3
01 | 6 | General | 01 4000 | 1 | Quality Requirements [Nuclear] | [Project Quality Assurance Plan] | QC Submittal | No | Yes | CO |  | 01 4000 1.4.A
01 | 7 | General | 01 4000 | 1 | Quality Requirements [Nuclear] | Construction Schedule | QC Submittal | No | Yes | CO |  | 01 4000 1.4.C
01 | 8 | General | 01 4000 | 1 | Quality Requirements [Nuclear] | Test and Inspection Plan | QC Submittal | No | Yes | CO |  | 01 4000 1.4.D
01 | 9 | General | 01 4000 | 1 | Quality Requirements [Nuclear] | Verification of System Completion | QC Verification | No | Yes | OBI |  | 01 4000 1.6.A.3
01 | 10 | Welding | 01 4444 | 2 | Offsite Welding and Joining Requirements | For SSCs that are designated ML-1 or ML-2, welding consumables shall be provided with Certified Material Test Reports (CMTRs) traceable by heat/lot number to the point-of-use. | QC Verification | No | No | QC |  | 01 4444 1.7.1
01 | 11 | Welding | 01 4444 | 2 | Offsite Welding and Joining Requirements | Inspection results, including weld maps, shall be documented and provided within one day after completion of associated inspection work. | QC Submittal | No | No | CO |  | 01 4444 1.8 D
01 | 12 | Welding | 01 4455 | 3 | Onsite Welding and Joining Requirements | Weld Inspection results | QC Submittal | No | No | CO |  | 01 4455 1.9.D
01 | 13 | Architectural | 01 7823 | 0 | Operation and Maintenance Data | Manual content is specified in individual Specification Sections to be reviewed at the time of Section submittals if review is required | QC Submittal | Yes | No | CO |  | 01 7823.1.4.A
01 | 14 | General | 01 7839 | 3 | Project Record Documents | Submit record digital data files and one set of record digital data file plots | QC Submittal | No | Yes | CO |  | 01 7839 1.3.A.1.b.3
03 | 15 | Structural | 03 3001 | 17 | Reinforced Concrete | Tests required for concrete | Testing | No | Yes | TA |  | 03 3001 3.11.C.1 - D.
03 | 16 | Structural | 03 3001 | 17 | Reinforced Concrete | Hot and Cold Weather Implementation Plan submittals requirements | QC Submittal | Yes | No | CO |  | Appendix C and D
03 | 17 | Civil | 03 3053 | 10 | Miscellaneous Cast-In-Place Concrete | Tests required for concrete | Testing | No | Yes | TA |  | 03 3053 3.4.C. - E.
03 | 18 | Civil | 03 3053 | 9 | Miscellaneous Cast-In-Place Concrete | Revise submittals for concrete mixes materials and admixtures | QC Submittal | Yes | No | CO |  | 04 3053 2.3 - 2.4
03 | 19 | Structural | 03 4100 | 3 | Precast Structural Concrete | Field Quality control testing of Sand-cement and nonshrink grout compressive testing | QC Submittal | Yes | No | CO |  | 03 4100 1.4.E Rev. 3
03 | 20 | Structural | 03 6000 | 4 | Grouting | Field Quality Control Test Reports | QC Submittal | No | No | CO | ACI 301 / ASME NQA-1 | 03 6000 1.4.E
03 | 21 | Structural | 03 6000 | 4 | Grouting | Field testing by certified testing agency | Testing | No | Yes | TA | ACI 301 / ASME NQA-1 | 03 6000 3.4.A Rev. 4
03 | 22 | Structural | 03 6021 | 0 | Grouting - High Confidence | CGD Plan Witness and Hold Points | QC Submittal | Yes | No | OBI |  | 03 6021 1.5.a.1.a
03 | 23 | Structural | 03 6021 | 0 | Grouting - High Confidence | Tests and inspection results | QC Submittal | Yes | No | OBI |  | 03 6021 1.5.i Rev. 0
03 | 24 | Structural | 03 6021 | 0 | Grouting - High Confidence | Field QC by testing | Testing | Yes | Yes | TA | ASTM C-579, ASTM C-109 | 03 6021 3.4.A -D Rev. 0
04 | 25 | Structural | 04 2220 | 4 | Reinforced Unit Masonry | Shop drawings for Masonry Units and Reinforcing Steele | QC Submittal | No | No | CO |  | 04 2220 1.3.B
04 | 26 | Structural | 04 2220 | 4 | Reinforced Unit Masonry | Mix designs for mortar and group | QC Submittal | No | No | CO |  | 04 2220 1.4.D
04 | 27 | Structural | 04 2220 | 4 | Reinforced Unit Masonry | Statement of Compressive Strength of Masonry | QC Submittal | No | No | CO |  | 04 2220 1.4.E
04 | 28 | Structural | 04 2220 | 4 | Reinforced Unit Masonry | Test Reports for Reinforcing Bars for each material type | QC Submittal | No | No | CO |  | 04 2220 1.4.F
04 | 29 | Structural | 04 2220 | 4 | Reinforced Unit Masonry | Weather-Related Construction Procedures | QC Submittal | No | No | CO |  | 04 2220 1.4.G
04 | 30 | Structural | 04 2220 | 4 | Reinforced Unit Masonry | Testing Agency Qualifications | QC Submittal | No | No | CO | ASTM C1093 | 04 2220 1.6.A
04 | 31 | Structural | 04 2220 | 4 | Reinforced Unit Masonry | Test grout for compressive strength and slump | Testing | No | Yes | TA | ASTM 476 and ASTM C-143 | 04 2220 2.12.D.2-3
05 | 32 | Structural | 05 0520 | 6 | Post-Installed Concrete and Grouted-Masonry Anchors - Normal Confidence | Field inspection and testing reports | QC Submittal | No | No | CO |  | 05 0520 1.6.A
05 | 33 | Structural | 05 0520 | 6 | Post-Installed Concrete and Grouted-Masonry Anchors - Normal Confidence | Submit installation inspection records | QC Submittal | No | No | CO |  | 05 0520 3.12.A
05 | 34 | Structural | 05 0520 | 6 | Post-Installed Concrete and Grouted-Masonry Anchors - Normal Confidence | Submit testing records | QC Submittal | No | No | CO |  | 05 0520 3.12.B
05 | 35 | Structural | 05 0521 | 4 | Post-Installed Concrete Anchors - Nuclear Safety | Submit verification documents for installation | QC Submittal | No | No | CO |  | 05 0521 1.6.B
05 | 36 | Structural | 05 0521 | 4 | Post-Installed Concrete Anchors - Nuclear Safety | Notify LANL Inspectors at least 24 hours prior to any Subcontractor installation, inspection, or testing activities associated with SSI and treat such tasks as hold/witness points | QC Submittal | No | Yes | CO |  | 05 0521 1.7.D.1
05 | 37 | Structural | 05 0521 | 4 | Post-Installed Concrete Anchors - Nuclear Safety | Verify anchor material (i.e., CMTR) at receipt on site | QC Verification | Yes | Yes | QC |  | 05 0521 1.7.F.1
05 | 38 | Structural | 05 0521 | 4 | Post-Installed Concrete Anchors - Nuclear Safety | Verify anchor installation in accordance with Specification | QC Verification | Yes | Yes | QC |  | 05 0521 1.7.F.2
05 | 39 | Structural | 05 0521 | 4 | Post-Installed Concrete Anchors - Nuclear Safety | Testing of permanent anchors shall be witness by the LANL Construction Inspector | Testing | No | Yes | TA |  | 05 0521 3.8.B.1
05 | 40 | Structural | 05 0521 | 4 | Post-Installed Concrete Anchors - Nuclear Safety | Submit installation inspection records | QC Submittal | No | No | CO |  | 05 0521 3.9.A
05 | 41 | Structural | 05 0521 | 4 | Post-Installed Concrete Anchors - Nuclear Safety | Submit testing records | QC Submittal | No | No | CO |  | 05 0521 3.9.B
05 | 42 | Structural | 05 2100 | 6 | Steel Joist Framing | Prepare test and inspection reports | QC Submittal | No | No | CO |  | 05 2100 3.3.D
07 | 43 | Architectural | 07 0150.19 | 4 | Preparation for Re-Roofing | Test and Evaluation Reports | QC Submittal | No | No | CO |  | 07 0150.19 1.6.B
07 | 44 | Architectural | 07 0150.19 | 4 | Preparation for Re-Roofing | Qualification statements | QC Submittal | No | No | CO |  | 07 0150.19 1.6.E
07 | 45 | Architectural | 07 0150.19 | 4 | Preparation for Re-Roofing | Test concrete substrate for capillary moisture by plastic sheet method | Testing | No | Yes | QC | ASTM 4263 | 07 0150.19 3.3.B Rev. 3
07 | 46 | Architectural | 07 0150.19 | 4 | Preparation for Re-Roofing | Perform fastener pull-out test | Testing | No | Yes | QC | ANSI/SPRI FX-1 | 07 0150.19 3.8.A
07 | 47 | Architectural | 07 1326 | 2 | Self-Adhering Sheet Waterproofing | Perform flood testing of treated area | QC verification |  |  | QC |  | 07 1326 3.6
07 | 48 | Architectural | 07 2400 | 4 | Exterior Insulation and Finish Systems | Qualifying testing agency will perform tests and inspections. Testing agency also will be responsible for preparing reports | Testing | No | Yes | TA |  | 07 2400 2.7.A.1.-4.
07 | 49 | Architectural | 07 2400 | 4 | Exterior Insulation and Finish Systems | Tests and reports | Testing | Yes | Yes | TA | ASTM E-2568, ICC-ES AC24, ICC-ES AC219 | 07 2400 3.8.C. and E.
07 | 50 | Architectural | 07 5213.13 | 3 | Atatic-Polypropylene Modified-Bitumen Roofing, Cold-Applied | Testing agency will perform test and inspections, and will prepare reports | Testing | Yes | Yes | TA | ASTM D-3617 | 07 5213.13 3.13.A. and B. Rev. 2
07 | 51 | Architectural | 07 5217 | 2 | Styrene-Butadiene-Styrene Modified-Bituminous Membrane Roofing, Cold-Applied | Field QC by testing agency | Testing | Yes | No | TA | ASTM D-3617 | 07 5217 3.14.A .-B..Rev. 1
07 | 52 | Fire | 07 8400 | 6 | Firestopping | Action Submittals for through & membrane penetrations and joints | QC Submittal | No | Yes | CO | IBC 110.3.8, 1705.18 | 07 8400 1.4 Rev. 6
08 | 53 | Architectural | 08 1100 | 3 | Metal Door and Frames | 2-Hr rated doors/frames present where required | QC verification | No | Yes | OBI | IBC and NFPA 80 | See Code-Based tab
08 | 54 | Architectural | 08 1213 | 4 | Hollow Metal Frames | 2-Hr rated doors/frames present where required | QC verification | No | Yes | OBI | IBC and NFPA 80 | See Code-Based tab
08 | 55 | Architectural | 08 1400 | 5 | Wood Doors | 2-Hr rated doors/frames present where required | QC verification | No | Yes | OBI | IBC and NFPA 80 | See Code-Based tab
08 | 56 | Architectural | 08 7100 | 6 | Door Hardware | Verification of correct devices | QC verification | No | Yes | OBI | IBC and NFPA 80 | See Code-Based tab
08 | 57 | Architectural | 08 8000 | 6 | Glazing | Fire-resistant glazing and storefronts | QC verification | No | Yes | OBI | IBC | See Code-Based tab
09 | 58 | Architectural | 09 5100 | 7 | Acoustical Ceilings | Field quality-control reports | QC Submittal | No | No | CO |  | 09 5100 1.5.G
11 | 59 | Mechanical | 11 5311.08 | 1 | Glovebox Design | QC Submittal | QC Submittal | No | Yes | CO |  | 11 5311.08 1.10.B Rev. 1
11 | 60 | Mechanical | 11 5311.10 | 4 | Glovebox Fabrication | Submit Inspection Data Sheet (Attachment 4) for each inspection | QC Submittal | Yes | Yes | CO |  | 11 5311.10 1.12.C Rev. 4
11 | 61 | Mechanical | 11 5311.10 | 4 | Glovebox Fabrication | QC Submittal (QA Document Package Attachment 2) | QC Submittal | No | Yes | CO |  | 11 5311.10 Att 2 Rev. 4
11 | 62 | Mechanical | 11 5311.18 | 1 | Glovebox Atmosphere Regenerable Purification Systems | Documentation Submittal Review | QC Submittal | No | Yes | CO |  | 11 5311.18 1.5.A Rev. 1
11 | 63 | Mechanical | 11 5311.18 | 1 | Glovebox Atmosphere Regenerable Purification Systems | Power termination/installation | QC Verification | Yes | Yes | QC |  | 11 5311.18 3.1.A Rev. 1
11 | 64 | Mechanical | 11 5311.18 | 1 | Glovebox Atmosphere Regenerable Purification Systems | Startup - ensure the purification unit has regenerated 3x prior to bringing online | QC Verification | No | Yes | QC |  | 11 5311.18 3.3.A Rev. 1
22 | 65 | Mechanical | 22 0535 | 0 | Electric Heat Tracing Systems | Submit catalog data, shop drawings, installation instructions, operation and maintenance instructions, warranty, and records of inspections, tests, and adjustments as needed | QC Submittal | No | No | CO |  | 22 0535 1.3.A.6
22 | 66 | Mechanical | 22 0535 | 0 | Electric Heat Tracing Systems | Inspect, test, and adjust electric heat tracing system IAW NECA 202 - maintain records for submittals | QC Verification | Yes | No | QC |  | 22 0535.3.5
22 | 67 | Structural | 22 0548.23 | 2 | Vibration and Seismic Controls for Mechanical Systems | Quality Control Submittals | QC Submittal | No | Yes | CO |  | 22 0548.23 1.5
22 | 68 | Mechanical | 22 0813 | 11 | Testing Piping Systems | Test Reports | QC Submittal | No | No | CO | ESM Chapter 17 Section Admin-4 1.0.B.3.a | 22 0813-1.6.B; 22 0813-3.1.D
22 | 69 | Civil | 22 0816 | 6 | Disinfection of Potable Water Piping [also 33 1300] | Disinfection Test Reports | QC Submittal | No | Yes | CO |  | 22 0816 1.4.A Rev.6
23 | 70 | Mechanical | 23 0593 | 4 | Testing, Adjusting, Balancing for HVAC | Provide advance written notice of testing readiness (not less than 15 days). Testing and commissioning will be performed by LANL (via STUPCOMM) | QC Submittal | No | Yes | LCA |  | 22 0593 3.1.B-C
23 | 71 | Mechanical | 23 0593 | 4 | Testing, Adjusting, Balancing for HVAC | Complete operational readiness prior to commencement of TAB services. Verify all items listed in 22 0593 3.1.C | QC Submittal | No | Yes | LCA |  | 22 0593 3.1.C
23 | 72 | Mechanical | 23 0800 | 0 | Commissioning of HVAC | Submit functional testing reports and performance testing reports | QC Submittal | No | No |  | Division 23 Sections | 22 0800 1.5.A.2
23 | 73 | Mechanical | 23 0800 | 0 | Commissioning of HVAC | Submit I&C and BAS submittals | QC Submittal | No | No |  | 25 5000 | 22 0800 1.5.A.3
23 | 74 | Mechanical | 23 0800 | 0 | Commissioning of HVAC | Submit Instrument calibration reports | QC Submittal | No | No |  | Division 23 and/or 25 Sections | 22 0800 1.5.A.4
23 | 75 | Mechanical | 23 2215 | 3 | Steam and Condensate Heating Piping and Specialties | Make action submittals IAW spec | QC Submittal | No | Yes | CO |  | 23 2115 1.3.A Rev. 3
23 | 76 | Mechanical | 23 2215 | 3 | Steam and Condensate Heating Piping and Specialties | Submit system and component documentation per 01 4115, installation examination required by section 3.1 of this procedure | QC Submittal | No | Yes | CO |  | 23 2115 1.3.B Rev. 3
23 | 77 | Mechanical | 23 2215 | 3 | Steam and Condensate Heating Piping and Specialties | Comply with listed Codes for Quality Assurance | QC Verification | No | Yes | QC |  | 23 2115 1.4 Rev. 3
23 | 78 | Mechanical | 23 2500 | 3 | HVAC Water Treatment | Manufacturers Field Reports | QC Submittal | No | No | CO |  | 23 2500 1.5.H
23 | 79 | Mechanical | 23 2500 | 3 | HVAC Water Treatment | Field quality-control reports | QC Submittal | No | No | CO |  | 23 2500 1.6.B
23 | 80 | Mechanical | 23 2500 | 3 | HVAC Water Treatment | Passivation Confirmation Report | QC Submittal | No | No | CO |  | 23 2500 1.6.C.3
23 | 81 | Mechanical | 23 3300 | 2 | Air Duct Accessories | Certification of welders, weld material, weld procedures, etc. | QC Submittal | No | No | CO |  | 23 3300 1.2.E-F
23 | 82 | Mechanical | 23 3400 | 1 | HVAC Fans | Field quality-control reports | QC Submittal | No | No | CO |  | 23 3400 1.6.A
23 | 83 | Mechanical | 23 4133.16 | 0 | HEPA Filters – ASME AG-1, Section FK, Special | Submit certifications | QC Submittal | No | No | CO |  | 23 4133.16 1.6 Rev 0
23 | 84 | Mechanical | 23 6200 | 1 | Packaged Compressor and Condenser Units | Field quality control reports | QC Submittal | No | No | CO |  | 23 6200 1.6.B; 23 6200 3.4.A
23 | 85 | Mechanical | 23 6200 | 1 | Packaged Compressor and Condenser Units | Perform field tests and inspections and prepare test reports | QC Submittal | No | No | CO |  | 23 6200 3.4.A
23 | 86 | Mechanical | 23 7413 | 3 | Packaged, Outdoor, Central Station | Field quality-control reports | QC Submittal | No | No | CO |  | 23 7413 1.3.C
23 | 87 | Mechanical | 23 8123 | 1 | Computer-Room Air-Conditioners | Field quality-control reports | QC Submittal | No | No | CO |  | 23 8123 1.5.B, 3.4.D
23 | 88 | Mechanical | 23 8239 | 1 | Unit Heaters | Field quality-control reports | QC Submittal | No | No | CO |  | 23 8239 1.5.B; 23 8339 3.2.A
25 | 89 | I&C | 25 0529 | 0 | Hangers and Supports for Building Automation Systems | Post-installed concrete anchoring of Seismically Exempt Equipment and components | QC Submittal | Yes | No | CO
26 | 90 | Electrical | 26 0519 | 8 | Low Voltage Electrical Power Conductors and Cables | Tool and instrument calibration records | QC Submittal | No | No | CO |  | 26 0519 1.4.A.1.a
26 | 91 | Electrical | 26 0519 | 8 | Low Voltage Electrical Power Conductors and Cables | Termination torque records | QC Submittal | No | No | CO |  | 26 0519 1.4.A.1.b & 3.6.L
26 | 92 | Electrical | 26 0519 | 8 | Low Voltage Electrical Power Conductors and Cables | Cable pulling records | QC Submittal | No | No | CO |  | 26 0519 1.4.A.1.c
26 | 93 | Electrical | 26 0519 | 8 | Low Voltage Electrical Power Conductors and Cables | Insulation resistance test results for each service conductor, feeder conductor 1/0 AWG or larger, critical system branch circuit conductor, or critical system control conductor | QC Submittal | Yes | No | CO |  | 26 0519 3.9.E.1
26 | 94 | Electrical | 26 0519 | 8 | Low Voltage Electrical Power Conductors and Cables | Witness and document torquing on not less than 10% of each type of connector and terminal | QC Verification | Yes | No | QC |  | 26 0519 3.9.E.3
26 | 95 | Electrical | 26 0529 | 7 | Hangers and Supports for Electrical Systems | Post-installed concrete anchoring of Seismically Exempt Equipment and components | QC Submittal | Yes | No | CO
26 | 96 | Electrical | 26 0700 | 4 | Induction Motors-500HP and Smaller | Verify Installation of motor conforms to manufacturer's instructions and design criteria | QC Verification | Yes | No | QC |  | 26 0813 3.4.A
26 | 97 | Electrical | 26 0700 | 4 | Induction Motors-500HP and Smaller | Verify Installation of motor conforms to manufacturer's instructions and design criteria | QC Verification | Yes | No | QC |  | 26 0813 3.4.B
26 | 98 | Electrical | 26 0700 | 4 | Induction Motors-500HP and Smaller | Manufacturer's Certificate of Installation | QC Submittal | No | No | CO |  | 26 0813 3.6.2
26 | 99 | Electrical | 26 0813 | 3 | Electrical Acceptance Testing | Test Reports | QC Submittal | Yes | No | CO |  | 26 0813 1.4.A.7
26 | 100 | Electrical | 26 2213 | 4 | Low Voltage Distribution Transformers | Visual verification of testing compliance with NECA 409 | QC Verification | Yes | No | QC | *NEIS NECA 409-2015 6.2 | 26 2213 3.5.A
26 | 101 | Electrical | 26 2213 | 4 | Low Voltage Distribution Transformers | Verification of proper documentation for measuring primary and secondary voltages and phase rotation | QC Verification | Yes | No | QC | *NEIS NECA 409-2015 6.4.1 | 26 2213 3.5.C
26 | 102 | Electrical | 26 2413 | 5 | Switchboards | Manufacturer's Certificate of Installation | QC Submittal | Yes | No | CO |  | 26 2413 3.6
26 | 103 | Electrical | 26 2419 | 5 | Motor Control Centers | Field Quality Control Records | QC Submittal | Yes | No | CO |  | 26 2419 1.4.B.2
26 | 104 | Electrical | 26 2419 | 5 | Motor Control Centers | Witness of torquing of all bus bar splices | QC Verification | Yes | No | QC / CEIO | *NEIS NECA 402 7.1 **NQA-1 | 26 2419.3.5.A.2
26 | 105 | Electrical | 26 2500 | 5 | Enclosed Bus Assemblies | Visual verification of testing compliance with NECA 408 | QC Verification | Yes | No | QC | *NEIS NECA 408 | 26 2500 3.6.B
26 | 106 | Electrical | 26 2713 | 5 | Electricity Metering | Witness of torquing electrical terminations (Coordinate electrical acceptance testing requirements per Section 26 0813) | QC Verification | Yes | No | QC / CEIO | NFPA 70 110.14.D (NEC) | 26 2713 3.3.B
26 | 107 | Electrical | 26 2726 | 6 | Wiring Devices | Witness test ground-fault circuit interrupter operation by using the integral test and reset functions | QC Verification | Yes | No | QC | OSHA 1926.20 | 26 2726 3.8.D
26 | 108 | Electrical | 26 2816 | 5 | Enclosed Switches and Circuit Breakers | Witness of torquing electrical terminations (Coordinate electrical acceptance testing requirements per Section 26 0813) | QC Verification | Yes | No | QC / CEIO | NFPA 70 110.14.D (NEC) | 26 2816 3.5.C 26 2816 3.5.D
26 | 109 | Electrical | 26 2816 | 5 | Enclosed Switches and Circuit Breakers | Witness of torquing electrical terminations (Coordinate electrical acceptance testing requirements per Section 26 0813) | QC Verification | Yes | No | QC / CEIO | NFPA 70 110.14.D (NEC) | 26 2816.3.5.C
26 | 110 | Electrical | 26 2816 | 5 | Enclosed Switches and Circuit Breakers | Witness of torquing electrical terminations (Coordinate electrical acceptance testing requirements per Section 26 0813) | QC Verification | Yes | No | QC / CEIO | NFPA 70 110.14.D (NEC) | 26 2816.3.5.C 26 28163.5.D
26 | 111 | Electrical | 26 2913 | 4 | Enclosed Controllers | Witness of torquing power conductor terminations (Coordinate electrical acceptance testing requirements in accordance with specification 26 0813) | QC Verification | Yes | No | QC / CEI O | NFPA 70 110.14.D (NEC) | 26 2913.3.6.C, 26 2913.3.6.E
26 | 112 | Electrical | 26 2923 | 4 | Variable Frequency Motor Controllers | Manufacturer's Certificate of Installation | QC Submittal | No | No | CO |  | 26 2923 1.3.B.2 & 3.5.B
26 | 113 | Electrical | 26 3334 | 2 | Stored Emergency Power Supply System | Manufacturer's certificate of installation | QC Submittal | No | No | CO |  | 26 3334.1.3.A.2 & 3.6
26 | 114 | Electrical | 26 3353 | 3 | Static Uninterruptible Power Supply | Manufacturer's Certificate of Installation | QC Submittal | Yes | No | CO |  | 26 3353 1.3.A.3
26 | 115 | Electrical | 26 3353 | 3 | Static Uninterruptible Power Supply | Witness proper torque of accessible bus connections and mechanical fasteners during installation of UPS | QC Verification | Yes | No | QC |  | 26 3353 3.6.B
26 | 116 | Electrical | 26 5200 | 7 | Safety Lighting | Test emergency lighting equipment in accordance with the manufacturer’s instructions and NECA/IESNA 500 | QC Verification | No | Yes | Cx | *NECA/IESNA 500, NFPA 70 700.3 | 26 5200 3.4.B
27 | 117 | Communications | 27 1000 | 8 | Structured Cabling | Fiber Test Reports | QC Submittal | No | No | CO |  | 27 1000 1.6.B & 3.12.B
27 | 118 | Communications | 27 1000 | 8 | Structured Cabling | Copper Test Reports | QC Submittal | No | No | CO |  | 27 1000 3.12.A
27 | 119 | Communications | 27 1000 | 8 | Structured Cabling | Raceway and enclosures verification for compliance with specification prior to the placement of any cable (coordinate with CEIO's rough-in inspection) | QC Verification | No | Yes | CEIO / NIE |  | 27 1000.1.4.A & 27 1500 18
27 | 120 | Secure Comm. | 27 1500.18 | 3 | Protected Transmission System Rough-In | Fluke LinkWare test results | QC Submittal | No | No | CO |  | 27 1500.18 1.7.A
27 | 121 | Electrical | 27 3000 | 4 | Voice Communications | Test reports | QC Submittal | No | No | CO |  | 27 3000 1.4.B.3
28 | 122 | Electrical/Security | 28 0528 | 4 | Pathways for Electronic Security | Test and inspection reports reports | QC Submittal | No | No | CO |  | 1.5.A.1
28 | 123 | Electrical | 28 1321 | 3 | Administrative Access Control System Rough-In | Test Reports | QC Submittal | No | No | CO |  | 28 1321 1.5.A.2
28 | 124 | Fire | 28 4600 | 4 | Fire Detection and Alarm | Installer’s Preliminary Test Report | QC Submittal | No | No | CO |  | 28 4600 1.5.C.1
28 | 125 | Fire | 28 4600 | 4 | Fire Detection and Alarm | Statement of Compliance | QC Submittal | No | No | CO |  | 28 4600 1.5.C.2
28 | 126 | Fire | 28 4600 | 4 | Fire Detection and Alarm | Final Test Report | QC Submittal | No | No | CO |  | 28 4600 1.5.C.4
31 | 127 | Civil | 31 2000 | 10 | Earth Moving | Test Reports - material compaction | QC Submittal | No | No | CO |  | 31 2000 1.4.A.3
31 | 128 | Civil | 31 2000 | 10 | Earth Moving | Test reports - tracing wire continuity | QC Submittal | No | No | CO |  | 31 2000 1.4.A.4
31 | 129 | Civil | 31 2000 | 10 | Earth Moving | Verify that moisture-density relationship per ASTM D 1557 for each soil type to be placed is completed | Testing | No | Yes | SI | IBC Table 1705.6 #3; see Code-Based tab | 31 2000 3.10.F.2-5
31 | 130 | Civil | 31 2323.33 | 6 | Flowable Fill | Submit material certifications, mix design and tests reports | QC Submittal | Yes | No | CO |  | 31 2323.33 1.3.A.1
31 | 131 | Civil | 31 2323.33 | 6 | Flowable Fill | Field tests reports | QC Submittal | Yes | No | QC |  | 31 2323.33 1.3.A.3
31 | 132 | Civil | 31 2323.33 | 6 | Flowable Fill | Field tests if required | Testing | No | Yes | OBI |  | 31 2323.33 3.5.A. - B.
32 | 133 | Civil | 32 1216 | 6 | Asphalt Paving | Material certifications documenting with NMDOT specifications | QC Submittal | Yes | No | CO |  | 32 1216 1.2.A.1
32 | 134 | Civil | 32 1216 | 6 | Asphalt Paving | Proposed mix design | QC Submittal | Yes | No | CO |  | 32 1216 1.2.A.2
32 | 135 | Civil | 32 1216 | 6 | Asphalt Paving | Certifications for the lab testing asphalt, equipment and personnel | QC Submittal | Yes | No | CO |  | 32 1216 1.2.A.4 - 5.
32 | 136 | Civil | 32 1216 | 6 | Asphalt Paving | Temporary and permanent traffic control plan | QC Submittal | Yes | No | CO |  | 32 1216 1.2.A.7-8
32 | 137 | Civil | 32 1216 | 6 | Asphalt Paving | Field and lab tests for Minor and Major asphalt Paving | Testing | No | Yes | TA |  | 32 1216 3.8.C.1 - 6.c
32 | 138 | Civil/Security | 32 3113 | 4 | Chain Link Fences and Gates | Two legible copies of batch tickets for each load of concrete | QC Submittal | No | No | CO |  | 32 3113 1.3.A.2
32 | 139 | Civil | 32 8400 | 3 | Planting Irrigation | Installation instruction for underground sprinkler system | QC Submittal | Yes | No | CO |  | 32 8400 1.3 A . 2
32 | 140 | Civil | 32 8400 | 3 | Planting Irrigation | Operation and maintenance manual for sprinkler system being installed | QC Submittal | Yes | No | CO |  | 32 8400 1.3 A.3
32 | 141 | Civil/Arch | 32 9219 | 5 | Seeding | Certification of material that complies with specifications | QC Submittal | Yes | No | CO |  | 32 9219 1.3.A.2
32 | 142 | Civil/Arch | 32 9223 | 3 | Sodding | Sod certification | QC Submittal | Yes | No | CO |  | 32 9223 1.2.A.1
32 | 143 | Civil/Arch | 32 9223 | 3 | Sodding | Sodding schedule | QC Submittal | Yes | No | CO |  | 32 9223 1.2.A.2
32 | 144 | Civil/Arch | 32 9300 | 4 | Plants | Planting schedule dates and type of work to be perform | QC Submittal | Yes | No | CO |  | 32 9300 1.3.A.1
32 | 145 | Civil/Arch | 32 9300 | 4 | Plants | Material lists with instructions | QC Submittal | Yes | No | CO |  | 32 9300 1.3.A.2
33 | 146 | Civil | 33 0513 | 6 | Manholes and Structures | Material Certification | QC Submittal | Yes | No | CO |  | 33 0513 1.4.A.1
33 | 147 | Civil | 33 0513 | 6 | Manholes and Structures | NMED-approved septic tank list certification number | QC Submittal | Yes | No | CO |  | 33 0513 1.4.A.2
33 | 148 | Civil | 33 0513 | 6 | Manholes and Structures | Installation instructions | QC Submittal | Yes | No | CO |  | 33 0513 1.4.A.3
33 | 149 | Civil | 33 0513 | 6 | Manholes and Structures | Manhole exfiltration test results | QC Submittal | Yes | No | CO |  | 33 0513 1.4.A.4
33 | 150 | Civil | 33 0530 | 0 | Coatings and Linings for Utilities | Material certifications | QC Submittal | Yes | No | CO |  | 33 0530 1.3.A.1
33 | 151 | Civil | 33 0530 | 0 | Coatings and Linings for Utilities | Test and inspection reports | QC Submittal | Yes | No | CO |  | 33 0530 1.3.A.2
33 | 152 | Civil | 33 1000 | 9 | Water Utilities | Installation instructions for valves and accessories | QC Submittal | Yes | No | CO |  | 33 1000 1.4.A.2
33 | 153 | Civil | 33 1000 | 9 | Water Utilities | Existing systems pressure calculations | QC Submittal | Yes | No | CO |  | 33 1000 1.4.A.3
33 | 154 | Civil | 33 1000 | 9 | Water Utilities | Certifications of welders and welding procedures | QC Submittal | Yes | No | CO |  | 33 1000 1.4.A.4
33 | 155 | Civil | 33 1000 | 9 | Water Utilities | Tracing wire continuity test report | QC Submittal | Yes | No | CO |  | 33 1000 1.4.A.6
33 | 156 | Civil | 33 1300 | 6 | Disinfecting of Water Utility Distribution [22 0816] | Test results | QC Submittal | Yes | No | CO |  | 33 1300 1.4.A.1 - 3
33 | 157 | Civil | 33 3000 | 7 | Sanitary Sewerage Utilities | Welders certifications and welding procedures | QC Submittal | Yes | No | CO |  | 33 3000 1.3.A.2
33 | 158 | Civil | 33 3000 | 7 | Sanitary Sewerage Utilities | Submittals for the Horizontal Directional Drilling | QC Submittal | Yes | No | CO |  | 33 3000 1.3.A.3
33 | 159 | Civil | 33 3000 | 7 | Sanitary Sewerage Utilities | Tracing wire continuity test report | QC Submittal | Yes | No | CO |  | 33 3000 1.3.A.4
33 | 160 | Civil | 33 3200 | 7 | Wastewater Utility Pumping Stations | Power and controls cables | QC Submittal | Yes | No | CO |  | 33 3200 1.3.A.2
33 | 161 | Civil | 33 3200 | 7 | Wastewater Utility Pumping Stations | Pump curves | QC Submittal | Yes | No | CO |  | 33 3200 1.3.B.1
33 | 162 | Civil | 33 3200 | 7 | Wastewater Utility Pumping Stations | Operation and maintenance data | QC Submittal | Yes | No | CO |  | 33 3200 1.3.B.2
33 | 163 | Civil | 33 3200 | 7 | Wastewater Utility Pumping Stations | Test procedure | QC Submittal | Yes | No | CO |  | 34 3200 1.3.B.2.b
33 | 164 | Civil | 33 4000 | 4 | Storm Drainage Utilities | Installation instructions for accessories | QC Submittal | Yes | No | CO |  | 33 4000 1.3.A.2
33 | 165 | Civil | 33 4000 | 4 | Storm Drainage Utilities | Certifications for welders and welding procedures | QC Submittal | Yes | No | CO |  | 33 4000 1.3.A.3
33 | 166 | Civil | 33 5100 | 11 | Natural-Gas Distribution | Certified material test repot | QC Submittal | Yes | No | CO |  | 33 5100 1.3.A.2
33 | 167 | Civil | 33 5100 | 11 | Natural-Gas Distribution | Certification of compliance | QC Submittal | Yes | No | CO |  | 33 5100 1.3.A.3
33 | 168 | Civil | 33 5100 | 11 | Natural-Gas Distribution | Offsite and onsite welding requirements | QC Submittal | Yes | No | CO |  | 33 5100 1.3.A.4
33 | 169 | Civil | 33 5100 | 11 | Natural-Gas Distribution | Horizontal Directional Drilling | QC Submittal | Yes | No | CO |  | 33 5100 1.3.A.5
33 | 170 | Civil | 33 5100 | 11 | Natural-Gas Distribution | Tracing wire continuity test report | QC Submittal | Yes | No | CO |  | 33 5100 1.3.A.6
33 | 171 | Civil | 33 5100 | 11 | Natural-Gas Distribution | Required fabrication requirements documents | QC Submittal | Yes | No | CO |  | 33 5100 1.3.B
33 | 172 | Civil | 33 6300 | 5 | Steam Energy Distribution | Certified material test report (CMTR) for the pipe | QC Submittal | Yes | No | CO |  | 33 6300 1.5.A.2
33 | 173 | Civil | 33 6300 | 5 | Steam Energy Distribution | Certification of welders and qualified welding procedures | QC Submittal | Yes | No | CO |  | 33 6300 1.5.A.3
33 | 174 | Civil | 33 6300 | 5 | Steam Energy Distribution | Welding process visual examination report | QC Submittal | Yes | No | CO |  | 33 6300 1.5.A.4
33 | 175 | Civil | 33 6300 | 5 | Steam Energy Distribution | Installation instructions | QC Submittal | Yes | No | CO |  | 33 6300 1.5.A.5
33 | 176 | Civil | 33 6300 | 5 | Steam Energy Distribution | Plan and profile for steam/condensate piping system | QC Submittal | Yes | No | CO |  | 33 6300 1.5.A.6
33 | 177 | Civil | 33 6300 | 5 | Steam Energy Distribution | Thermal expansion calculation for steam/condense piping system | QC Submittal | Yes | No | CO |  | 33 6300 1.5.A.7
33 | 178 | Electrical | 33 7119 | 6 | Electrical Underground Ducts and Manholes | Pre-Concrete Placement Inspection | QC Verification | Yes | Yes | QC/OBI |  | 33 7119 3.3.J Rev. 6
33 | 179 | Electrical | 33 7119 | 6 | Electrical Underground Ducts and Manholes | Blockage Test | QC Verification | Yes | Yes | QC/OBI |  | 33 7119 3.3.K Rev. 6
33 | 180 | Electrical | 33 7119 | 6 | Electrical Underground Ducts and Manholes | Blockage Test Reports | QC Submittal | No | No | CO |  | 33 7119 3.3.K.4
33 | 181 | Electrical | 33 7119 | 6 | Electrical Underground Ducts and Manholes | Manhole Inspection | QC Verification | Yes | Yes | QC/OBI |  | 33 7119 3.7.B Rev. 6
40 | 182 | Mechanical | 40 0504 | 0 | Process Piping | Submit Test and Inspection Plans | QC Submittal | No | Yes | CO |  | 40 0504 1.4.C.5 Rev. 0 40 0504 1.5.B Rev 0
40 | 183 | Mechanical | 40 0504 | 0 | Process Piping | Submit Test Reports | QC Submittal | No | Yes | CO |  | 40 0504 1.4.C.6 Rev. 0 40 0504 1.5.B Rev 0
40 | 184 | Mechanical | 40 0504 | 0 | Process Piping | Submit certifications | QC Submittal | No | Yes | CO |  | 40 0504 1.4.C.7 Rev. 0
41 | 185 | Mech/Struc | 41 2213.13 | 2 | Bridge Cranes | Certification of installation | QC Submittal | No | Yes | CO |  | 41 2213.13 3.5.A Rev 2
41 | 186 | Mech/Struc | 41 2213.13 | 2 | Bridge Cranes | Quality control testing | QC Submittal | No | Yes | CO |  | 41 2213.13 3.6.B Rev 2
41 | 187 | Mech/Struc | 41 2225 | 1 | Hoist and Trolleys | Submittals IAW 01 3300 | QC Submittal | No | Yes | CO | Section 01 3300 | 41 2225 1.5 Rev. 1

## Code-Based Inspections
Reference | Title | Description | Notes
Constructor shall notify the STR when work is ready for inspection and provide access to and means for inspections of such work (2021 IBC 110.5)
| 2021 UNIFORM PLUMBING CODE -- HOLD POINTS FOR LANL INSPECTOR (OBI) | Applicable to plumbing and fixtures, water heaters, water supply and distribution, sanitary drains and vents, storm drainage and fuel gas piping.
2021 UPC 105.2 | Underground inspection | The underground inspection shall be made after trenches or ditches are excavated and bedded, piping installed, and before backfill is put in place.
2021 UPC 105.2 | Rough-in inspection | Rough-in inspection shall be made prior to the installation of wall or ceiling membranes.
2021 UPC 105.2 | Final inspection | Final inspection shall be made upon completion of the installation.
| 2021 UNIFORM MECHANICAL CODE -- HOLD POINTS FOR LANL INSPECTOR (OBI) | Applicable to ventilation, exhaust, ducting, combustion, chimney and vent, boiler and pressure vessels, refrigeration, hydronic, fuel gas piping and process piping.
2021 UMC 105.2 | Underground inspection | The underground inspection shall be made after trenches or ditches are excavated and bedded, piping installed, and before backfill is put in place.
2021 UMC 105.2 | Rough-in inspection | Rough-in inspection shall be made prior to the installation of wall or ceiling membranes.
2021 UMC 105.2 | Final inspection | Final inspection shall be made upon completion of the installation.
2020 NATIONAL ELECTRCIAL CODE -- HOLD POINTS FOR LANL CHIEF ELECTRICAL INSPECTOR'S OFFICE (CEIO/LANL OSH-ISH)
2021 IBC K106.2 | Underground inspection | Underground inspection shall be made after trenches or ditches are excavated and bedded, piping and conductors installed, and before backfill is put in place. Where excavated soil contains rocks, broken concrete, frozen chunks, and other rubble that would damage or break the raceway, cable or conductors, or where corrosive action will occur, protection shall be provided in the form of granular or selected material, approved running boards, sleeves or other means.
2021 IBC K106.3 | Rough-in inspection | Rough-in inspection shall be made after the roof, framing, fireblocking and bracing are in place and all wiring and other components to be concealed are complete, and prior to the installation of wall or ceiling membranes.
2021 IBC 110.3.10 | Final inspection (CEIO) | Final inspection shall be made upon completion of the installation (and to receive authorization to energize; ref. LANL P101-13 Electrical Safety [Att. A 3.4.3.B])
2021 INTERNATIONAL FIRE CODE -- HOLD POINTS FOR LANL INSPECTION (FPO)
2015 IFC 105.2.2 | Final inspection | Before a new operational permit is is approved, the fire code official is authorized to inspect the receptacles, vehicles, buildings, devices, premises, storage spaces or areas to be used to determine compliance with this code or any operational constraints required.
2021 INTERNATIONAL BUILDING CODE -- SECTION 110.3 REQUIRED INSPECTIONS -- HOLD POINTS FOR LANL INSPECTOR (OBI)
2021 IBC 110.3.1 | Footing and foundation inspection | Footing and foundation inspections shall be made after excavations for footings are complete and any required reinforcing steel is in place. For concrete foundations, any required forms shall be in place prior to inspection. Materials for the foundation shall be on the job, except where concrete is ready mixed in accordance with ASTM C 94, the concrete need not be on the job.
2021 IBC 110.3.2 | Concrete slab and under-floor inspection | Concrete slab and under-floor inspections shall be made after in-slab or under-floor reinforcing steel and building service equipment, conduit, piping accessories and other ancillary equipment items are in place, but before any concrete is placed or floor sheathing installed, including the subfloor.
2021 IBC 110.3.3 | Lowest floor elevation | In flood hazard areas, upon placement of the lowest floor, including the basement, and prior to further vertical construction, the elevation certification required in Section 1612.5 shall be submitted to the building official. | In flood hazard area only
2021 IBC 110.3.4 | Frame inspection | Framing inspections shall be made after the roof deck or sheathing, all framing, fire-blocking and bracing are in place and pipes, chimneys and vents to be concealed are complete and the rough electrical, plumbing, heating wires, pipes and ducts are approved.
2021 IBC 110.3.6 | Lath, gypsum board and gypsum panel product inspection | Lath, gypsum board and gypsum panel product inspections shall be made after lathing, gypsum board and gypsum panel products, interior and exterior, are in place, but before any plastering is applied or gypsum board and gypsum panel product joints and fasteners are taped and finished. | only for fire-resistance-rated assembly or shear assembly
2021 IBC 110.3.7 | Weather-exposed balcony and walking surface waterproofing | Where balconies or other elevated walking surfaces have weather-exposed surfaces, and the structural framing is protected by an impervious moisture barrier, all elements of the impervious moisture barrier system shall not be concealed until inspected and approved | Exception: Where special inspections are provided in accordance with Section 1705.1.1, Item 3
2021 IBC 110.3.8 | Fire- and smoke-resistant penetrations | Protection of joints and penetrations in fire-resistance-rated assemblies, smoke barriers and smoke partitions shall not be concealed from view until inspected and approved. | Includes fire-resistant doors (incl. access, frames, glazing, hardware), windows
2021 IBC 110.3.9 | Energy efficiency inspections | Inspections shall be made to determine compliance with Chapter 13 and shall include, but not be limited to, inspections for: envelope insulation R- and U-values, fenestration U-value, duct system R-value, and HVAC and water-heating equipment efficiency. | Additional inspections may be required for LEED and/or Guiding Principles when followed (larger projects; ref. ESM Ch. 14)
2021 IBC 110.3.10 | Final inspection | The final inspection shall be made after all work required by the building permit is completed.
2021 INTERNATIONAL BUILDING CODE -- SECTION 1705 REQUIRED SPECIAL INSPECTIONS AND TESTS (MOST COMMONLY USED) -- HOLD POINTS FOR LANL SPECIAL INSPECTOR (SI)
2021 IBC 1705.2.1 | Structural Steel - Periodic Special Inspection | Fabrication, Installation, Welding and High strength Bolting | See exceptions under 1705.2
2021 IBC 1705.2.1 | Structural Steel -- Continuous Special Inspection | Fabrication, Installation, Welding and High strength Bolting | See exceptions under 1705.2
2021 IBC 1705.2.2 | CFS Deck -- Periodic Special Inspection | Material, placement, welding and fastening | See exceptions under 1705.2
2021 IBC 1705.2.2 | CFS Deck -- Continuous Special Inspection | Material, placement, welding and fastening | See exceptions under 1705.2
2021 IBC 1705.2.3 | Open-web Steel Joists and Joist Girders -- Periodic Special Inspection- | End connections and bridging | See exceptions under 1705.2
2021 IBC 1705.2.3 | Cold-formed steel trusses -- Special Inspection | temporary and permanent individual truss member restraint/bracing | applicable only to trusses spanning 60 feet or greater
2021 IBC 1705.3 | Concrete Construction -- Periodic Special inspection | Reinforcement, welds, anchors cast-in or post-installed, design mixes not pre-approved, curing, erection of precast members, concrete strength, and formwork | See exceptions under 1705.3. Where P-I anchors are shown as seismically-exempt, no SI required.
2021 IBC 1705.3 | Concrete Construction -- Continuous Special inspection | Welds, post-installed anchors, strength, slump, air, temperature, application, and prestressing. | See exceptions under 1705.3. Where P-I anchors are shown as seismically-exempt, no SI required.
2021 IBC 1705.4 | Masonry Construction -- Periodic Special inspection | Grout, mortar, anchoring, structural elements, rebar, pre-stressing tendons | See exceptions under 1705.4. Where P-I anchors are shown as seismically-exempt, no SI required.
2021 IBC 1705.4 | Masonry Construction -- Continuous Special inspection | welding, prestressing, grout and anchors | See exceptions under 1705.4. Where P-I anchors are shown as seismically-exempt, no SI required.
2021 IBC 1705.6 | Soils -- Periodic Special inspection | Excavations and subgrade | See exceptions under 1705.6
2021 IBC 1705.6 | Soils -- Continuous Special inspection | Backfill | See exceptions under 1705.6
2021 IBC 1705.10 | Fabricated Structural Items -- Periodic Special inspection | Offsite Fabrication Inspection
2021 IBC 1705.13 | Seismic Resistance -- Special inspection | Structural Steel Systems, CFS light-frame construction, Designated Seismic Systems, and Plumbing, Mechanical and Electrical Components | See exceptions under 1705.13
2021 IBC 1705.14 | Seismic Resistance -- Testing | Structural Steel Systems, CFS light-frame construction, Designated Seismic Systems, and Plumbing, Mechanical and Electrical Components
2021 IBC 1705.15 | Sprayed Fire-Resistant Materials -- Periodic Special inspection | application, patching, and before concealment
2021 IBC 1705.16 | Mastic and Intumescent Fire-Resistant Coatings -- Periodic Special inspection | application and before concealment
2021 IBC 1705.17 | Exterior Insulation and Finish Systems (EIFS) -- Periodic Special inspection | Water-resistive barrier coating | exception for those over a water-resistive barrier with a means of draining moisture to the exterior or EIFS over masonry or concrete walls
2021 IBC 1705.18 | Fire-Resistant Penetrations and Joints -- Periodic Special inspection | Penetration firestops, fire-resistant joints, and perimeter fire barrier systems
2021 IBC 1705.19 | Smoke Control -- Special inspection | Prior to concealment of ductwork and Prior to occupancy