Form must be signed and approved by a Certified DCPSO in order to procure (per ASM Form 410).

(data for example only, delete when using form)

| PSCS # Pressure System ID# | TA | Bldg | Vessel Type ASME Section | Product Information Manufacturer and Model Number | Rating Gallons, Cubic Feet, BTU, etc | Maximum Allowable Working Pressure (gauge) Psig | Minimum and Maximum Allowable Working Temperature F | ASME Relief Device Required | Relief Flow Corrosion Allowance Inch | CSD1 or NFPA 85 | Relief Devices Supplied by Fabricator or others? |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 2201 | 53 | 4 | Section I (Power Boiler) | Clever Brooks CBEX | 200 HP (669,500 BTU/Hr Boiler Output) | 200 psig saturated steam | 75 to 388 F | 2 (1) 1-1/2” (1) 1-1/4” | 1/16 | CSD-1 | Fabricator |
| 2201 | 53 | 4 | Section I (Power Boiler) |  | 250,000 BTU/Hr Boiler rating | 175 psig hot water | 75 to 250 F | 2 (1) 1-1/2 (1) 1-1/4 | 1/16 | CSD-1 | Fabricator |
| 2201 | 53 | 4 | Section I (Power Boiler) | Clever Brooks CBEX Elite | 1200 HP (40,170,000 BTU/Hr Boiler Output) | 200 psig saturated steam | 75 to 388 F | 3 2-1/2” each | 1/16 | NFPA 85 | Fabricator |
| 2011 | 53 | 1 | Section IV (Heating Boiler) | Cleaver Brooks CFLC | Boiler rating 10,000,000 BTU/Hr (9,400,000 BTU/HR Output) | 160 psig | 75 to 250 F | 1 set at 125 psig | 1/16 | CSD-1 | LANL Supplied see ADMIN-3-FMO1-RO1 for updated information. |
| 5903 | 55 | 0400 | Section VIII (Pressure Vessel Div. 1 (Design by Rule) | Prentex Alloy Fabriators, Inc. | 72 OD x 140 Seam | -15 (full vacuum) to 150 psig | -20 to 650 psig | NA | 1/16 | NA | Fabricator |
| 247 | 03 | 2327 | Section VIII (Heat Exchanger Div. 1 (Design by Rule) Tubular Exchanger Manufacturers Association (TEMA) | Alloy Engineering | Shell and Tube Exchanger 24 in x 100 in | 250 psig (shell and tubes) | 75 to 1200 F | 1 shell 1 ½ in 1 tube 1 in | 1/16 | NA | Fabricator |
| 3864 | 03 | 0040 | Section VIII Div. 1 (Cryogenic) Interior CGA 341 Exterior | Chart Industries HS-1500SC | 1580 gallon Cryogenic LN2 | 250 psig | -320F to 100 F | Internal Vessel 2 Rupture Discs 2 Relief Devices Annulus: 1 rupture disc | 1/16 | NA | Fabricator |
| 3036 | 53 | 0003 | Section VIII (Pressure Vessel) Div. 2 (Design by Analysis) | Prentex Alloy Fabriators, Inc. | 500 gallon vertical storage tank; flammable liquid | -15 (full vacuum) to 150 psig | 0 to 100 F | 1 each 1 ½ inch 150 psig | 1/16 | NA | Fabricator |
| 7777 | 03 | 0003 | Section VIII (Pressure Vessel) . Div. 3 (Extreme pressures or impulse loaded) | Engineered Pressure Systems, Inc | 2.5 meter Diameter x 7 Meter Long | 1500 bar (3,132,815 psig) | 40 F to 140 F | 1 2” rupture disc | 1/16 | NA | Fabricator |
| 5751 | 50 | 0001 | Section X, (Fiber-reinforced or plastic) RTP-1 | B&D Plastics, LLC | 5,800 gallon | 15 psig | 140 F | 1 each 2 inch 15 psig set | 1/16 | NA | Fabricator |
| 47 | 03 | 0170 | Section XII (Transport Tanks) | Gardner Cryogenics Liquid Helium Semi-Trailer | 15000 gallons 175-40 | 200 psig | 4 K to 300 K | 200 psig 2 outer rupture discs (200 psig) 2 annulus rupture discs (15 psig) | 1/16 | NA | Fabricator |

DCPSO:						Z #: 		 	Signature: 						Date:

# Footnotes

Recommend minimum 1/16 inch (0.0625 inch) or code minimum if greater

NFPA 85 applies to boilers greater than or equal to 12,500,000 BTU/Hr; CSD-1 applies to lower than 12,500,000 BTU/Hr