SECTION 01 3545

WATER DISCHARGE REQUIREMENTS

*************************************************************************************************************

LANL MASTER SPECIFICATION

Word file at http://engstandards.lanl.gov

This template must be edited for each project.  In doing so, specifier must add job-specific requirements.  Brackets are used in the text to indicate designer choices or locations where text must be supplied by the designer.  Once the choice is made or text supplied, remove the brackets.  The specifications must also be edited to delete specification requirements for processes, items, or designs that are not included in the project -- and specifier’s notes such as these.   To seek a variance from requirements in the specifications that are applicable, contact the Engineering Standards Manual (ESM) Civil POC. Please contact POC with suggestions for improvement as well.

When assembling a specification package, include applicable specifications from all Divisions, especially Division 1, General requirements.

Specification developed for ML-4 projects.  For ML-1, 2, and 3 applications, additional requirements and independent reviews should be added if increased confidence in procurement or execution is desired; see ESM Chapter 1, Section Z10 Specifications and Quality sections.

As with all LANL Master Specs, LANL must perform all tasks when not subcontracted.
*************************************************************************************************************

GENERAL

SECTION INCLUDES

Requirements for all LANL and Subcontractor personnel when there is a planned or accidental discharge of water, including those not covered by a NPDES permit, Ground Water Discharge Plan, or approved Notice of Intent (NOI).

RELATED SECTIONS

Section 22 0816, Disinfection of Potable Water Piping

DEFINITIONS

Discharge: Release of water to environment or sanitary sewer system due to an accidental spill or planned construction activity, e.g., flushing, piping disinfection, chemical water treatment of piping systems, hydrostatic piping tests, etc.

Best Management Practices (BMPs): Schedules of activities, prohibition of practices, maintenance procedures, and other management practices to prevent or reduce pollution of waters of the United States.  BMPs also include treatment requirements, operating procedures, and practices to control facility site runoff, spillage or leaks, sludge or waste disposal, or drainage from raw material storage. Physical practices to control facility site runoff can be, but are not limited to silt fences, graveled construction area entry/exit points, dikes, berms, wattles, ground covers, reduced discharge rates, armoring, or other such methods emplaced to eliminate erosion or transport by water of soil or other contaminants.

PRODUCTS

Not used.

EXECUTION

  - SubCONTRACTOR REQUIREMENTS (LANL, WHEN LANL IS PERFORMING WORK)

Discharges to Environment:

Discharges shall not cause or have the reasonable potential to cause or contribute to a violation of a water quality standard.

Employ BMPs to prevent erosion from discharge of water.

Chlorinated water used for disinfection shall be dechlorinated with a neutralizing agent per Section 22 0816 prior to discharge.  If discharge is not to a watercourse (e.g., flat ground), then total chlorine concentration shall be reduced to less than 1 ppm (part per million) -- typically the same as that in the Safe Drinking Water Act.

Discharges to a watercourse shall have a total chlorine concentration not greater than 0.011 mg/L (11 parts per billion). (This value is based on 1999 changes in the New Mexico stream standards that dropped chlorine limit from 1 ppm to 11 ppb).

For discharges of less than 5000 gallons, notify LANL Subcontract Technical Representative (STR) at least 5 working days before the planned discharge.

For discharges of 5000 gallons or more, notify LANL STR at least 30 working days before the planned discharge.

Discharges to Sanitary Sewer:

Notify LANL STR prior to any discharge.

Volumes greater than 1000 gallons shall not be discharged into the sanitary sewer systems without special approval by Sanitary Wastewater Operations Manager (665-7855) obtained via LANL STR.

Properly characterize discharges through the Waste Stream Profile (found in the Waste Compliance and Tracking System (WCATS) process and meet the TA-46 Wastewater Treatment Plant Waste Acceptance Criteria (WAC), refer to LANL Procedure P930-1 especially Attachment 16.

a. 	WAC limits for total chlorine concentration are 3 mg/L (3 ppm).  De-chlorinate water used for disinfection in excess of 20 gallons with neutralizing agent per Section 22 0816 prior to discharge.

Notify LANL STR immediately in the event of any accidental or unplanned discharge.

LANL REQUIREMENTS (e.g., STR)

Discharges to the Environment:

Keep a written record of each discharge by project.

For planned discharges of less than 5000 gallons, notify LANL Environmental Compliance Programs Group (ENV-CP) five working days prior to the discharge.  Following ENV-CP approval, complete and return attached form “Notice of Intent to Discharge/General Discharge Record” to ENV-CP, (e.g., Jacob Meadows jmeadows@lanl.gov).  Discharges will be documented by ENV-CP and submitted to NMED in LANL’s Quarterly Discharge Report.

For planned discharges of 5000 gallons or more, notify LANL ENV-CP Group at least [30 working days] in advance of the planned discharge. ENV-CP will review the proposed discharge to determine if submittal of an NOI is required.  If required, ENV-CP will develop and submit the NOI to NMED (NMED has up to 30 working days to respond).  ENV-CP will coordinate, if necessary, a review for potential impacts to critical habitat and Threatened and Endangered Species.

Discharges to the Sanitary Sewer:

Assist Subcontractor with characterizing discharges using Waste Stream Profile process and meeting the TA-46 Wastewater Treatment Plant Waste Acceptance Criteria (WAC) described in 3.1.B.3 above.

Notify Sanitary Wastewater Operations Manager (665-7855) at least 5 working days in advance for approval of planned discharge into sanitary waste water system.

Notify the LANL ENV-CP Group immediately in the event of any accidental or unplanned discharge.

END OF SECTION

**************************************************************

Do not delete the following reference information:

**************************************************************

THE FOLLOWING REFERENCE IS FOR LANL USE ONLY

This project specification is based on LANL Master Specification 01 3545, Rev. 7, dated February 27, 2015.

### NOTICE OF INTENT TO DISCHARGE

### GENERAL DISCHARGE RECORD

| LOCATION: TA: |  | BLDG: |  |
| --- | --- | --- | --- |
| FIRE HYDRANT / PIPE / SECONDARY CONTAIMENT / MANHOLE #: |  |
| USER GROUP: |  | CONTACT PERSON: |  |
| PHONE: |  | PAGER: |  |
| PERSON CONDUCTING SECONDARY CONTAINMENT DRAINAGE ACTIVITY: |  |
| DATE and TIME of DISCHARGE: |  | / |  |
| DURATION of DISCHARGE: |  | / |  |
| ENV-CP CONTACT: |  | Jacob Meadows, cell 231-0460, fx: 665-9344, jmeadows@lanl.gov |
| DESCRIPTION of DISCHARGE: |  |
| VOLUME of DISCHARGE: |  |
| CANYON AFFECTED: |  |
| SAMPLES TAKEN: | YES: |  | NO: |  |  |
| COMMENTS: |  |
| REVIEWED BY: |  | DATE: |  |
|  | ENV-CP |  |  |