Section 02 4115 
Electrical Demolition

  - *************************************************************************************************************

    - LANL MASTER SPECIFICATION SECTION

Rev. 4 Summary of Changes: Edited and updated as required for import into SpecLink.

      - NOTE TO SPECIFIER ON USAGE IN SPECLINK: Activate the Section by turning on Seq #0000, followed by activating paragraphs in PART 1, Article SECTION INCLUDES. This will activate related articles, paras/subparas in the rest of the Section (i.e., SECTION INCLUDES in PART 1 activates articles and paras/subparas in PARTS 2 and 3). If there are choice fields to edit the entire Section (typically in this first author note or beginning of the Section), make selections at those locations, which will filter through the remaining Section. All Articles, paragraphs and subparagraphs must be activated sequentially from top to bottom, unless noted otherwise.

      - This template must be edited for each project. In doing so, Specifier must add job-specific requirements. Selections and choice fields are used to indicate designer choices or locations where text must be supplied by the designer. The section must also be edited to remove requirements for processes, items, or designs that are not included in the project.

      - To seek a variance from applicable requirements in this Section, contact the Engineering Standards Manual (ESM) Electrical POC  (LANL access only). Please contact POC with suggestions for improvement as well. LANL personnel should submit here: Suggested Change or Request Clarification; subcontractors via email to engstandards@lanl.gov.

      - When assembling a specification package, include applicable Sections from all Divisions, especially Division 1, General Requirements.

      - Section is developed for ML-4 projects.  For ML-1, 2, and 3 applications, additional requirements and independent reviews should be added if increased confidence in procurement or execution is desired; see LANL ESM Chapter 1 - General, Section Z10 Specifications and Quality sections.

  - *************************************************************************************************************

PART 1 - GENERAL

Section Includes

      - ***************************************************************************************

      - Edit the following paragraphs to match Project requirements; omit those that are not needed.

      - ***************************************************************************************

Removal of existing electrical equipment, wiring, and conduit in areas to be remodeled; removal of designated construction; dismantling, cutting, and alterations for completion of the Work.

Disposal of materials.

Storage of removed materials.

Identification of utilities.

Removal of salvaged items and delivery to LANL.

Protection of items to remain ​​<< as scheduled at end of section; or  as indicated on Drawings>>​​.

Relocation of existing electrical equipment to accommodate construction.

related requirements

Section << 01 2500 - Substitution Procedures>>.

Section << 01 3300 - Submittal Procedures>>.

reference standards

29 CFR 1910 - Occupational Safety and Health Standards.

29 CFR 1926 - Safety and Health Regulations for Construction.

40 CFR 273 - Standards for Universal Waste Management.

40 CFR 761 - Polychlorinated Biphenyls (PCBs) Manufacturing, Processing, Distribution In Commerce, And Use Prohibitions.

49 CFR 178 - Specifications for Packaging.

NFPA 70 - National Electrical Code.

NFPA 70E - Standard for Electrical Safety in the Workplace.

LANL-PERFORMED WORK

None.

SUBMITTALS

Submit the following in accordance with Section ​<< 01 3300 - Submittal Procedures>>​.

        - ******************************************************************************

        - Edit the following subparagraphs to match Project requirements; omit subparagraphs that are not needed. Include submittals only to the extent required to assure quality.

        - ******************************************************************************

Action Submittal: Drawings: Indicate << demolition; and  removal sequence and location of salvageable items>>; location and construction of temporary work. Describe demolition removal procedures and schedule.

Informational Submittal at Closeout:  Project Record Documents: Record actual locations of capped << utilities;  conduits and equipment abandoned in place;  _______; and  _______>>.

REGULATORY REQUIREMENTS

      - ***************************************************************************************

      - NFPA 70, referenced in the choice field in the paragraph below, is an installation Code.  Unless electrical work is being performed to facilitate the demolition, this choice field should be set to N/A.

      - ***************************************************************************************

Conform to requirements of << NFPA 70 ,; or  None - N/A>><< 29 CFR 1926 ,; or  None - N/A>><<NFPA 70E>>, and LANL Policy P101-13 – Electrical Safety Program (LANL access only).

Each person performing electrical demolition shall be a “qualified person” as defined by <<NFPA 70E>>.

The following publications form a part of this specification to the extent referenced.

Environmental Protection Agency (EPA):

<<40 CFR 761>>

<<40 CFR 273>>​.

U.S. Department of Labor, Occupational Safety and Health Administration (OSHA):

<<29 CFR 1910>> Subpart G, Occupational Health and Environmental Control.

Department of Transportation (DOT):

<<49 CFR 178>>

COORDINATION

      - ***************************************************************************************

      - Edit the following paragraphs to match Project requirements; omit paragraphs that are not needed.

      - ***************************************************************************************

Conduct demolition to minimize interference with adjacent​​​<< and occupied; or  None - N/A>>​​​ building areas.

Coordinate and sequence demolition so as not to cause shutdown of operation of surrounding areas.

Shut-down Periods:

Arrange timing of electrical shut-down periods with the LANL Subcontract Technical Representative (STR).  Do not shut down any utility without prior written approval.

Keep shut-down period to minimum or use intermittent period as directed by the LANL STR.

Maintain life-safety systems in full operation in occupied facilities or provide notice a minimum of 3 days in advance.

Identify salvage items in cooperation with the LANL STR.

PART 2 - PRODUCTS

product options and substitutions

Alternate products may be accepted; follow Section << 01 2500 - Substitution Procedures>>.

MATERIALS AND EQUIPMENT

Provide materials and equipment for patching and extending work as specified in the individual Sections.

PART 3 - EXECUTION

EXAMINATION

Before work begins on the demolition or salvage of electrical equipment, wiring, or systems:

Inspect the site to identify any hazardous materials such as PCBs, asbestos, lead, mercury, or other heavy metal, or toxic, combustible, flammable, or explosive materials, or radioactive materials that may be handled, disturbed, or removed.  Typical locations of hazardous materials include:

Lead: Batteries in emergency luminaires, exit signs, fire alarm panels, security systems, UPS systems, and some switchgear. Lightning protection components on some exhaust stacks. Lamp bases

PCBs: Oil-filled transformers; potting material and/or capacitors in lighting ballasts; oil-filled capacitors associated with motors, UPS systems, voltage regulators, power-factor correction equipment

Asbestos: Pipe insulation, electrical insulation, circuit breakers

Mercury: Fluorescent lamps, HID lamps, thermostats, “silent” wall switches, some “silent” enclosed relays (Mercury wetted contacts)

Radioactive materials: Self-luminous exit signs, smoke detectors.

Verify whether PCB ballasts exist in luminaires that will be removed or relocated. If PCB light fixture ballasts exist, then follow requirements in the PCB BALLAST HANDLING AND DISPOSAL Article below.

Have the inspection results available at the worksite, including any drawings, plans or specifications, as appropriate, to show the locations of any hazardous substances.

Ensure that any hazardous materials found are suitably contained or removed.

During demolition work, if hazardous materials are discovered that were not identified in the initial inspection required above, stop work in the area and notify the STR. Do not resume work in the area until directed by the STR.

Verify wiring and equipment indicated to be demolished supply only abandoned facilities.

Verify termination points and lockout-tagout device locations are correct for the systems to be disconnected or removed.

Demolition Drawings are based on field observation and/or existing record documents.  Report discrepancies to the STR before beginning demolition work.

Beginning of demolition work means Subcontractor accepts existing conditions.

PREPARATION

      - ***************************************************************************************

      - Edit the following paragraphs to match Project requirements; omit articles that are not needed.

      - ***************************************************************************************

Protect existing materials, appurtenances, and equipment which are not to be demolished.  Repair or replace existing materials, appurtenances, and equipment, building exterior and interior, and landscaping altered or damaged during demolition work to match existing undisturbed conditions at no additional cost to LANL.

Erect, and maintain temporary safeguards, << including warning signs and lights;  barricades; and  similar measures>> for protection of the public, LANL personnel, Subcontractor’s employees, and existing improvements to remain.

Provide temporary egress signage and emergency lighting to meet Life Safety Code requirements.

Provide and maintain temporary weather protection during interval between demolition and removal of existing construction on exterior surfaces and installation of new construction to ensure that no water leakage or damage, or wind damage occurs to structure or interior areas of existing building.

Existing ​<< passenger elevator(s);  freight elevator(s); and  dumwaiter(s)>>​ ​<< may; or  may not>>​ be used for debris removal. ​<< Protect from damage.  Damage due to work of this Section shall be the responsibility of the Subcontractor.; or  None - N/A>>​

Use​<< a debris chute and ; or  None - N/A>>​covered debris bins to​<< remove and; or  None - N/A>>​ temporarily store  materials​<< from the _______; or  None - N/A>>​.  Location of​<< debris chute and; or  None - N/A>>​ bins shall be approved by the STR.

Maintain parking areas, driveways, exterior walkways, exit paths, and landscaping in a clean, undisturbed condition.

Coordinate utility outages with the LANL STR.

Request underground utilities and other underground systems to be located and marked within and surrounding construction areas.

All work on energized electrical utilities will be performed or supervised by LANL.

Protect utilities, and other underground systems, that are indicated to remain, from damage.

Protect smoke detectors from dust intrusion.

Provide temporary wiring and connections to maintain existing systems during construction. In particular, security systems, safety class systems, safety significant systems, and life safety systems must be maintained in operation at all times. This includes security and safety lighting.

      - ***************************************************************************************

      - Edit the following paragraphs to match Project requirements; omit paragraphs that are not needed.

      - ***************************************************************************************

Existing Medium-Voltage Utility System: Protect existing medium-voltage (e.g., 15 kV, 5 kV) utility equipment (e.g., utility transformers, switchgear, cables, ductbanks and manholes). Do not disturb or operate medium-voltage utility systems or equipment. Coordinate utility shutdowns, or equipment removal, with the LANL Utilities and Infrastructure Group through the LANL STR at least << 5; or  _______>> working days before required date.

Existing Low-Voltage Electrical Service or Feeder: Maintain existing low-voltage (e.g., 480 V, 208 V) electrical system in operation until new system is complete and ready for operation.  Disable system only to make switchovers and connections.  Obtain permission through the STR from the LANL Utilities and Infrastructure Group at least << 2; or  _______>> working days before partially or completely disabling system.  Minimize outage durations.  If required, make temporary connections to maintain systems in areas adjacent to work area.

Existing Fire Alarm System: Maintain existing fire alarm system in service until new system is accepted.  Disable system only to make switchovers and connections. Obtain permission through the LANL STR from the LANL Fire Marshal at least << 2; or  _______>> working days before partially or completely disabling system.  Minimize outage duration.  If required, make temporary connections to maintain service in areas adjacent to work area.

Existing Communication/Data System: Coordinate demolition work through the LANL STR with the LANL Telephony Group. Maintain existing telecommunications system in service until new system is complete and ready for service.  In general, the LANL Telephony Group will make switchovers and connections.  Obtain permission through the LANL STR from the LANL Telephony Group before removing telecommunications wiring or equipment.

      - ***************************************************************************************

      - Use the following paragraphs as many times to match special systems on Project; delete if not needed. For some systems, LANL will remove devices, then the Subcontractor will return to remove cables, conduit, and boxes.

      - ***************************************************************************************

Existing << _______>> System: Maintain existing system in service until new << _______>> system is complete and ready for service.  Disable system only to make switchovers and connections. Obtain permission through the LANL STR from << _______>> at least << 2; or  _______>>  working days before partially or completely disabling system.  Minimize outage duration. If required, make temporary connections to maintain service in areas adjacent to work area.

DEMOLITION AND EXTENSION OF EXISTING ELECTRICAL WORK

      - ***************************************************************************************

      - Edit the following paragraphs to match Project requirements; omit paragraphs that are not needed.

      - ***************************************************************************************

Demolish, relocate, and extend existing electrical work to installations to accommodate new construction.

Establish an electrically safe work condition in areas where electrical work is to be removed.

Comply with ​​​​<< LANL Policy P101-13 Electrical Safety Program (LANL access only); or  Sub-Contractors approved Safety & Health Plan>>​​​​

Comply with ​​​<< LANL Policy P101-18 Lockout/Tagout Program (LANL access only).; or  Sub-Contractor's approved Lockout/Tagout Program.>>​​​ Disconnect or shut off service to areas where electrical work is to be removed. Properly lockout and tag disconnecting means. Verify zero-voltage before beginning demolition.

Disconnect, remove, and cap designated utility lines within demolition areas.  Mark locations of disconnected utilities.  Identify utilities and indicate capping locations on Project Record Documents.

Protect and retain power to existing active equipment that is to remain.

Maintain access to existing electrical installations which remain active.  Modify installation or provide access panel as appropriate.

Install temporary wiring and connections to maintain existing systems during construction.

Remove equipment, materials, or fixtures which are to be reused.  Store and protect to prevent damage.

Disconnect, remove, or relocate existing electrical material and equipment interfering with new installation.

Remove electrical fixtures, equipment, related switches, receptacles, outlets, conduit, and wiring, which are not part of final project.  Note: Some equipment contains capacitors which can store energy even when disconnected from the system.  Understand the equipment before attempting to remove.

Remove items in an orderly manner.

Remove abandoned wiring to panelboard circuit breaker or source of supply, or as indicated on drawings.

Remove exposed abandoned raceways, including abandoned raceways above accessible ceiling finishes.  Cut raceways flush with walls and floors, seal openings, and patch surfaces.

Disconnect abandoned outlets and remove devices.  Remove abandoned outlets if raceway servicing them is abandoned and removed.  Provide blank cover for abandoned outlets which are not removed.

Remove lamps from abandoned luminaires. Refer to LAMP HANDLING AND DISPOSAL Article below.

Disconnect and remove abandoned luminaires. Refer to PCB BALLAST HANDLING AND DISPOSAL Article below. Remove brackets, stems, hangers, and other accessories.

Remove abandoned cable tray systems.

Disconnect and remove abandoned panelboards and distribution equipment.

Disconnect and remove electrical devices and equipment supplying utilization equipment that has been removed.

Remove exposed abandoned fasteners and supports, including abandoned components above accessible ceiling finishes. Cut embedded support elements flush with walls and floors.

        - ******************************************************************************

        - Edit the following subparagraph to match Project requirements; omit subparagraph if not needed.

        - ******************************************************************************

Disconnect and remove << _______>>.

Cap abandoned empty raceway at both ends.

If certain raceways and boxes are abandoned but not scheduled for removal, identify those items on the "As Built Drawings".

Provide proper and permanent support to adjacent structure for all raceways, cable trays, luminaires, and equipment to remain.

Repair adjacent construction and finishes damaged during demolition and extension work.

Patch and seal unused existing wall penetrations to match existing conditions and to restore fire rating.

Extend existing installations using materials and methods compatible with existing electrical installations, or as specified.  This includes the extension of the circuit from the last active device to the next device in the system to be activated.

        - ******************************************************************************

        - Edit the following subparagraph to match Project requirements; omit if not needed.

        - ******************************************************************************

Reconnect equipment being disturbed by renovation work and required for continued use to << ___ or; or  None - N/A>>​​ nearest available panel.

Investigate and measure the nature and extent of unanticipated items that conflict with intended function or design. Submit written report with accurate detailed information to the LANL STR. While awaiting instructions from the STR, rearrange selective demolition schedule as necessary to continue overall job progress without delay.

Stop work and notify the LANL STR immediately if structure or other items to remain appear to be endangered. Do not resume work until directed by the STR.

Remove demolished materials as work progresses.

EXISTING Electrical Distribution Equipment

Verify and identify loads supplied by circuits in existing electrical distribution equipment (e.g., switchgear, switchboards, motor control centers, panelboards) affected by the Work.

Tag unused circuits as spare.

Where existing circuits are indicated to be reused, confirm that these circuits are available and will not be feeding existing loads.

Remove existing cables/conductors that are no longer in use from distribution equipment to equipment.

Re-label circuit breakers, switches, and controllers to indicate loads supplied. Provide new, updated circuit directories where circuits in a panelboard have been modified or rewired.

PCB BALLAST HANDLING AND DISPOSAL

Generally, high power factor fluorescent light ballasts manufactured before 1978 and some HID ballasts contain PCB compounds in their capacitors. PCB ballast handling, storage, and disposal shall be in accordance with <<40 CFR 761>> and other applicable EPA PCB regulations.

Inspect all ballasts in all light fixtures (which will become the property of the Subcontractor and will be removed from the project site as part of this project) and take the actions described below.

All ballasts labeled as "NON-PCBs" or "NO PCBs" shall become the property of the Subcontractor.  If the PCB content is not stated on the ballast label, handle the ballast as a PCB ballast.

Remove PCB ballasts from the light fixtures and cut the wires off. However, before removal, carefully inspect PCB ballasts for leaks. If ballast appears to be leaking (evidenced by potting compound leaking out or by an oily film on the ballast surface) handle the ballast per <<40 CFR 761>> and other applicable EPA PCB regulations. Basically, this means the ballast is to be carefully removed from the fixture and placed in an approved drum. See subparagraph below for the drum specifications. The person removing the ballast from the fixture shall wear neoprene protective gloves, eye protection, and protective clothing as necessary.

If the fixture has also been contaminated, it will require cleaning to less than 10 micrograms/100 square centimeters contamination before disposal. This cleaning must be done by an approved PCB subcontractor and is not considered a part of this subcontract.  Contact the LANL STR to arrange cleanup by LANL.

Place the ballasts in US DOT approved type 17C or type 17H drums (barrels) furnished by the Subcontractor. Both 55-gallon and 30-gallon drums that meet the requirements of <<49 CFR 178>> are available from most drum suppliers. The quantity and size of the drums will be determined by the Subcontractor at the time of construction.

Place these barrels in storage with the cover that came with the barrels, in a location within a building, as designated by the LANL STR. Do not place the barrels outside where they are exposed to weather.

THESE BALLASTS ARE NOT TO BE REMOVED FROM THE WORK SITE BY THE SUBCONTRACTOR. To do so would violate DOT hazardous waste regulations and may result in a fine to the Subcontractor.

Label and mark the PCB storage drums with EPA approved PCB labels and the storage area with signs, marks, and lines to meet state and federal regulations.

Provide approved PCB absorbent materials to be stored immediately adjacent to the drum storage area. Do not place loose absorbent material in the drums.

Provide to the LANL STR, in written form, a total count of these ballasts (or their total weight by barrel) and where they are stored.

When the ballast demolition is completed and all PCB ballasts are placed in drums ready to be picked up for disposal, notify the STR. The STR will make pickup arrangements.

LAMP HANDLING AND DISPOSAL

Most lamps (fluorescent, incandescent, and HID) contain mercury and/or lead (in the base) as well as other heavy metals and compounds which are regulated by the EPA during the disposal process. The handling, storage, and disposal of lamps shall be in accordance with <<40 CFR 273>>.

Handle lamps which have been removed from service for disposal as follows:

Remove all lamps (fluorescent, incandescent, and HID) from light fixtures before removal of the fixture from its mounted position. This is to reduce the likelihood that the lamp(s) will be broken. If the Subcontractor breaks more than 1% of the total lamps removed for the project, the Subcontractor will be charged the cost difference between disposal of broken lamps and disposal of unbroken lamps for all lamps broken in excess of 1% of the total lamps removed in the project.

Provide containers large enough to fully conceal the removed lamps and appropriate for lamp transportation. Place removed lamps in containers and mark container with the number and type of lamps. Place containers in storage in a location on LANL property (this may be in another building) arranged by the LANL STR. The Subcontractor shall label the area as "Hazardous Material Storage - Mercury".

Provide to the LANL STR, in written form, a count of all stored lamps by type at the completion of the project.

The STR will make arrangements for the lamps to be picked up.

CLEANING AND REPAIR

      - ***************************************************************************************

      - Edit the following paragraphs to match Project requirements; omit paragraphs that are not needed. Identify on the Drawings items to be cleaned or repaired.

      - ***************************************************************************************

Clean and repair existing materials and equipment which remain or are to be reused.

Electrical Distribution Equipment: Clean exposed surfaces and check tightness of electrical connections. Replace damaged circuit breakers and provide approved closure plates for vacant positions.

Luminaires: Remove existing luminaires for cleaning.  Use mild detergent to clean all exterior and interior surfaces; rinse with clean water and wipe dry.  Replace lamps, ballasts (if required) and broken electrical parts. Test for proper operation.

DISPOSITION OF MATERIAL AND EQUIPMENT

Remove and protect items indicated ​​<< on Drawings; or  in Schedule>>​​ to be salvaged and deliver in good condition to LANL at the location designated by the STR.

Items of salvageable value may be removed as work progresses.  Transport salvaged items from site as they are removed.

Unless indicted otherwise, material removed under this Subcontract which is not to be salvaged or reused in the Project shall become the property of the Subcontractor.

Unless indicated otherwise, immediately remove demolished material from site.  Do not store or permit debris to accumulate at the site. Dispose of materials legally off site. Do not burn or bury materials on site.

Upon completion, clean the entire area of demolition residue satisfactory for the continuation of the Work. Remove temporary work.

INSTALLATION of Relocated Equipment

Install relocated materials and equipment under the provisions of the applicable Sections of these Specifications.

SCHEDULES

      - ***************************************************************************************

      - Edit the following paragraphs to match Project requirements; omit paragraphs that are not needed. Include schedule when known items are to be turned over to LANL, salvaged and reused in construction later, or are destined for other use. Identify on the Drawings items to be cleaned or repaired.

      - ***************************************************************************************

Remove, store, and protect the following materials and equipment:

<< _______>>.

<< _______>>.

<< _______>>.

Remove the following equipment and materials for retention by LANL.  Deliver to location designated by the LANL STR:

<< _______>>.

<< _______>>.

<< _______>>.

LANL will remove the following material and equipment before start of demolition:

<< _______>>.

<< _______>>.

<< _______>>.

Protect the following materials and equipment to remain in place during construction:

<< _______>>.

<< _______>>.

<< _______>>.

END OF SECTION

    - **********************************************************************************************

      - Do not omit the following reference information:

    - **********************************************************************************************

THE FOLLOWING STATEMENT IS FOR LANL USE ONLY

THIS PROJECT SPECIFICATION SECTION IS BASED ON LANL MASTER SPECIFICATION SECTION 02 4115, REV. 4, DATED APRIL 15, 2026.