Section 03 6000 
Grouting

  - *************************************************************************************************************

    - LANL MASTER SPECIFICATION SECTION

Rev. 5 Summary of Changes: Edited and updated as required for import into SpecLink.

      - NOTE TO SPECIFIER ON USAGE IN SPECLINK: Activate the Section by turning on Seq #0000, followed by activating paragraphs in PART 1, Article SECTION INCLUDES. This will activate related articles, paras/subparas in the rest of the Section (i.e., SECTION INCLUDES in PART 1 activates articles and paras/subparas in PARTS 2 and 3). If there are choice fields to edit the entire Section (typically in this first author note or beginning of the Section), make selections at those locations, which will filter through the remaining Section. All Articles, paragraphs and subparagraphs must be activated sequentially from top to bottom, unless noted otherwise.

      - This template must be edited for each project. In doing so, Specifier must add job-specific requirements. Selections and choice fields are used to indicate designer choices or locations where text must be supplied by the designer. The section must also be edited to remove requirements for processes, items, or designs that are not included in the project.

      - To seek a variance from applicable requirements in this Section, contact the Engineering Standards Manual (ESM) Structural POC  (LANL access only). Please contact POC with suggestions for improvement as well. LANL personnel should submit here: Suggested Change or Request Clarification; subcontractors via email to engstandards@lanl.gov.

      - When assembling a specification package, include applicable sections from all Divisions, especially Division 1, General Requirements.

      - This Section has been written to meet requirements of buildings classified as Natural Phenomena Hazard (NPH) Risk Category (RC) I, II, III or IV, and projects classified as ML-3 or ML-4. In general, this section does not apply to nuclear facilities. This section may apply to facilities that, because of the low amount of nuclear material at risk, are classified as RC IV.

      - For nuclear applications, ML-1/ML-2 (and ML-3 potentially), and NPH Design Category 3 (NDC-3), Section ​<< 03 6021 - Grouting - High Confidence>>​  should be used.

      - ==========================================================

      - This section includes concrete repair material, Portland cement grout, rapid-curing epoxy grout, and non-shrink cementitious grout that will be used in structural applications (i.e., the grout will be part of a load path)* vs. nonstructural applications (e.g., minor/local concrete surface repair, etc.).

        - • The concrete repair material herein is a dimensionally stable (i.e., “shrinkage-compensated”), pre-mixed, pre-packaged product. Although generally termed “material” (versus grout) herein, its procurement and use is similar enough to warrant inclusion in this Section.

        - • The Portland cement grout herein is a site-mixed, “general purpose grout.” While being the cheapest of the alternatives herein, it lacks many of the attributes the others have, chief among them being dimensional stability (i.e., it’s much more subject to shrinkage than the alternatives).

        - • The rapid-curing epoxy grout herein is a pre-mixed, pre-packaged product that is typically used for grouting base plates, machinery, equipment, etc.; and when dynamic/impact loading, vibration, or chemical attack is/are applicable. It’s ideal for applications where precise change in elevation during curing is required. Additionally, epoxy grout can be tailored to provide improved properties related to high early strength; and high chemical, acid, and fatigue resistance

        - • The non-shrink cementitious grout herein is a pre-mixed, pre-packaged product typically used for grouting base plates, machinery, equipment, etc. While non-shrink cementitious grout is typically less resistant to chemical attack and fatigue than epoxy grout, it is more resistant to heat and tends to be less expensive. It is also more “precise” than the Portland cement grout option herein.

      - * Although grout for prestressed, precast concrete (ref. Section << 03 4100 - Precast Structural Concrete>>) and reinforced masonry (ref. Section << 04 2220 - Reinforced Unit Masonry>>) is structural, its use in those applications is too specialized to be included herein; therefore, Sections << 03 4100 - Precast Structural Concrete>> and << 04 2220 - Reinforced Unit Masonry>> have their own grout requirements.

  - *************************************************************************************************************

PART 1 - GENERAL

SECTION INCLUDES

Requirements for furnishing, delivering, and installing site-mixed and/or pre-mixed, pre-packaged material including:

        - ******************************************************************************

        - Select the grouting or repair material to be used in the project from the list below.

        - If two or more materials are retained and their intended locations are not identified elsewhere (e.g., in other specification sections or drawings), revise this Section (at minimum PART 3) to clearly indicate the location of each material.

        - ******************************************************************************

Concrete repair material

Portland cement grout

Rapid-curing epoxy grout

Non-shrink cementitious grout

      - ***************************************************************************************

      - Use this section for structural repairs only. Do not use for cosmetic/surface repairs.  Use ACI 301 guidelines for cosmetic or nonstructural surface repairs.

      - Per ACI 301-20, 5.2.1.6 Surface Repair Materials — "Unless otherwise specified, use repair mortar for surface defects. For exposed concrete, repair mortar shall match the color of the adjacent concrete." Refer to ACI 301-20, Section 5.3.7, Repair of Surface Defects, for additional requirements.

      - Select repair materials specified in ACI 301-20 or listed in this Section. If using materials from Section << 03 6021 - Grouting - High Confidence>>​​, be aware that the repaired surface may not visually match the existing in-situ concrete.

      - ***************************************************************************************

Do not use this Section for cosmetic repairs, such as filling form-tie holes and other nonstructural surface defects.

Related Requirements

Section << 01 2500 - Substitution Procedures>>.

Section << 01 4000 - Quality Requirements - Non-Nuclear>>.

Section ​<< 01 6000 - Product Requirements>>​.

Section << 03 3001 - Reinforced Concrete>>.

reference standards

ACI CODE-318 - Building Code for Structural Concrete—Code Requirements and Commentary.

ACI SPEC-117 - Specification for Tolerances for Concrete Construction and Materials.

ACI SPEC-301 - Specifications for Concrete Construction.

ASTM C33/C33M - Standard Specification for Concrete Aggregates.

ASTM C40 - Standard Test Method for Organic Impurities in Fine Aggregates for Concrete.

ASTM C109/C109M - Standard Test Method for Compressive Strength of Hydraulic Cement Mortars (Using 50 mm [2 in.] Cube Specimens).

ASTM C150/C150M - Standard Specification for Portland Cement.

ASTM C157/C157M - Standard Test Method for Length Change of Hardened Hydraulic-Cement Mortar and Concrete.

ASTM C307 - Standard Test Method for Tensile Strength of Chemical-Resistant Mortar, Grouts, and Monolithic Surfacings.

ASTM C531 - Standard Test Method for Linear Shrinkage and Coefficient of Thermal Expansion of Chemical-Resistant Mortars, Grouts, Monolithic Surfacings, and Polymer Concretes.

ASTM C579 - Standard Test Methods for Compressive Strength of Chemical-Resistant Mortars, Grouts, Monolithic Surfacings, and Polymer Concretes.

ASTM C666 - Standard Test Method for Resistance of Concrete to Rapid Freezing and Thawing.

ASTM C827/C827M - Standard Test Method for Change in Height at Early Ages of Cylindrical Specimens of Cementitious Mixtures.

ASTM C882/C882M - Standard Test Method for Bond Strength of Bonding Systems Used with Concrete by Slant Shear.

ASTM C942 - Standard Test Method for Compressive Strength of Grouts for Preplaced-Aggregate Concrete in the Laboratory.

ASTM C1090 - Standard Test Method for Measuring Changes in Height of Cylindrical Specimens of Hydraulic-Cement Grout.

ASTM C1107/C1107M - Standard Specification for Packaged Dry, Hydraulic-Cement Grout (Nonshrink).

ASTM C1202 - Standard Test Method for Electrical Indication of Concrete’s Ability to Resist Chloride Ion Penetration.

ASTM C1218/C1218M - Standard Test Method for Water-Soluble Chloride in Mortar and Concrete.

ICRI 310.2R - Selecting and Specifying Concrete Surface Preparation for Sealers, Coatings, Polymer Overlays, and Concrete Repair.

DEFINITIONS

For definitions and acronyms, refer to COE Glossary of Terms.

Cementitious materials: Materials as defined in <<ACI CODE-318>> Chapter 2, which have cementing value when used in concrete either by themselves, such as Portland cement, blended hydraulic cements, and expansive cement; or such materials in combination with fly ash, other raw or calcined natural pozzolans, silica fume, and slag cement.

Creep: Time-dependent deformation due to sustained load.

Material: Unless stated otherwise, any/all of concrete repair material, Portland cement grout, rapid-curing epoxy grout, and non-shrink cementitious grout.

Restore: Repair a structural item (e.g., beam, column, foundation, etc.) to its near-original state.

Shrinkage: Time-temperature-humidity-dependent volume reduction of concrete as a result of hydration, moisture migration, and drying process.

Unsound concrete—concrete that is fractured, delaminated, spalled, deteriorated, defective, contaminated, or otherwise damaged.

f’c: Specified compressive strength of material, psi.

ACTION SUBMITTALS

      - ***************************************************************************************

      - Request only the submittals necessary to verify compliance with Project requirements. For example, based on how the four material types are specified in Part 2, the first paragraph below is required only to verify compliance for Portland cement grout.

      - ***************************************************************************************

Product data on Portland cement, fine aggregate (demonstrating compliance with <<ASTM C33/C33M>> and <<ASTM C40>>)<< and Insert Other Specified Requirements Here; or  None - N/A>>.

Product data for each pre-packaged material to be used, including Technical Data Sheet, Safety Data Sheet and manufacturer’s instructions for mixing, handling, surface preparation, placement, temperature limits, yield, working time, and curing.

Manufacturer's Certificates of Compliance: Certify << non-shrink cementitious grout; and  Insert Other Products Here>> meet or exceed <<ASTM C1107/C1107M>><< and Insert Other Specified Requirements Here; or  None - N/A>>.

Mix Designs: Submit proposed mix design, historical test data or trial batch test data << for each class of site-mixed Portland-cement grout; or  None - N/A>> to LANL for review prior to commencement of Work.

      - ***************************************************************************************

      - Use ACI 301 guidelines for cosmetic or nonstructural surface repairs. Select repair materials specified in ACI 301 or listed in this Section. If using materials from this Section, be aware that the repaired surface may not visually match the existing in-situ concrete.

      - For structural repairs, submit a detailed repair procedure/specification through Specification Section << 03 3001 - Reinforced Concrete>>, Table A1 – Design Change(s). The submittal must include the following:

        - Description of the damage and extent of deterioration.

        - Scope/Applicability: Define applicable repair types (e.g., deep honeycomb, shallow-to-medium patches). Demolition and removal procedures, Surface preparation method(s), Placement method (e.g., form-and-pour, shotcrete, hand patching).

        - Application Type: Specify whether the repair is formed or unformed.

        - Approved Repair Materials: List all approved materials for each repair type.

        - Temperature Limits: State acceptable temperature ranges for material placement.

        - Placement Notes: Include specific instructions for material handling and placement.

        - Curing Requirements: Detail curing methods and durations.

        - QA Acceptance Criteria: Define measurable quality standards, criteria and or requirements for acceptance of completed repairs. Include an inspection and testing plan to verify compliance.

        - Required Hold Points: Identify inspection and approval stages before proceeding.

        - Schedule and sequencing of the repair work.

        - Engineering justification for the proposed method, if deviating from original design intent.

      - Refer to the following documents for additional guidance on large structural concrete repairs:

        - ICRI 030130 Guide specifications structural concrete repair

        - UFGS 03 0100 – Rehabilitation of Concrete

        - RIB 03 0100 – Maintenance of Concrete

        - ACI SPEC-563 – Repair of Concrete in Buildings—Specification

        - Five Star Design-a-Spec – Structural Concrete

        - ACI 548.15 – Specification for Crack Repair by Epoxy Injection

        - ACI 546.3R Guide for the Selection of Materials for the Repair of Concrete

        - ACI PRC-546 Concrete Repair—Guide

        - ACI Field Guide to Concrete Repair Application Procedures and the videos at ACI Repair Application Procedures and Case Studies

      - ***************************************************************************************

Concrete Structural-Repair Procedures: Include detailed repair locations (e.g., annotated photos or drawing markups), << repair methods (preparation, placement);  equipment;  materials;  required hold points; and  QA acceptance criteria>> to be used for each repair type.

      - ***************************************************************************************

      - Retain the “inspections option” in the Field-QC paragraph below if this option is also to be retained in the Field-QC article in PART 3.

      - ***************************************************************************************

Field Quality-Control Results: Submit results of Subcontractor-furnished tests​​​<< and inspections; or  None - N/A>>​​​.

Sustainable Design Submittals

Manufacturer's Certificate: Certify products meet or exceed specified sustainable design requirements related to recycled content and point of origin of materials.

          - **********************************************************************

          - Edit material certifications list to suit products specified in this Section and Project sustainable design requirements.

          - If both sustainability requirements shown here are determined to be cost-prohibitive to the project, omit SUSTAINABILITY DESIGN SUBMITTALS.

          - **********************************************************************

Materials Resources Certificates:

Certify recycled material content for recycled content products.

Certify source for regional materials and distance from Project site.

QUALITY ASSURANCE

      - ***************************************************************************************

      - Use this article to specify compliance with overall reference standards affecting all products and installation included in this Section.

      - ***************************************************************************************

The work shall be subject to inspection at all times by LANL and, if applicable, LANL’s Independent Testing Agency for the purpose of determining that the work is properly executed in accordance with this Section. Failure to detect defective workmanship or material during any interim inspection shall not constitute acceptance of workmanship and materials.

      - ***************************************************************************************

      - Include the following paragraph if Site-Mixed Portland Cement Grout is used by the project.

      - ***************************************************************************************

Site-Mixed Portland Cement Grout: Acquire all materials from same source as used to produce the specific mix design for all work. Formally notify LANL of any material source changes prior to grout placement including the test agency test documentation. The Subcontractor must provide LANL a certificate of conformance prior to the initial placement that confirms the source of the constituents, that tests confirm compliance, and that these sources are the same for the mix design testing and the placed mix.

      - ***************************************************************************************

      - Include the following paragraph if required by the project.

      - ***************************************************************************************

Mockup: ​​<< provide dimensions>>​​ to evaluate mixing, head-box placement, form tightness, finish, and curing.

DELIVERY, STORAGE, AND HANDLING

Section << 01 6000 - Product Requirements>>​: Requirements for transporting, handling, storing, and protecting products.

Deliver pre-mixed, pre-packaged material in manufacturer's unopened containers with proper labels intact.

Store all materials in a dry shelter, protected from moisture and, for pre-mixed, pre-packaged material, maintained at a temperature and humidity as required by manufacturer(s)

Do not use material stored beyond the shelf life recommended by the manufacturer(s).

FIELD CONDITIONS

Refer to Section << 01 6000 - Product Requirements>>: Environmental conditions affecting products on site.

For pre-mixed, pre-packaged material, do not perform installation if ambient temperature exceeds that which is specified by manufacturer(s). In the case of non-prepackaged, Portland cement grout, comply with <<ACI SPEC-301>> <<ACI 301>>​.

For pre-mixed, pre-packaged material, maintain minimum temperature specified by manufacturer before, during, and after installation, until material has set. In the case of site-mixed Portland cement grout, comply with <<ACI SPEC-301>>​.

PART 2 - PRODUCTS

GENERAL

      - ***************************************************************************************

      - The prohibition in the following paragraph is due to non-shrink grouts being designed for use in confined conditions, where their expansive properties are controlled. When placed in unconfined conditions, as in some concrete repairs, they can cause cracking, thermal expansion mismatches with concrete, and other related issues.

      - ***************************************************************************************

Do not use rapid-curing epoxy grout or non-shrink cementitious grout for concrete repair.

      - ***************************************************************************************

      - Retain the following paragraphs for concrete repair materials, portland cement grout, and non-shrink cementitious grout.

      - ***************************************************************************************

Limit water-soluble chloride ion content to a maximum of 0.05 percent by mass of cementitious material in accordance with <<ASTM C1218/C1218M>>, unless otherwise approved by the EOR.

Select bonding agents, primers, and curing materials that are compatible with the grout or repair products and the substrate.

      - ***************************************************************************************

      - Edit sustainable design requirements to suit content of this Section and Project sustainable design requirements.

      - If both sustainability requirements shown here are determined to be grossly prohibitive to the project, omit Article SUSTAINABILITY CHARACTERISTICS.

      - ***************************************************************************************

SUSTAINABILITY CHARACTERISTICS

Materials and Resources Characteristics:

        - ******************************************************************************

        - It must be noted that the nature of grout materials may limit the achievable recycled content. Retain this subparagraph to encourage selection of manufacturers that can provide higher recycled content while meeting performance requirements. If grout with acceptable high recycled content is not available and compliant with design requirements, omit this subparagraph.

        - ******************************************************************************

Recycled Content Materials: Furnish manufacturers certification of production with maximum available recycled content​<< including:; or  .>>​

          - **********************************************************************

          - List materials specified in this section required to have recycled content.

          - **********************************************************************

<< _______>>.

        - ******************************************************************************

        - Specifier Note: Many grout manufacturers may not be local to LANL. Retain this requirement to encourage selection of manufacturers that can provide regional materials. If this requirement is not consistent with the Project sustainability criteria, omit this subparagraph.

        - ******************************************************************************

Regional Materials: Furnish materials extracted, processed, and manufactured within 500 miles of Project site​<< including:; or  .>>​

          - **********************************************************************

          - List materials specified in this section required to have recycled content.

          - **********************************************************************

​<< _______>>​.

      - ***************************************************************************************

      - The following four (4) Articles are designer-choice based on project-specific requirements. Retain those which apply.

      - ***************************************************************************************

CONCRETE REPAIR MATERIAL

      - ***************************************************************************************

      - Either retain the following “Manufacturer” paragraph, or the descriptive specifications and Properties paragraphs— do not include both.

      - If retaining the Manufacturer paragraph, keep the first product option for horizontal repairs, and keep the second option for vertical or overhead (V/O) repairs. Refer to the following links for product data: Five Star Structural Concrete, Structural Concrete V/O, Structural Concrete ES, SIKA SikaEmaco S 466 and S -488CL.

      - ***************************************************************************************

Manufacturer:

Five Star Products, Inc.: ​​​<< Structural Concrete;  Structural Concrete V/O;  Structural Concrete ES; and  _______>>​​​.

SIKA SikaEmaco: << S 466;  S 488CI; and  _______>>.

        - ******************************************************************************

        - Add other products as required. Ensure added products meet the requirements of the Properties paragraphs below.

        - ******************************************************************************

​<< _______>>​

        - ******************************************************************************

        - Include the following subparagraph only if strictly necessary. In General, use an FCR to request alternate grouting products.

        - ******************************************************************************

Substitutions: ​​​​​<< Alternate products may be accepted; follow Section 01 2500 - Substitution Procedures; or  Not Permitted – No Substitutions>>​​​​​.

      - ***************************************************************************************

      - Choose between the above paragraph OR the following two paragraphs. The products listed in the paragraph above meet the descriptive specifications and properties outlined in the two following paragraphs. If a different product is selected, the author must ensure no conflicts exist with these paragraphs

      - ***************************************************************************************

Concrete Repair Material: Blended, packaged cement-based mortar requiring only the addition of potable water. The material shall not contain any chlorides or lime other than amounts contained within the hydraulic cement composition, and it shall be dimensionally stable (i.e., “shrinkage-compensated”).

Properties: Certified to meet the following minimum properties when tested in accordance with the respective indicated ASTM standard:

      - ***************************************************************************************

      - Edit the options in the following table in accordance with project requirements.

      - Regarding the tabulated default values, the 1st option pertains to material not used for overhead or vertical repairs, and the 2nd option pertains to material that is used for overhead and/or vertical repairs. If both of the aforementioned repair types are applicable, then edit Result column of table accordingly. For example, in the Compressive Strength row, the result would include both of the following statements:

      - 6,000 psi min. at 7days for horizontal repairs

      - 4,000 psi min. at 7days for overhead/ vertical repairs

      - The reason for the range (of coulombs) in the option for chloride permeability is because ASTM C 1202 results are expressed this way (ref. Table X1.1 therein). Per Table X1.1, a result of 100 – 1,000 coulombs is, qualitatively, “Very Low.”

      - ***************************************************************************************

| ​ Property | ​ Test | ​ Result |
| --- | --- | --- |
| Compressive Strength | <<ASTM C109/C109M>> (Field-QC test)* | ​​​​​​​​​<< 4,000; 5000; 6,000; or ______>>​​​​​​​​​ psi minimum at 7 days* |
| Bond Strength | <<ASTM C882/C882M>> | ​​​​​​​​​<< 2,150; 2,200; or ______>>​​​​​​​​​ psi minimum at 7 days |
| Length Change/Drying Shrinkage | <<ASTM C157/C157M>> | ​​​​​​​​​<< -0.09; -0.13; or ______>>​​​​​​​​​% maximum at 28 days |
| Freeze/Thaw Resistance | <<ASTM C666>> Procedure A | ​​​​​​​​​​​<< 90; 95; or ______>>​​​​​​​​​​​% minimum at 300 cycles |
| Chloride Permeability | <<ASTM C1202>> | ​​​​​​​​​​​<< 100–1,000; or ______>>​​​​​​​​​​​​ coulombs maximum at 28 days |

      - *Compliance shall be proven via the field-quality-control testing indicated in Part 3 Herein.

PORTLAND CEMENT GROUT MATERIALS

Portland cement: <<ASTM C150/C150M>>, Type I and II.

Water

Potable; containing no impurities, suspended particles, algae or dissolved natural salts in quantities capable of causing:

Corrosion of steel.

Volume change increasing shrinkage cracking.

Efflorescence.

Excess air entraining.

      - ***************************************************************************************

      - Grout used for large-volume placements filling spaces greater than 3 in. should include coarse aggregate (CA). Refer to Five Star Products’ A Professional’s Handbook on Grouting and Concrete Repair for details.

      - This section excludes CA for the following reasons: large-volume, deep pours are uncommon; adding CA may increase the risk of alkali-silica reaction (ASR); and mixture proportions are not prescriptive (e.g., x part cement, y part sand, z part CA).

      - If a deep pour is necessary, prior to proceeding, contact Engineering Standards Manual Structural POC.

      - ***************************************************************************************

Fine Aggregate

Washed natural sand.

Gradation in accordance with <<ASTM C33/C33M>>​ and represented by smooth granulometric curve within required limits.

Free from injurious amounts of organic impurities as determined by<<ASTM C40>>.

Mix

Portland cement, sand and water. Do not use ferrous aggregate or staining ingredients in grout mixes.

      - ***************************************************************************************

      - Epoxy grout is typically used for grouting base plates, machinery, equipment, etc.; and when dynamic/impact loading, vibration, or chemical attack is/are applicable. It’s ideal for applications where precise change in elevation during curing is required. Additionally, epoxy grout can be tailored to provide improved properties related to: high early strength, and high chemical, acid, and fatigue resistance. Refer to the following links for product data: Five Star® HP Epoxy Grout, SikaFlow®-648, Epoxy Grout J55.

      - ***************************************************************************************

RAPID-CURING EPOXY GROUT

      - ***************************************************************************************

      - The products listed in the following paragraph meet the descriptive specifications and properties outlined in the two subsequent paragraphs.

      - Either retain the “Manufacturer” paragraph or retain the descriptive specifications and Performance Criteria paragraphs. Do not include both.

      - ***************************************************************************************

Manufacturers

Five Star Products, Inc.: << Five Star HP Epoxy Grout;  _______; or  None - N/A>>

Dayton Superior: << Epoxy Grout J55;  _______; or  None - N/A>>

SIKA: << SikaFlow 648;  ___; or  None - N/A>>

        - ******************************************************************************

        - Add other products as required. Ensure added products meet the requirements of the Properties paragraphs below.

        - ******************************************************************************

​<< _______>>​

        - ******************************************************************************

        - Include the following subparagraph only if strictly necessary. In General, use an FCR to request alternate grouting products.

        - ******************************************************************************

Substitutions: ​​​​<< Alternate products may be accepted; follow Section 01 2500 - Substitution Procedures; or  Not Permitted – No Substitutions>>​​​​.

      - ***************************************************************************************

      - Choose between the above paragraph OR the following two paragraphs

      - Edit the following descriptive specifications to identify project requirements and to eliminate any/all conflicts with Properties indicated subsequently.

      - ***************************************************************************************

Rapid-Curing Epoxy Grout: Provide a precision, high-strength, minimal-shrinkage, 100 percent solids, three-component epoxy grout. The material shall be rapid-curing, exhibit low creep, provide a high effective bearing area, and offer high resistance to vibration and chemicals.

Properties: Certified to meet the following minimum properties when tested in accordance with the respective ASTM standard:

      - ***************************************************************************************

      - Edit the options in the following table in accordance with project requirements. Ensure the “C579” Procedure used here is mirrored in the Epoxy-Grout paragraph in PART 3 Article FIELD QUALITY CONTROL.

      - The default value of f’c, in the following table, represents the lowest strength reported by all manufacturers considered. This approach is used because f’c may be reported for different consistencies (e.g., flowable/standard and fluid/high flow), and the names or number of consistencies can vary among manufacturers.

      - ***************************************************************************************

| ​ Property | ​ Test | ​ Result |
| --- | --- | --- |
| Compressive Strength | <<ASTM C579>> ​​​​<< Procedure B; or None - N/A>>​​​​ (Field-QC test)* | ​​​​​<< 12,000; or ______>>​​​​​ psi minimum at 7 days* |
| Tensile Strength | <<ASTM C307>> | ​​​​​<< 2,000; or ______>>​​​​​ psi minimum |
| Coefficient of Expansion | <<ASTM C531>> | ​​​​​<< 30E-6; or ______>>​​​​​ maximum per degree F |

      - *Compliance shall be proven via the field-quality-control testing indicated in PART 3 herein.

      - ***************************************************************************************

      - Non-shrink cementitious grout is typically used for grouting base plates, machinery, equipment, etc. While non-shrink cementitious grout is typically less resistant to chemical attack and fatigue than epoxy grout, it tends to be more resistant to heat and less expensive. It is also more “precise” than a Portland cement grout, especially one that requires measurement of dry constituents.

      - ***************************************************************************************

NON-SHRINK CEMENTITIOUS GROUT

      - ***************************************************************************************

      - The products listed in paragraph below meet the descriptive specifications and the Properties in the two subsequent paragraphs. For additional details refer to Five Star® Grout, QUIKRETE: Non-shrink Precision Grout.

      - Either retain the “Manufacturer paragraph” or the descriptive specifications and Properties Paragraphs. Do not include both.

      - ***************************************************************************************

Manufacturers (listed in descending order of precision/performance):

Five Star Products, Inc.: << Five Star Grout;  _______; or  None - N/A>>​

QUIKRETE: << Non-shrink Precision Grout;  _______; or  None - N/A>>​

        - ******************************************************************************

        - Add other products as required. Ensure added products meet the requirements of the Properties paragraphs below.

        - ******************************************************************************

​<< _______>>​

        - ******************************************************************************

        - Include the following subparagraph only if strictly necessary. In General, use an FCR to request alternate grouting products.

        - ******************************************************************************

Substitutions: ​​​<< Alternate products may be accepted; follow Section 01 2500 - Substitution Procedures; or  Not Permitted – No Substitutions>>​​​.

      - ***************************************************************************************

      - Choose between the above paragraph OR the following two paragraphs

      - Edit the following descriptive specifications to identify project requirements and to eliminate any/all conflicts with Properties indicated subsequently.

      - ***************************************************************************************

Non-shrink Cementitious Grout: Pre-mixed, ready-for-use formulation requiring only addition of water; non-shrink, non-corrosive, non-metallic, non-gas forming, no chlorides.

Properties: Certified to maintain initial placement volume or expand after set, and to meet the following minimum properties when tested in accordance with the respective indicated ASTM standard:

      - ***************************************************************************************

      - Edit the options in the following table in accordance with project requirements.

      - Regarding the tabulated default values of f’c, they are the lowest strengths that all the manufacturers considered report (i.e., for grout that is fluid/contains max. amount of water). The reason being, f’c is typically reported for multiple consistencies (i.e., plastic, flowable and fluid), and the number and /or names of the consistencies can vary from manufacturer to manufacturer.

      - ***************************************************************************************

| ​ Property | ​ Test | ​ Time | ​ Result |
| --- | --- | --- | --- |
| Early Height Change | <<ASTM C827/C827M>> |  | ​​​​​​​​​​​​​<< +4.0%; or ______>>​​​​​​​​​​​​​ maximum |
| Hardened Height Change | <<ASTM C1090>> |  | ​​​​​​​​​​​​​<< 0%; or ______>>​​​​​​​​​​​​​ minimum ​​​​​​​​​​​​​<< +0.3%; or ______>>​​​​​​​​​​​​​ maximum |
| Compressive Strength* | <<ASTM C109/C109M>> (as modified by <<ASTM C1107/C1107M>>, or as indicated in<<ASTM C942>>) (Field-QC test)* | 1 day | ​​​​​​​​​​​​​<< 2,000; or ______>>​​​​​​​​​​​​​ psi minimum |
|  |  | 7 days | ​​​​​​​​​​​​​<< 5,000; or ______>>​​​​​​​​​​​​​ psi minimum |
|  |  | 28 days | ​​​​​​​​​​​​​<< 6,500; or ______>>​​​​​​​​​​​​​ psi minimum* |

      - *Compliance shall be proven via the field-quality-control testing indicated in PART 3 herein.

FORMWORK

      - ***************************************************************************************

      - Retain the following paragraph for concrete repair materials, rapid curing epoxy grout, and non-shrink cementitious grout.

      - ***************************************************************************************

Follow all recommendations pertaining to formwork material and accessories made by the manufacturer(s) of the pre-mixed, pre-packaged concrete-repair and/or grout material(s) to be used.

      - ***************************************************************************************

      - Retain the following paragraph for Portland cement grout and in most situations.

      - ***************************************************************************************

<< Where there is no conflict with the preceding formwork provision, as well as for site-mixed Portland cement grout,;  Where there is no conflict with the preceding formwork provision, ; or  For site-mixed Portland cement grout,>> Provide formwork in accordance with the Article FORM MATERIALS AND ACCESSORIES in PART 2 of Section << 03 3001 - Reinforced Concrete>>.

PART 3 - EXECUTION

EXAMINATION

Verify that areas to receive material are clean and properly prepared, including verification of alignment, elevations, and clearances prior to repair or grouting.

Do not proceed until unsatisfactory conditions are corrected.

GENERAL

      - ***************************************************************************************

      - Include the following paragraph if applicable to the project.

      - ***************************************************************************************

If structural concrete repair is included in the scope of work, obtain LBO approval of the repair scheme or plan. Perform all repair work in accordance with the approved plan.

      - ***************************************************************************************

      - For general guidance on mixing, placement/installation, and testing, refer to the following Five Star instructional videos, as well as the Five Star Installation Checklists for Concrete Installation/Repair, and for Epoxy and Cementitious Grouting. In most grout and concrete repair projects, preparation is the most critical step. Typically, 90–95% of the effort involves surface preparation, equipment selection, and the installation and fabrication of forms, while only 5–10% is dedicated to material application or placement.

      - ***************************************************************************************

Verify that all required personnel, training, materials, tools, equipment, personal protective equipment (PPE), manufacturer’s installation instructions/recommendations, and Safety Data Sheets (SDS/MSDS) are available and ready at each stage of the work.

Align, level, and maintain final positioning of components to be repaired/grouted.

      - ***************************************************************************************

      - Depending on the complexity of the repair or grouting work, include the following paragraph to ensure proper planning and execution.

      - ***************************************************************************************

Prior to starting grout or repair installation, conduct a preconstruction meeting to address ​<< site safety;  training;  means and methods;  materials;  finishing requirements;  Methods of curing and time required for curing;  testing; and  ______>>​ necessary to achieve the grouting or repair objectives.

SURFACE PREPARATION

      - ***************************************************************************************

      - Proper preparation—especially surface preparation—is critical for the successful installation of grouts and concrete repair materials. Therefore, field inspection of this step is essential to ensure the performance and quality of the work. Refer to the figure below, this link and video for a quick visual guide to Concrete Surface Profile (CSP). Typically, visual inspection and touch are sufficient to verify proper surface preparation. Alternatively, refer to the following video for information on digitally measuring surface profiles.

      - Source: Concrete Surface Prep Part 3: Grades of Roughness

      - ***************************************************************************************

Follow all surface preparation recommendation provided by the manufacturer(s) of the pre-mixed, pre-packaged material for the intended application or use.

Remove foreign materials from metal surfaces in contact with material.

Maintain moisture and temperature within the limits specified by the manufacturer(s) of the pre-mixed, pre-packaged material to be used.

Install bonding agent in accordance with the manufacturer’s instructions, if required.

      - ***************************************************************************************

      - Retain the following paragraph for site-mixed portland cement grout.

      - ***************************************************************************************

For site-mixed Portland cement grout only, in addition to the preceding Paragraphs, the following shall be done (as applicable)

Remove defective concrete, laitance, dirt, oil, grease and other foreign material from concrete surfaces by brushing, hammering, chipping or other similar means until sound, clean concrete surface is achieved.

Roughen concrete lightly, but not enough to interfere with placement of grout. Meet <<ICRI 310.2R>>​ CSP 3–5.

Saturate concrete surfaces with clean water; remove excess water, leave none standing.

INSTALLATION

Formwork

        - ******************************************************************************

        - Retain the following subparagraph for concrete repair materials, rapid curing epoxy grout, and non-shrink cementitious grout.

        - ******************************************************************************

Follow all manufacturer recommendations for formwork installation for the of the pre-mixed, pre-packaged concrete-repair and/or grout material(s) to be used.

        - ******************************************************************************

        - Retain the following subparagraph in most situations and select the option applicable to your project from the three choices provided in the field below.

        - ******************************************************************************

<< Where there is no conflict with the preceding formwork provision, as well as for site-mixed Portland cement grout,;  Where there is no conflict with the preceding formwork provision, ; or  For site-mixed Portland cement grout,>>​​ provide formwork as follows:

Construct to be leak-proof, and anchor and shore to resist material pressures.

Install with sufficient clearance to allow proper material placement.

Coat with approved form release agents.

Comply with the requirements specified in the Article General in PART 3 of Section << 03 3001 - Reinforced Concrete>>.

Mixing

        - ******************************************************************************

        - For general recommendations on mixing and placement, refer to the following Five Star instructional videos Precision Cementitious Grout Mixing, Precision Epoxy Grout Mixing, Concrete Repair Mixing.

        - ******************************************************************************

Follow all manufacturer recommendations for mixing of the pre-mixed, pre-packaged material to be used. Use only mixers approved by the material manufacturer, and measure all components accurately.

        - ******************************************************************************

        - Some manufacturers of pre-mixed, pre-packaged cementitious repair materials and grouts recommend extending the product with coarse aggregate (CA) under certain conditions (e.g., large-volume placements several inches deep). For additional guidance, see the product Technical Data Sheets (TDS) and Five Star Products’ A Professional’s Handbook on Grouting and Concrete Repair.

        - However, extending is not permitted without prior approval from LANL for the following reasons:

          - Large-volume, deep placements are uncommon.

          - The addition of CA introduces the potential for alkali-silica reaction (ASR).

          - The use of CA may interfere with field quality control, since the 2-inch test cubes specified in ASTM C109 do not include aggregate.

        - ******************************************************************************

If the work requires extending pre-mixed, pre-packaged material with aggregate, and the manufacturer permits it, obtain written approval from LANL STR before proceeding.

        - ******************************************************************************

        - Retain the following subparagraph for site-mixed portland cement grout.

        - ******************************************************************************

For site-mixed Portland cement grout only, perform the following:

Use proportions as determined by mix design.

Prepare grout with water to obtain consistency to permit placing and packing.

Mix water and grout in two steps

Pre-mix using approximately 2/3 of water.

After partial mixing, add remaining water to bring mix to desired placement consistency and continue mixing two (2) to three (3) minutes.

Mix only quantities of grout capable of being placed within 30 minutes after mixing. Mix with properly sized and powered mechanical mixers.

Do not add additional water after grout has been mixed.

f’c per  <<ASTM C109/C109M>> (Field-QC test)*: << 2,400; or  _______>> psi minimum in 48 hours, and << 7,000; or  _______>> psi minimum in 28 days*.

          - * Compliance shall be proven via the field-quality-control testing indicated subsequently herein.

Mix material near the work area and transport it promptly in a manner that prevents segregation.

Placing

        - ******************************************************************************

        - Retain the following subparagraph for concrete repair materials, rapid curing epoxy grout, and non-shrink cementitious grout.

        - ******************************************************************************

Place pre-mixed, pre-packaged material in accordance with the manufacturer’s installation instructions and recommendations. Do not use material that has begun to set or that has exceeded the manufacturer’s recommended working time.

        - ******************************************************************************

        - Retain the following subparagraph in most situations and select the option applicable to your project from the three choices provided in the field below.

        - ******************************************************************************

<< Where there is no conflict with the preceding placing provision, as well as for site-mixed Portland cement grout,;  Where there is no conflict with the preceding placing provision,; or  For site-mixed Portland cement grout,>> develop a grouting plan addressing material placement, finishing and include the following:

Provisions to eliminate of the possibility of entrapping air.

          - NOTE: This is typically achieved for grouted base plates by providing an additional hole(s) in the plate that allows for an air path for the air to escape during grouting operations.

Provisions to ensure placement of material quickly and continuously.

Where leveling shims are to be removed after grouting they shall be coated/wrapped with a bond breaker (e.g., paste wax, polyethylene film, etc.), and removal shall occur no sooner than 48 hours after grout has been placed.

          - NOTE: Leveling jack screws may be used in lieu of leveling shims that are to be removed.

        - ******************************************************************************

        - The following is a designer-choice.

        - ******************************************************************************

Obtain LBO approval of grouting plan, and then place material in accordance with the plan.

Do not place material using of pneumatic-pressure or dry-packing methods.

Do not vibrate placed material, and do not place material when the area is subject to vibration from nearby equipment.

Curing

        - ******************************************************************************

        - Retain the following subparagraph for concrete repair materials, rapid curing epoxy grout, and non-shrink cementitious grout.

        - ******************************************************************************

Follow all curing recommendations provided by the manufacturer(s) of the pre-mixed, pre-packaged material.

        - ******************************************************************************

        - Retain the following subparagraph in most situations involving cementitious material and select the option applicable to your project from the three choices provided in the field below.

        - ******************************************************************************

​​<< Where there is no conflict with the preceding curing provision, as well as for site-mixed Portland cement grout,;  Where there is no conflict with the preceding curing provision,; or  For site-mixed Portland cement grout,>>​​ curing of cementitious materials shall include the following:

Prevent rapid loss of water from material during first 48 hours by use of approved membrane curing compound or by using of wet burlap method.

After the material has attained its initial set, keep it continuously damp for a minimum of three (3) days.

Immediately after placement, protect material from premature drying, excessively hot or cold temperatures, and mechanical damage.

FIELD QUALITY CONTROL

Provide a certified testing agency to perform field testing in accordance with <<ACI SPEC-301>> and under provisions of Section << 01 4000 - Quality Requirements - Non-Nuclear>>.

      - ***************************************************************************************

      - Proper preparation—especially surface preparation—is critical for the successful installation of grouts and concrete repair materials. Therefore, field inspection of this step is essential to ensure the performance and quality of the work. Refer to the figure below, this link and video for a quick visual guide to Concrete Surface Profile (CSP). Typically, visual inspection and touch are sufficient to verify proper surface preparation. Alternatively, refer to the following video for information on digitally measuring surface profiles.

      - Source: Concrete Surface Prep Part 3: Grades of Roughness

      - ***************************************************************************************

Verify that ​<< concrete; and  metal>>​ surface profile and preparation meets specified requirements. ​<< Document final surface using photos or other appropriate methods.; or  None - N/A>>​

      - ***************************************************************************************

      - Five Star Products’ A Professional’s Handbook on Grouting and Concrete Repair notes that ASTM C579 includes three different test procedures (i.e., Procedures A–C), and that the results from these methods can vary by as much as 2,000 psi. Accordingly, the following epoxy-grout paragraph provides flexibility in demonstrating that the f’c value specified in Part 2 is met or exceeded.

      - The default procedure is Procedure B, as indicated in Part 2. If a different procedure is selected, ensure that the one referenced here matches the procedure applicable to the 7-day f’c value specified in Part 2.

      - Except for the above option, the wording in the next two paragraphs has been adapted from ACI 301-16/20, Section 13.1.4.4(c).

      - ***************************************************************************************

Rapid-Curing Epoxy grout: Determine f’c per <<ASTM C579>>  << Procedure B; or  None - N/A>>. The test result shall be considered satisfactory if 7-day f’c value meets or exceeds that which is indicated herein.

      - ***************************************************************************************

      - Select the cementitious material(s) applicable to your project from the three options provided in the choice field below.

      - ***************************************************************************************

​<< Concrete Repair Material;  Non-Shrink Cementitious Grout; and  Portland Cement Grout>>​: Determine f’c per <<ASTM C109/C109M>>. The test result shall be considered satisfactory if the 28-day f’c value meets or exceeds that which is indicated herein.

      - ***************************************************************************************

      - Testing of concrete repair material is required for structural repairs but not for cosmetic/surface repairs.Per ACI 301-20, 5.2.1.6 Surface Repair Materials — "Unless otherwise specified, use repair mortar for surface defects. For exposed concrete, repair mortar shall match the color of the adjacent concrete." For additional details refer to ACI 301-20 Section 5.3.7 Repair of surface defects . Use ACI 301 guidelines for cosmetic or nonstructural surface repairs. Select repair materials specified in ACI 301 or listed in this Section. If using materials from this Section, be aware that the repaired surface may not visually match the existing in-situ concrete.

      - ***************************************************************************************

Prepare and test 2-inch cube samples for each material used, each day it is installed. Use test results to verify that the applicable material strength specified in Part 2 has been achieved prior to final acceptance of the work. The number of samples to be prepared and tested daily shall be as follows:

        - ******************************************************************************

        - Select the material(s) applicable to your project from the three options provided in the choice field below.

        - ******************************************************************************

<< Concrete Repair Material; and  Portland Cement Grout>>: Two (2) samples per installed material.

Rapid-Curing Epoxy Grout: Two (2) samples per batch consistency (i.e., fluid, flowable, or plastic) used in the installation.

Non-Shrink Cementitious Grout: Two (2) samples per batch consistency (i.e., fluid or flowable) used in the installation.

      - ***************************************************************************************

      - Edit the following acceptance criteria paragraph to meet the specific project and product requirements. For instance in the case of repair materials the following is typical:

      - Nonstructural repairs—Sound the patch 7 days after repair. If no solid ring, investigate and rework as required.

      - Small structural repairs—Sound the patch 7 days after repair. If no solid ring, perform NDT (UPV/impact-echo) to locate voids in larger areas and rework as required.

      - For large structural repairs, require the development and submittal of a detailed repair procedure/specification. Refer to the ACTION SUBMITTALS article for specific requirements and guidance on this matter.

      - ***************************************************************************************

Acceptance Criteria:

Meet or exceed specified ​​<< compressive strength;  dimensional stability; and  concrete surface profile (CSP)>>​​.

No voids under plates or at grout-to-concrete interfaces.<< Ensure at least 95% contact area after set, with no voids larger than 2 in².; or  None - N/A>> Verify the absence of voids under plates and at grout-to-concrete interfaces by sounding << or; or  and>> non-destructive testing (NDT) << seven (7)>>  days after placement<< , or as directed by the EOR; or  None - N/A>>.

Unless otherwise specified, comply with construction tolerances as defined in <<ACI SPEC-117>>.

Finished Elevations: Within << ±1/16;  ±1/8; or  _______>>​ inch of required plane.

END OF SECTION

    - **********************************************************************************************

      - Do not omit  the following reference information:

    - **********************************************************************************************

  - THE FOLLOWING STATEMENT IS FOR LANL USE ONLY

THIS PROJECT SPECIFICATION SECTION IS BASED ON LANL MASTER SPECIFICATION SECTION 03 6000, REV. 5, DATED APRIL 15, 2026.