Section 07 1326 
Self-Adhering Sheet Waterproofing

  - *************************************************************************************************************

    - lANL MASTER SPECIFICATION SECTION

Rev. 3 Summary of Changes: Edited and updated as required for import into SpecLink.

      - NOTE TO SPECIFIER ON USAGE IN SPECLINK: Activate the Section by turning on Seq #0000, followed by activating paragraphs in PART 1, Article SECTION INCLUDES. This will activate related articles, paras/subparas in the rest of the Section (i.e., SECTION INCLUDES in PART 1 activates articles and paras/subparas in PARTS 2 and 3). If there are choice fields to edit the entire Section (typically in this first author note or beginning of the Section), make selections at those locations, which will filter through the remaining Section. All Articles, paragraphs and subparagraphs must be activated sequentially from top to bottom, unless noted otherwise.

      - This template must be edited for each project. In doing so, Specifier must add job-specific requirements. Selections and choice fields are used to indicate designer choices or locations where text must be supplied by the designer. The section must also be edited to remove requirements for processes, items, or designs that are not included in the project.

      - To seek a variance from applicable requirements in this Section, contact the Engineering Standards Manual (ESM) Architectural POC  (LANL access only). Please contact POC with suggestions for improvement as well. LANL personnel should submit here: Suggested Change or Request Clarification; subcontractors via email to engstandards@lanl.gov.

      - When assembling a specification package, include applicable specification sections from all Divisions, especially Division 1, General Requirements.

      - Section is developed for ML-4 projects. For ML-1, 2, and 3 applications, additional requirements and independent reviews should be added if increased confidence in procurement or execution is desired; see LANL ESM Chapter 1 - General, Section Z10 Specifications and Quality sections.

  - *************************************************************************************************************

PART 1 - GENERAL

SECTION INCLUDES

      - ***************************************************************************************

      - Select the option (nonreinforced or reinforced) for modified bituminous sheet waterproofing here; it updates the rest of the Section. Molded-sheet drainage panels and insulation are designer-choice. Retain paragraphs based on project-specific requirements.

      - ***************************************************************************************

Modified bituminous sheet waterproofing - ​​​<< Modified Bituminous Sheet; or  Modified Bituminous Sheet, Fabric Reinforced>>​​​

Molded-sheet drainage panels

Protection course

Insulation

RELATED REQUIREMENTS

Section << 01 8113.13 - Sustainable Design>>.

Section ​<< 07 2100 - Thermal Insulation>>​.

REFERENCE STANDARDS

ASTM C272/C272M - Standard Test Method for Water Absorption of Core Materials for Sandwich Constructions.

ASTM C578 - Standard Specification for Rigid, Cellular Polystyrene Thermal Insulation.

ASTM C836/C836M - Standard Specification for High Solids Content, Cold Liquid-Applied Elastomeric Waterproofing Membrane for Use with Separate Wearing Course.

ASTM D146/146M - Standard Test Methods for Sampling and Testing Bitumen-Saturated Felts and Woven Fabrics for Roofing and Waterproofing.

ASTM D412 - Standard Test Methods for Vulcanized Rubber and Thermoplastic Elastomers--Tension.

ASTM D570 - Standard Test Method for Water Absorption of Plastics.

ASTM D1621 - Standard Test Method for Compressive Properties of Rigid Cellular Plastics.

ASTM D1970/D1970M - Standard Specification for Self-Adhering Polymer Modified Bituminous Sheet Materials Used as Steep Roofing Underlayment for Ice Dam Protection.

ASTM D4258 - Standard Practice for Surface Cleaning Concrete for Coating.

ASTM D5385/D5385M - Standard Test Method for Hydrostatic Pressure Resistance of Waterproofing Membranes.

ASTM D6135 - Standard Practice for Application of Self-Adhering Modified Bituminous Waterproofing.

ASTM D6506/D6506M - Standard Specification for Asphalt Based Protection Board for Below-Grade Waterproofing.

ASTM E96/E96M - Standard Test Methods for Gravimetric Determination of Water Vapor Transmission Rate of Materials.

ASTM E154/E154M - Standard Test Methods for Water Vapor Retarders Used in Contact with Earth Under Concrete Slabs, on Walls, or as Ground Cover.

NRCA (WM) - The NRCA Waterproofing Manual.

      - ***************************************************************************************

      - Edit submittals to include only those absolutely necessary to assure requirements and features that are important for the specific project will be met.

      - ***************************************************************************************

SUBMITTALS

Action Submittals

Product Data: Include manufacturer’s written instructions for evaluating, preparing, and treating substrate, technical data, and tested physical and performance properties of waterproofing.

Shop Drawings: Show locations and extent of waterproofing. Include details for substrate joints and cracks, sheet flashings, penetrations, inside and outside corners, tie-ins with adjoining waterproofing, and other termination conditions.

        - ******************************************************************************

        - Verify these requirements below against LANL ESM Chapter 14 - Sustainable Design, Attachment 1 "Required Attribute" Column and, if applicable, the LEED prerequisites and project credits. Material content is required. This subparagraph is activated automatically based on selections made for Protection Course in PART 2, Article Auxiliary Materials, when applicable.

        - ******************************************************************************

Sustainable Design (SD) Submittals: Provide material content documentation in accordance with the requirements of this Section.​<< Submit any additional documentation for this product category, as applicable under Section  01 8113.13 - Sustainable Design with this Section's submittal.; or  None - N/A>>​

Informational Submittals

Product Test Reports: Based on evaluation of comprehensive tests performed by a qualified testing agency, for waterproofing.

        - ******************************************************************************

        - Retain the following submittal when project requires manufacturer's certificates.

        - ******************************************************************************

Manufacturer’s Certificate: Certify ​​​<< products; or  _______>>​​​ meet or exceed ​​​<< specified requirements; or  _______>>​​​.

Manufacturer’s Installation Instructions: Submit special procedures and perimeter conditions requiring special attention.

        - ******************************************************************************

        - Retain the following submittals when project requires special warranties and/or warranty documentation.

        - ******************************************************************************

Special Warranties.

At Closeout: Warranty Documentation.

QUALITY ASSURANCE

Perform work in accordance with <<NRCA (WM)>>.

Membrane Manufacturer: Company specializing in waterproofing sheet membranes with minimum three years documented experience.

Applicator: Company specializing in performing work of this Section approved by manufacturer.

      - ***************************************************************************************

      - Verify these requirements against LANL ESM Chapter 14 - Sustainable Design, Attachment 1 "Required Attribute" Column and, if applicable, the LEED prerequisites and project credits. Recovered content materials requirement must be met. This paragraph and its subparagraphs are activated automatically based on selections made for Protection Course in PART 2, Article Auxiliary Materials, when applicable.

      - ***************************************************************************************

Sustainable Design Requirements

Recovered Content Materials: Furnish material recovered content for:

Extruded/Molded-polystyrene board insulation 9 percent recovered material.

FIELD CONDITIONS

Apply waterproofing within the range of ambient and substrate temperatures recommended by waterproofing manufacturer.  Do not apply waterproofing to a damp or wet substrate.

      - ***************************************************************************************

      - Retain the following Article when project requires special warranties.

      - ***************************************************************************************

WARRANTY

Special Manufacturer’s Warranty: Manufacturer’s standard form in which manufacturer agrees to replace waterproofing material that does not comply with requirements or that fails to remain watertight within specified warranty period.

Warranty Period: Manufacturer’s standard warranty period from date of Substantial Completion.

PART 2 - PRODUCTS

MATERIALS

Modified Bituminous Sheet Waterproofing

        - ******************************************************************************

        - Retain Modified Bituminous Sheet or Modified Bituminous Sheet, Fabric Reinforced based on project-specific requirements.

        - ******************************************************************************

Modified Bituminous Sheet: Not less than 60-mil thick, self-adhering sheet consisting of rubberized asphalt laminated to a polyethylene film with release liner on adhesive side and formulated for application with primer or surface conditioner that complies with VOC limits of not more than 250 g/L.

Manufacturers and Products:

Carlisle Coatings & Waterproofing Inc.; CCW MiraDRI 860/861.

Grace, W.R. & Co.; Bituthene ​<< 3000; or  4000>>​.

Henry Company; Blueskin WP 200.

Meadows, W.R., Inc.; SealTight Mel-Rol.

Tamko Building Products, Inc.; TW-60.

Physical Properties

Tensile Strength: 250 psi minimum; <<ASTM D412>>, Die C, modified.

Ultimate Elongation; 300 percent minimum; <<ASTM D412>>, Die C, modified.

Low-Temperature Flexibility: Pass at minus 20 degrees F <<ASTM D1970/D1970M>>.

Crack Cycling: Unaffected after 100 cycles of 1/8-inch movement; <<ASTM C836/C836M>>​.

Puncture Resistance: 40 lbf minimum; <<ASTM E154/E154M>>.

Hydrostatic-Head Resistance: 150 feet minimum; <<ASTM D5385/D5385M>>.

Water Absorption: 0.15 percent weight-gain maximum after 48-hour immersion at 70 degrees F; <<ASTM D570>>.

Vapor Permeance: 0.05 perms; <<ASTM E96/E96M>>, Water Method.

Modified Bituminous Sheet, Fabric Reinforced: 60-mil- thick, self-adhering sheet consisting of rubberized-asphalt membrane embedded in spun-bonded polyester or fiberglass nonwoven fabric reinforcement laminated to a 0.05-mil thick polyester film with release liner on adhesive side.

Manufacturers and Products:

Protecto Wrap Company; Jiffy Seal 140/60

Royston Laboratories, Div. of Chase Corporation; Royal-Gard

Physical Properties

Pliability: No cracks when bent 180 degrees over a 1-inch mandrel at minus 25 degrees F; <<ASTM D146/146M>>.

Hydrostatic-Head Resistance: 150 feet minimum.

Vapor Permeance: 0.05 perms, <<ASTM E96/E96M>>, Water Method.

AUXILIARY MATERIALS

General: Furnish auxiliary materials recommended by waterproofing manufacturer for intended use and compatible with sheet waterproofing.

        - ******************************************************************************

        - Retain the following subparagraph when Modified Bituminous Sheet is selected for project.

        - ******************************************************************************

Furnish liquid-type auxiliary materials that comply with VOC limits of not more than 250 g/L.

Primer: Liquid waterborne or solvent-borne primer as recommended for substrate by manufacturer of sheet waterproofing material.

Surface Conditioner: Liquid, waterborne surface conditioner recommended for substrate by manufacturer of sheet waterproofing material.

Liquid Membrane: Elastomeric, two-component liquid, cold fluid applied, trowel grade or low viscosity.

Substrate Patching Membrane: Low-viscosity, two-component, asphalt-modified coating.

Sheet Strips: Self-adhering, rubberized-asphalt sheet strips of same material and thickness as sheet waterproofing.

Mastic, Adhesives, and Tape: Liquid mastic and adhesives, and adhesive tapes recommended by waterproofing manufacturer.

Metal Termination Bars: Aluminum bars, approximately 1 by 1/8 inch thick, predrilled at 9-inch centers.

Protection Course:

        - ******************************************************************************

        - Select one of the following subparagraphs for the protection course.

        - ******************************************************************************

Protection Course: <<ASTM D6506/D6506M>>, semi-rigid sheets of fiberglass or mineral-reinforced-asphaltic core, pressure laminated between two asphalt-saturated fibrous liners and as follows:

Thickness: 1/8 inch nominal, for vertical applications; 1/4 inch, nominal, elsewhere.

Adhesive: Rubber-based solvent type recommended by waterproofing manufacturer for type of protection course.

        - *** OR ***

Protection Course: Fan folded, with a core of extruded-polystyrene board insulation faced on << one; or  both>> side(s) with plastic film, nominal thickness 1/4 inch, with compressive strength of not less than 8 psi per <<ASTM D1621>>, and maximum water absorption by volume of 0.6 percent per <<ASTM C272/C272M>>.

        - *** OR ***

Protection Course: Unfaced, fan-folded, extruded-polystyrene board insulation, nominal thickness 1/4 inch with compressive strength of not less than 8 psi per <<ASTM D1621>>.

        - *** OR ***

Protection Course: Extruded-polystyrene board insulation, unfaced, <<ASTM C578>>, Type X, 1/2 inch thick.

        - *** OR ***

Protection Course: Molded-polystyrene board insulation, <<ASTM C578>>, Type I, 0.90-lb/cu.ft. minimum density, 1-inch minimum thickness.

      - ***************************************************************************************

      - Retain the following paragraph when molded-sheet drainage panels are in project-scope.

      - ***************************************************************************************

Molded-Sheet Drainage Panels

        - ******************************************************************************

        - Select one of the following subparagraphs for the molded-sheet drainage panels.

        - ******************************************************************************

Nonwoven-Geotextile-Faced, Molded-Sheet Drainage Panel: Manufactured composite subsurface drainage panels consisting of a nonwoven, needle-punched geotextile facing with an apparent opening size not exceeding No. 70 sieve laminated to one side with or without a polymeric film bonded to the other side of a studded, non-biodegradable, molded-plastic-sheet drainage core, with a vertical flow rate of 9 to 15 gpm per ft.

        - *** OR ***

Woven-Geotextile-Faced, Molded-Sheet Drainage Panel: Manufactured composite subsurface drainage panels consisting of a woven-geotextile facing with an apparent opening size not exceeding No. 40 sieve laminated to one side with or without a polymeric film bonded to the other side of a studded, non-biodegradable, molded-plastic-sheet drainage core, with a horizontal flow rate not less than 2.8 gpm per ft.

      - ***************************************************************************************

      - Retain the following paragraph when insulation is in project-scope.

      - ***************************************************************************************

Insulation:

Refer to Section << 07 2100 - Thermal Insulation>>.

PART 3 - EXECUTION

EXAMINATION

Verify substrate surfaces are durable; free of matter detrimental to adhesion or application of waterproofing system.

Verify items penetrating surfaces to receive waterproofing are securely installed.

Verify substrate surface slopes to drain for horizontal waterproofing applications.

PREPARATION

Clean, prepare, and treat substrates according to manufacturer’s written instructions. Provide clean, dust-free, and dry substrates for waterproofing application.

Mask off adjoining surfaces not receiving waterproofing to prevent spillage and overspray affecting other construction.

Remove grease, oil, bitumen, form-release agents, paints, curing compounds, and other penetrating contaminants or film-forming coatings from concrete.

Remove fins, ridges, mortar, and other projections and fill honeycomb, aggregate pockets, holes, and other voids.

Prepare, fill, prime, and treat joints and cracks in substrates. Remove dust and dirt from joints and cracks in accordance with <<ASTM D4258>>.

Bridge and cover ​<< isolation joints;  expansion joints;  discontinuous deck-to-wall joints; and  discontinuous deck-to-deck joints>>​ with overlapping sheet strips.

Invert and loosely lay first sheet strip over center of joint. Firmly adhere second sheet strip to first and overlap to substrate.

Corners: Prepare, prime, and treat inside and outside corners in accordance with <<ASTM D6135>>.

Prepare, treat, and seal vertical and horizontal surfaces at terminations and penetrations through waterproofing and at drains and protrusions in accordance with <<ASTM D6135>>.

MODIFIED BITUMINOUS SHEET WATERPROOFING APPLICATION

Install modified bituminous sheets per waterproofing manufacturer’s written instructions and according to recommendations in <<ASTM D6135>>.

Apply primer to substrates at required rate and allow to dry. Limit priming to areas that will be covered by sheet waterproofing in same day. Reprime areas exposed for more than 24 hours.

Apply and firmly adhere sheets over area to receive waterproofing. Accurately align sheets and maintain uniform 2-1/2-inch minimum lap widths and end laps. Overlap and seal seams and stagger end laps to ensure watertight installation.

Horizontal Application: Apply sheets from low point to high point of decks to ensure that side laps shed water.

Apply continuous sheets over sheet strips bridging substrate cracks, construction, and contraction joints.

Seal exposed edges of sheets at terminations not concealed by metal counterflashings or ending in reglets with mastic.

Install sheet waterproofing and auxiliary materials to tie into adjacent waterproofing.

Repair tears, voids, and lapped seams in waterproofing not complying with requirements. Slit and flatten fishmouths and blisters. Patch with sheet waterproofing extending 6 inches beyond repaired areas in all directions.

Install protection course with butted joints over waterproofing membrane immediately.

Correct deficiencies in or remove sheet waterproofing that does not comply with requirements; repair substrates, reapply waterproofing, and repair sheet flashings.

      - ***************************************************************************************

      - Retain the following Article when molded-sheet drainage panels are in project-scope.

      - ***************************************************************************************

MOLDED-SHEET DRAINAGE PANEL INSTALLATION

Place and secure molded-sheet drainage panels, with geotextile facing away from wall or deck substrate, according to manufacturer’s written instructions. Use adhesives​<< or mechanical fasteners; or  None - N/A>>​ that do not penetrate waterproofing. Lap edges and ends of geotextile to maintain continuity. Protect installed molded-sheet drainage panels during subsequent construction.

For vertical applications, install << board insulation; or  protection course>> before installing drainage panels.

      - ***************************************************************************************

      - Retain the following Article when insulation is in project-scope.

      - ***************************************************************************************

INSULATION INSTALLATION

Install ​​<< one or more layers of board insulation to achieve required thickness; and  insulation drainage panels>>​​ over waterproofed surfaces. Cut and fit to within 3/4 inch of projections and penetrations.

On vertical surfaces, set insulation units in adhesive or tape applied according to manufacturer’s written instructions.

On horizontal surfaces, loosely lay insulation units according to manufacturer’s written instructions. Stagger end joints and tightly abut insulation units.

FIELD QUALITY CONTROL

On completion of horizontal membrane installation, dam installation area in preparation for flood testing.

Flood to minimum depth of << 1; or  _______>> inch with clean water. After 48 hours, inspect for leaks.

When leaking is found, remove water, repair leaking areas with new waterproofing materials as directed by LANL STR; repeat flood test. Repair damage to building.

When area is proven watertight, drain water and remove dam.

PROTECTION AND CLEANING

Do not permit foot or vehicular traffic on unprotected membrane.

Protect waterproofing from damage and wear during remainder of construction period.

      - ***************************************************************************************

      - Retain the following paragraph when board insulation type protection course, board insulation and/or insulation drainage panels are in project-scope.

      - ***************************************************************************************

Protect installed ​​<< board insulation; and  insulation drainage panels>>​​ from damage due to UV light, harmful weather exposures, physical abuse, and other causes. Provide temporary coverings where insulation will be subject to abuse and cannot be concealed and protected by permanent construction immediately after installation.

Clean spillage and soiling from adjacent construction using cleaning agents and procedures recommended by manufacturer of affected construction.

END OF SECTION

    - *********************************************************************************************

      - Do not omit the following reference information:

    - *********************************************************************************************

THE FOLLOWING STATEMENT IS FOR LANL USE ONLY

THIS PROJECT SPECIFICATION SECTION IS BASED ON LANL MASTER SPECIFICATION SECTION 07 1326, REV. 3, DATED APRIL 15, 2026.