Section 08 3323 
Overhead Coiling Doors

  - *************************************************************************************************************

    - LANL MASTER SPECIFICATION SECTION

Rev. 5 Summary of Changes: Edited and updated as required for import into SpecLink.

      - NOTE TO SPECIFIER ON USAGE IN SPECLINK: Activate the Section by turning on Seq #0000, followed by activating paragraphs in PART 1, Article SECTION INCLUDES. This will activate related articles, paras/subparas in the rest of the Section (i.e., SECTION INCLUDES in PART 1 activates articles and paras/subparas in PARTS 2 and 3). If there are choice fields to edit the entire Section (typically in this first author note or beginning of the Section), make selections at those locations, which will filter through the remaining Section. All Articles, paragraphs and subparagraphs must be activated sequentially from top to bottom, unless noted otherwise.

      - This template must be edited for each project. In doing so, Specifier must add job-specific requirements. Selections and choice fields are used to indicate designer choices or locations where text must be supplied by the designer. The section must also be edited to remove requirements for processes, items, or designs that are not included in the project.

      - To seek a variance from applicable requirements in this Section, contact the Engineering Standards Manual (ESM) Architectural POC  (LANL access only). Please contact POC with suggestions for improvement as well. LANL personnel should submit here: Suggested Change or Request Clarification; subcontractors via email to engstandards@lanl.gov.

      - When assembling a specification package, include applicable Sections from all Divisions, especially Division 1, General Requirements.

      - Section is developed for ML-4 projects. For ML1, 2, and 3 applications, additional requirements and independent reviews should be added if increased confidence in procurement or execution is desired; see LANL ESM Chapter 1 - General, Section Z10 specifications and quality sections.

  - *************************************************************************************************************

PART 1 - GENERAL

SECTION INCLUDES

      - ***************************************************************************************

      - The following paragraphs are designer-choice. Retain paragraphs for type(s) of door(s) selected for project based on project-scope. Selections here update the entire Section.

      - ***************************************************************************************

Non fire-rated Service doors​​​​<< with integral pass doors; or  None - N/A>>​​​​.

Non fire-rated Insulated Service doors​​<< with integral pass doors; or  None - N/A>>​​.

Fire-rated Service doors​​<< with integral pass doors; or  None - N/A>>​​.

Fire-rated Insulated Service doors​​<< with integral pass doors; or  None - N/A>>​​.

RELATED REQUIREMENTS

Section << 05 5000 - Metal Fabrications>>

Section << 08 7100 - Door Hardware>>

REFERENCE STANDARDS

AAMA 611 - Specification for Anodized Architectural Aluminum.

AAMA 2603 - Voluntary Specification, Performance Requirements and Test Procedures for Pigmented Organic Coatings on Aluminum Extrusions and Panels (with Coil Coating Appendix).

ABA Standards - ABA Accessibility Standards.

ASCE 7 - Minimum Design Loads and Associated Criteria for Buildings and Other Structures.

ASTM A653/A653M - Standard Specification for Steel Sheet, Zinc-Coated (Galvanized) or Zinc-Iron Alloy-Coated (Galvannealed) by the Hot-Dip Process.

ASTM A666/A666M - Standard Specification for Annealed or Cold-Worked Austenitic Stainless Steel Sheet, Strip, Plate, and Flat Bar.

ASTM B209/B209M - Standard Specification for Aluminum and Aluminum-Alloy Sheet and Plate.

ASTM B221 - Standard Specification for Aluminum and Aluminum-Alloy Extruded Bars, Rods, Wire, Profiles, and Tubes.

ASTM E84 - Standard Test Method for Surface Burning Characteristics of Building Materials.

ASTM E90 - Standard Test Method for Laboratory Measurement of Airborne Sound Transmission Loss of Building Partitions and Elements.

ASTM E283/E283M - Standard Test Method for Determining Rate of Air Leakage Through Exterior Windows, Skylights, Curtain Walls, and Doors Under Specified Pressure Differences Across the Specimen.

ASTM E330/E330M - Standard Test Method for Structural Performance of Exterior Windows, Doors, Skylights and Curtain Walls by Uniform Static Air Pressure Difference.

ASTM E413 - Classification for Rating Sound Insulation.

ASTM E1996 - Standard Specification for Performance of Exterior Windows, Curtain Walls, Doors, and Impact Protective Systems Impacted by Windborne Debris in Hurricanes.

NAAMM AMP 500-06 - Metal Finishes Manual.

NEMA ICS 1 - Industrial Control and Systems General Requirements.

NEMA ICS 2 - Industrial Control and Systems Controllers, Contactors and Overload Relays Rated 600 Volts.

NEMA IA 10030 - Industrial Control and Systems:  Enclosures.

NFPA 70 - National Electrical Code.

NFPA 80 - Standard for Fire Doors and Other Opening Protectives.

NFPA 105 - Standard for Smoke Door Assemblies and Other Opening Protectives.

NFPA 252 - Standard Methods of Fire Tests of Door Assemblies.

UL 325 - Standard for Door, Drapery, Gate, Louver, and Window Operators and Systems.

UL 723 - Standard for Test for Surface Burning Characteristics of Building Materials.

UL 1784 - Standard for Air Leakage Tests of Door Assemblies and Other Opening Protectives.

      - ***************************************************************************************

      - Edit submittals to include only those absolutely necessary to assure requirements and features that are important for the specific project will be met.

      - ***************************************************************************************

ACTION SUBMITTALS

Product Data: For each type and size of overhead coiling door and accessory.

Include construction details, material descriptions, dimensions of individual components, profiles for slats, and finishes.

Include rated capacities, operating characteristics, electrical characteristics, and furnished accessories.

Include description of automatic-closing device and testing and resetting instructions.

Shop Drawings: For each installation and for special components not dimensioned or detailed in manufacturer's product data.

Include plans, elevations, sections, and mounting details.

Include details of equipment assemblies, and indicate dimensions, required clearances, method of field assembly, components, and location and size of each field connection.

Include points of attachment locations.

For exterior components, include details of provisions for assembly expansion and contraction and for excluding and draining moisture to the exterior.

Show locations of controls, locking devices​<< , detectors or replaceable fusible links; or  None - N/A>>​, and other accessories.

Include diagrams for power, signal, and control wiring.

      - ***************************************************************************************

      - Retain the following paragraph when project requires samples for initial selection.

      - ***************************************************************************************

Samples for Initial Selection: Manufacturer's finish charts showing full range of colors and textures available for units with factory-applied finishes.

Include similar Samples of accessories involving color selection.

Samples for Verification: For each type of exposed finish on the following components, in manufacturer's standard sizes:

Curtain slats<< , including full vision window secured to slat; or  None - N/A>>.

Bottom bar​<< with sensor edge; or  None - N/A>>​.

Guides.

Brackets.

Hood.

Locking device(s).

Include similar Samples of accessories involving color selection.

INFORMATIONAL SUBMITTALS

Qualification Data: For Installer.

      - ***************************************************************************************

      - The following paragraph is activated automatically based on selections in PART 2, Article Performance Requirements.

      - ***************************************************************************************

Oversize Construction Certification: For door assemblies required to be fire-rated and that exceed size limitations of labeled assemblies.

      - ***************************************************************************************

      - Retain the following paragraph when project requires sample warranty.

      - ***************************************************************************************

Sample Warranty: For special warranty.

At Closeout:

Maintenance Manual with Maintenance Data for overhead coiling doors.

Warranty: For overhead doors and all components.

QUALITY ASSURANCE

Installer Qualifications: An entity that employs installers and supervisors who are trained and approved by manufacturer for both installation and maintenance of units required for this Project.

Maintenance Proximity: Not more than ​​<< four; or  _______>>​​ hours normal travel time from Installer's place of business to Project site.

Source Limitations: Obtain overhead coiling doors from a single-source manufacturer. Obtain operators and controls from overhead coiling-door manufacturer.

      - ***************************************************************************************

      - Retain the following paragraph when fire-rated door assemblies are in project-scope.

      - ***************************************************************************************

Fire-Rated Door Assemblies: Where fire-rated door assemblies are indicated or required, comply with <<NFPA 80>>.

WARRANTY

Special Warranty: Manufacturer agrees to repair or replace components of doors that fail in materials or workmanship within specified warranty period.

Warranty Period: << Two; or  _______>> years from date of Substantial Completion.

PART 2 - PRODUCTS

MANUFACTURERS

Cookson Company.

Overhead Door Company.

Wayne-Dalton Door Company.

PERFORMANCE REQUIREMENTS

      - ***************************************************************************************

      - The following two paragraphs are designer-choice. Retain the first paragraph when fire-rated assemblies are required for project. Retain the second paragraph when sound control doors are required for project.

      - ***************************************************************************************

Fire-Rated Door Assemblies: Complying with <<NFPA 80>> and listed and labeled by qualified testing agency acceptable to LANL for fire-protection ratings and temperature-rise limits, based on testing at as close to neutral pressure as possible according to <<NFPA 252>>.

        - ******************************************************************************

        - Retain the following subparagraphs based on type of fire-rated assemblies in project-scope. Selection of the type here updates the entire Section.

        - ******************************************************************************

Oversize Fire-Rated Door Assemblies: For units exceeding sizes of tested assemblies, provide certification by a qualified testing agency that doors comply with standard construction requirements for tested and labeled fire-rated door assemblies except for size.

Smoke-Control and Draft-Control Assemblies: Where indicated, provide doors that are listed and labeled with the letter "S" on the fire-rating label by a qualified testing agency for smoke-control and draft-control, based on testing according to <<UL 1784>>; with maximum air-leakage rate of 3.0 cfm/sq. ft. of door opening at 0.10-inch wg for both ambient and elevated temperature tests.

      - ***************************************************************************************

      - Selection of sound-control doors here updates the entire Section.

      - ***************************************************************************************

Sound-Control Doors: Assemblies tested in a laboratory for sound-transmission-loss performance according to <<ASTM E90>>, calculated according to <<ASTM E413>>, and rated for not less than the STC value indicated.

Wind Performance of Exterior Doors: Capable of withstanding the following design wind loads:

Design Wind Load: As indicated on Drawings, acting inward and outward.

Testing: In accordance with <<ASTM E330/E330M>>.

Deflection Limits: Design overhead coiling doors to withstand design wind load without evidence of permanent deformation or disengagement of door components.

Operability under Wind Load: Design overhead coiling doors to remain operable under design wind load, acting inward and outward.

Windborne-Debris Impact Resistance: Provide ​​<< glazed; and  impact-protective>>​​ overhead coiling doors that pass missile-impact and cyclic-pressure tests according to <<ASTM E1996>> utilizing wind design criteria as indicated on Drawings.

Large-Missile Test: For overhead coiling doors located within 30 feet of grade.

Small-Missile Test: For overhead coiling doors located more than 30 feet above grade.

Seismic Performance: Overhead coiling doors shall withstand the effects of earthquake motions determined according to <<ASCE 7>> based on seismic design criteria indicated on Drawings.

MATERIAL, GENERAL

Electrical Components, Devices, and Accessories: Listed and labeled as defined in <<NFPA 70>>, by a qualified testing agency, and marked for intended location and application.

Refer to Section << 05 5000 - Metal Fabrications>> for << miscellaneous steel supports;  door-opening framing;  corner guards; and  bollards>>.

      - ***************************************************************************************

      - IMPORTANT: Selections made in Article Door Assembly  update the applicable paragraphs/subparagraphs in the related articles in PART 2.

      - ***************************************************************************************

DOOR ASSEMBLY

      - ***************************************************************************************

      - Retain the following paragraph when fire-rated door assemblies are in project-scope.

      - ***************************************************************************************

Fire Rating: ​​​​​​​​​​<< 3/4 hour;  1 hour;  1-1/2 hours;  3 hours; or  4 hours>>​​​​​​​​​​ ​​​​​​​​​​<< with temperature-rise limit;  with smoke-control and draft-control;  with temperature-rise limit and smoke-control and draft-control; or  None - N/A>>​​​​​​​​​​.

Air Infiltration: Maximum rate of 1.0 cfm/sq. ft. at 15 and 25 mph when tested according to <<ASTM E283/E283M>>.

      - ***************************************************************************************

      - The following two paragraphs are designer-choices. Retain the first paragraph for sound-control door assemblies. Retain the second paragraph for non-fire rated and fire-rated insulated service doors.

      - ***************************************************************************************

STC Rating: 20 minimum.

Curtain R-Value: Minimum 7.0 deg F x h x sq. ft. /BTU.

Door Curtains:

Material: ​​​​​<< Galvanized steel;  Stainless steel; or  Aluminum>>​​​​​.

Slats: << Curved; or  Flat>> profile slats of << 1-7/8-inch;  2-5/8-inch;  3-1/4-inch; or  Insert dimension>> center-to-center height.

        - ******************************************************************************

        - The following four subparagraphs are designer-choices. Select one of the following three subparagraphs for the type of slat (perforated vs. fenestrated vs. vision). Retain the last subparagraph for non-fire rated and fire-rated insulated service doors.

        - ******************************************************************************

Perforated Slats: Approximately ​​​​​​<< 1/16-inch pinholes;  3/32-inch pinholes;  7/8-inch wide by 3/8-inch-high slots; or  Insert dimension>>​​​​​​.

          - *** OR ***

Fenestrated Slats: Approximately ​​​​​​<< 3- by 5/8-inch;  4- by 5/8-inch;  10- by 1-inch; or  Insert dimensions>>​​​​​​ openings spaced approximately ​​​<< 1-1/2 inches; or  Insert dimension>>​​​ apart and beginning 12 inches from jamb guides.

          - *** OR ***

Vision Panels: Approximately 10- by 1-inch openings spaced approximately 2 inches apart and beginning 12 inches from end guides; in ​​​​​<< two;  three; or  Insert number>>​​​​​ rows of slats at height indicated on Drawings; installed with​​​<< insulated; or  None - N/A>>​​​ vision-panel glazing.

Insulated-Slat Interior Facing: Metal.

Gasket Seal. Manufacturer's standard continuous gaskets between slats.

Bottom Bar: Two angles, each not less than​​​​​​​​​<< 1-1/2 by 1-1/2 by 1/8 inch thick; or  Insert dimensions>>​​​​​​​​​​; fabricated from material and finished << to match door; or  Insert requirement>>.

Curtain Jamb Guides: Material with exposed finish matching curtain slats.

      - ***************************************************************************************

      - Retain the following paragraph if the service door includes integral pass doors. The following selections in the paragraph below regarding the pass door frame type is a designer-choice based on project-specific requirements.

      - A hinged frame pass door swings as a single integrated unit — simple and compact, but heavier and less durable. Hinged frame designs cannot maintain a continuous fire barrier and are therefore not fire-rated.

      - A rigid frame pass door uses a stationary frame with only the leaf operating — stronger, more stable, and suitable for high-performance or insulated systems. Rigid frame types may be used adjacent to fire-rated doors instead.

      - ***************************************************************************************

Pass Door(s): The following frame(s) with << lockset; or  exit hardware>>.

Hinged frame (non fire-rated)

Rigid frame (fire-rated)

Hood: Match curtain material and finish.

Shape: ​​​​​​<< Round;  Square;  As indicated on Drawings; or  Insert shape>>​​​​​​.

Mounting: << Face of wall;  Between jambs; or  As indicated on Drawings>>.

Locking Devices: Equip door with ​​​​<< slide bolt for padlock;  locking device assembly;  chain lock keeper; and  safety interlock switch>>​​​​.

Locking Device Assembly: ​​​​​<< Single-jamb side; or  Both jamb sides>>​​​​​ locking bars, operable from ​​​​​<< inside with thumbturn;  outside with cylinder;  outside only, with cylinder;  inside and outside with cylinders; or  Insert requirement>>​​​​​.

      - ***************************************************************************************

      - The subparagraphs in the paragraph below are designer-choices. Retain based on project-specific requirements.

      - ***************************************************************************************

Curtain Accessories: Equip door with:

        - ******************************************************************************

        - Smoke seals are required for smoke-control and draft-control fire-rated doors.

        - ******************************************************************************

Smoke seals

        - ******************************************************************************

        - Weatherseals are required for exterior doors.

        - ******************************************************************************

Weatherseals

        - ******************************************************************************

        - Push/pull handles required for push-up-operated or emergency-operated doors.

        - ******************************************************************************

Push/pull handles

        - ******************************************************************************

        - Pull-down straps are required for doors more than 84 inches high.

        - ******************************************************************************

Pull-down strap

        - ******************************************************************************

        - Pole hooks and poles are required for doors more than 84 inches high.

        - ******************************************************************************

Pole hook

        - ******************************************************************************

        - Automatic closing devices are required for fire-rated doors.

        - ******************************************************************************

Automatic-closing device

<< Insert item>>

      - ***************************************************************************************

      - The following two paragraphs are designer-choices. Retain door operator type based on project-specific requirements.

      - ***************************************************************************************

Manual Door Operator: ​​​​​<< Push-up operation;  Chain-hoist operator;  Manufacturer's standard crank operator;  Awning-crank operator; or  Wall-crank operator>>​​​​​.

        - ******************************************************************************

        - Retain the following subparagraphs when "crank operator" option is selected in the paragraph above.

        - ******************************************************************************

Provide operator with through-wall shaft operation.

Provide operator with manufacturer's standard removable operating arm.

Electric Door Operator:

Usage Classification: ​<< Heavy duty, 25 or more cycles per hour and more than 90 cycles per day;  Standard duty, up to 25 cycles per hour and up to 90 cycles per day;  Medium duty, up to 12 cycles per hour and up to 50 cycles per day;  Light duty, up to 10 cycles per hour; or  _______>>​.

Operator Location: ​​<< Top of hood;  Front of hood;  Wall;  Bench;  Through wall; or  As indicated on Drawings>>​​.

Safety: Listed according to <<UL 325>>​ by a qualified testing agency for commercial or industrial use​<< with moving parts of operator enclosed or guarded if exposed and mounted at 8 feet or lower; or  None - N/A>>​.

Motor Exposure: ​<< Interior; or  Exterior, wet, and humid>>​.

Motor Electrical Characteristics:

Horsepower: ​​​​​<< 1/2;  1;  2;  3; or  Insert value>>​​​​​ HP.

          - **********************************************************************

          - Select one of the following two subparagraphs based on project-specific requirements.

          - **********************************************************************

Voltage: ​​​​<< 115 VAC;  208 VAC; or  230 VAC>>​​​​, single phase, 60 Hz.

          - *** OR ***

Voltage: ​​​<< 208 VAC;  230 VAC; or  460 VAC>>​​​, three phase, 60 Hz.

Emergency Manual Operation: ​<< Push-up;  Chain; or  Crank>>​ type.

Obstruction-Detection Device: ​<< Photoelectric sensor;  Photoelectric sensor; self-monitoring type;  Electric sensor edge on bottom bar;  Electric sensor edge on bottom bar; self-monitoring type;  Pneumatic sensor edge on bottom bar; or  Insert type>>​.

Sensor Edge Bulb Color: ​​​<< Black;  As selected by Architect from manufacturer's full range; or  Insert color>>​​​.

Control Station(s): ​​​​​<< Interior mounted;  Exterior mounted;  Where indicated on Drawings; or  Insert location>>​​​​​.

Other Equipment: ​​​​​​<< Audible and visual signals;  Portable radio-control system; and  Insert device>>​​​​​​.

Door Finish:

        - ******************************************************************************

        - Select one of the three subparagraphs for door finish based on project-specific requirements.

        - ******************************************************************************

Steel Finish: ​​​​​​<< Factory Prime Finish - Manufacturer's standard color;  Baked-Enamel or Powder-Coated Finish - Color as indicated by manufacturer's designations;  Baked-Enamel or Powder-Coated Finish - Color matching Architect's sample;  Baked-Enamel or Powder-Coated Finish - Color as selected by Architect from manufacturer's full range; or  Baked-Enamel or Powder-Coated Finish -  Insert color>>​​​​​​.

        - *** OR ***

Stainless Steel Finish: ​<< No. 4 (polished directional satin);  No. 2B (bright, cold rolled); or  Insert finish>>​.

        - *** OR ***

Aluminum Finish: ​​​​​​​​<< Clear anodized;  Light bronze anodized;  Medium bronze anodized;  Dark bronze anodized;  Black anodized;  Anodized color matching Architect's sample;  Anodized color as selected by Architect from full range of industry colors and color densities;  Baked-Enamel or Powder-Coated Finish - Color as indicated by manufacturer's designations;  Baked-Enamel or Powder-Coated Finish - Color matching Architect's sample;  Baked-Enamel or Powder-Coated Finish - Color as selected by Architect from manufacturer's full range; or  Baked-Enamel or Powder-Coated Finish -  Insert color>>​​​​​​​​.

Interior Curtain-Slat Facing Finish: ​<< Match finish of exterior curtain-slat face;  Finish as indicated by manufacturer's designations;  Finish matching Architect's sample;  Finish as selected by Architect from manufacturer's full range; or  Insert finish>>​.

DOOR CURTAINS

Curtains: Fabricate overhead coiling-door curtain of interlocking metal slats, designed to withstand wind loading indicated, in a continuous length for width of door without splices. Unless otherwise indicated, provide slats of thickness and mechanical properties recommended by door manufacturer for performance, size, and type of door indicated, and as follows:

        - ******************************************************************************

        - Select one of the three subparagraphs for door curtain slat material based on project-specific requirements.

        - ******************************************************************************

Steel Door Curtain Slats: Zinc-coated (galvanized), cold-rolled structural-steel sheet; complying with <<ASTM A653/A653M>>, with G90 zinc coating; nominal sheet thickness (coated) of 0.028 inch.

        - *** OR ***

Stainless Steel Door Curtain Slats: <<ASTM A666/A666M>>, Type 304; sheet thickness of 0.025 inch.

        - *** OR ***

Aluminum Door Curtain Slats: <<ASTM B209/B209M>> sheet or <<ASTM B221>> extrusions, manufacturer's standard alloy and temper for type of use and finish indicated; thickness of 0.050 inch.

        - ******************************************************************************

        - The following two subparagraphs are designer-choices. Retain the first subparagraph when vision panels are selected for project. Retain the second subparagraph for non-fire rated and fire-rated insulation service doors.

        - ******************************************************************************

Vision-Panel Glazing: Manufacturer's standard clear glazing, fabricated from transparent acrylic sheet or fire-protection-rated glass as required for type of door; set in glazing channel secured to curtain slats.

Insulation: Fill slats for insulated doors with manufacturer's standard thermal insulation complying with maximum flame-spread and smoke-developed indexes of 75 and 450, respectively, according to <<ASTM E84>> or <<UL 723>>​. Enclose insulation completely within slat faces.

Metal Interior Curtain-Slat Facing: Match metal of exterior curtain-slat face, with ​​​​​​​​​<< minimum steel thickness of 0.010 inch; or  minimum aluminum thickness of 0.032 inch>>​​​​​​​​​.

Curtain Jamb Guides: Manufacturer's standard angles or channels and angles of same material and finish as curtain slats unless otherwise indicated, with sufficient depth and strength to retain curtain, to allow curtain to operate smoothly, and to withstand loading. Slot bolt holes for guide adjustment. Provide removable stops on guides to prevent overtravel of curtain​​​​<< , and a continuous bar for holding windlocks; or  None - N/A>>​​​​.

      - ***************************************************************************************

      - Retain the following paragraph if the service door includes integral pass doors.

      - ***************************************************************************************

Pass Door(s): Swinging door and frame assembly constructed integrally with the coiling-door assembly​​​<< and bearing the same fire rating, as applicable; or  None - N/A>>​​​. Comply with <<ABA Standards>> for accessibility requirements.

Door Frame and Integral Jamb Guide: Fabricate of angles or channels and angles of same material and finish as curtain slats unless otherwise indicated, with sufficient depth and strength to retain curtain, to allow curtain to operate smoothly, and to withstand loading.

        - ******************************************************************************

        - Retain the following two subparagraphs based on frame type selected for project.

        - ******************************************************************************

Hinged Frame (non fire-rated doors): Hinged pass door and frame that swings out of the way, as a unit, to allow use of the full coiling-door opening width. One jamb of the pass door frame hinged and the other jamb having a guide for the lower, narrower part of the coiling-door curtain.

Rigid Frame (fire-rated doors): Rigid pass door and frame that are built into the rigid, lower part of the door curtain and that raise with the curtain.

Locking Hardware:

​​​​​​​<< Lockset; or  Exit Hardware>>​​​​​​​: ​​​​​​​<< As specified in Section 08 7100 - Door Hardware;  As selected by Architect from manufacturer's full range.; or  Insert requirement>>​​​​​​​

Lock Cylinders: ​​<< As specified in Section 08 7100 - Door Hardware;  Standard with manufacturer; or  Keyed to building keying system>>​​.

Keys: ​​​​​​<< Two;  Three; or  Insert number>>​​​​​​​ for each cylinder.

Thresholds: Equip pass doors with integral thresholds that comply with <<ABA Standards>>.

HOOD

General: Form sheet metal hood to entirely enclose coiled curtain and operating mechanism at opening head. Contour to fit end brackets to which hood is attached. Roll and reinforce top and bottom edges for stiffness. Form closed ends for surface-mounted hoods and fascia for any portion of between-jamb mounting that projects beyond wall face. Equip hood with intermediate support brackets as required to prevent sagging.

        - ******************************************************************************

        - Select one of the three subparagraphs for hood material based on project-specific requirements.

        - ******************************************************************************

Galvanized Steel: Nominal 0.028-inch thick, hot-dip galvanized-steel sheet with G90 zinc coating, complying with <<ASTM A653/A653M>>​.

        - *** OR ***

Stainless Steel: 0.025-inch thick, stainless-steel sheet, Type 304, complying with <<ASTM A666/A666M>>.

        - *** OR ***

Aluminum: 0.040 inch-thick aluminum sheet complying with <<ASTM B209/B209M>>, of alloy and temper recommended by manufacturer and finisher for type of use and finish indicated.

        - ******************************************************************************

        - Retain the following subparagraph for fire-rated doors.

        - ******************************************************************************

Include automatic drop baffle on fire-rated doors to guard against passage of smoke or flame.

Exterior-Mounted Doors: Fabricate hood to act as weather protection and with a perimeter sealant-joint-bead profile for applying joint sealant.

Removable Metal Soffit: Formed or extruded from same metal and with same finish as curtain if hood is mounted above ceiling unless otherwise indicated.

LOCKING DEVICES

      - ***************************************************************************************

      - Retain the following paragraphs based on project-specific requirements.

      - ***************************************************************************************

Slide Bolt: Fabricate with side-locking bolts to engage through slots in tracks for locking by padlock, located on both left and right jamb sides, operable from coil side.

Locking Device Assembly: Fabricate with cylinder lock, spring-loaded dead bolt, operating handle, cam plate, and adjustable locking bars to engage through slots in tracks.

Lock Cylinders: << As specified in Section  08 7100 - Door Hardware;  Standard with manufacturer; or  Keyed to building keying system>>.

Keys: ​​​<< Two;  Three; or  Insert number>>​​​ for each cylinder.

Chain Lock Keeper: Suitable for padlock.

Safety Interlock Switch: Equip power-operated doors with safety interlock switch to disengage power supply when door is locked.

CURTAIN ACCESSORIES

      - ***************************************************************************************

      - Retain the following paragraphs based on project-specific requirements.

      - ***************************************************************************************

Smoke Seals: Equip each fire-rated door with replaceable smoke-seal perimeter gaskets or brushes for smoke and draft control as required for door listing and labeling by a qualified testing agency.

Weatherseals for Exterior Doors: Equip each exterior door with weather stripping gaskets fitted to entire exterior perimeter of door for a weather-resistant installation, unless otherwise indicated.

At door head, use 1/8inch thick, replaceable, continuous-sheet baffle secured to inside of hood or field-installed on the header.

At door jambs, use replaceable, adjustable, continuous, ​​​​<< flexible, 1/8 inch thick seals of flexible vinyl, rubber, or neoprene;  nylon brushes; or  Insert material>>​​​​.

Push/Pull Handles: Equip each push-up-operated or emergency-operated door with lifting handles on each side of door, finished to match door.

Pull-Down Strap: Provide pull-down straps for doors more than 84 inches high.

Pole Hooks: Provide pole hooks and poles for doors more than 84 inches high.

Automatic-Closing Device: Equip each fire-rated door with an automatic-closing device or holder-release mechanism and governor unit complying with <<NFPA 80>> and an easily tested and reset release mechanism.<< Testing for manually operated doors shall allow resetting by opening the door without re-tensioning the counterbalance mechanism.; or   Release mechanism for motor-operated doors shall allow testing without mechanical release of the door.>>​ Automatic-closing device shall be designed for activation by the following:

Replaceable fusible links with temperature rise and melting point of ​<< 165 degrees F; or  Insert temperature>>​ interconnected and mounted on both sides of door opening.

        - ******************************************************************************

        - Select one of the following two subparagraphs based on project-specific requirements.

        - ******************************************************************************

Manufacturer's standard UL-labeled smoke detector and door-holder-release devices.

        - *** OR ***

Manufacturer's standard UL-labeled heat detector and door-holder-release devices.

Building fire-detection, smoke-detection, and fire-alarm systems.

COUNTERBALANCE MECHANISM

General: Counterbalance doors by means of manufacturer's standard mechanism with an adjustable-tension, steel helical torsion spring mounted around a steel shaft and contained in a spring barrel connected to top of curtain with barrel rings. Use grease-sealed bearings or self-lubricating graphite bearings for rotating members.

Counterbalance Barrel: Fabricate spring barrel of manufacturer's standard hot-formed, structural-quality, seamless or welded carbon-steel pipe, of sufficient diameter and wall thickness to support rolled-up curtain without distortion of slats and to limit barrel deflection to not more than 0.03 inch/ft. of span under full load.

Counterbalance Spring: One or more oil-tempered, heat-treated steel helical torsion springs. Size springs to counterbalance weight of curtain, with uniform adjustment accessible from outside barrel. Secure ends of springs to barrel and shaft with cast-steel barrel plugs.

        - ******************************************************************************

        - Retain the following subparagraph for fire-rated doors.

        - ******************************************************************************

Fire-Rated Doors: Equip with auxiliary counterbalance spring and prevent tension release from main counterbalance spring when automatic-closing device operates.

Torsion Rod for Counterbalance Shaft: Fabricate of manufacturer's standard cold-rolled steel, sized to hold fixed spring-ends and carry torsional load.

Brackets: Manufacturer's standard mounting brackets of either cast iron or cold-rolled steel plate.

      - ***************************************************************************************

      - The following two Articles Manual Door Operator and Electric Door Operator are designer-choices. Retain door operator type based on project-specific requirements.

      - ***************************************************************************************

MANUAL DOOR OPERATOR

General: Equip door with manual door operator by door manufacturer.

      - ***************************************************************************************

      - Select one of the following three paragraphs based on project-specific requirements.

      - ***************************************************************************************

Push-up Door Operation: Lift handles and pull rope for raising and lowering doors, with counterbalance mechanism designed such that required lift or pull for door operation does not exceed 25 lbf.

      - *** OR ***

Chain-Hoist Operator: Consisting of endless steel hand chain, chain-pocket wheel and guard, and gear-reduction unit with a maximum 25 lbf for door operation. Provide alloy-steel hand chain with chain holder secured to operator guide.

      - *** OR ***

Crank Operator: Consisting of crank and crank gearbox, steel crank drive shaft, and gear-reduction unit, of type indicated. Size gears to require not more than 25 lbf to turn crank. Fabricate gearbox to be oil-tight and to completely enclose operating mechanism. Provide manufacturer's standard crank-locking device.

ELECTRIC DOOR OPERATOR

General: Electric door operator assembly of size and capacity recommended and provided by door manufacturer for door and operation-cycles requirement specified, with electric motor and factory-prewired motor controls, starter, gear-reduction unit, solenoid-operated brake, clutch, control stations, control devices, integral gearing for locking door, and accessories required for proper operation.

Comply with <<NFPA 70>>.

Control equipment complying with <<NEMA ICS 1>>, <<NEMA ICS 2>>, and <<NEMA IA 10030>>, with <<NFPA 70>> Class 2 control circuit, maximum 24 VAC or VDC.

Door Operator Location(s): Operator location indicated for each door.

        - ******************************************************************************

        - Select one of the following subparagraphs for door operator location based on project-specific requirements.

        - ******************************************************************************

Top-of-Hood Mounted: Operator is mounted to the right or left door head plate with the operator on top of the door-hood assembly and connected to the door drive shaft with drive chain and sprockets. Headroom is required for this type of mounting.

        - *** OR ***

Front-of-Hood Mounted: Operator is mounted to the right or left door head plate with the operator on coil side of the door-hood assembly and connected to the door drive shaft with drive chain and sprockets. Front clearance is required for this type of mounting.

        - *** OR ***

Wall Mounted: Operator is mounted to the inside front wall on the left or right side of door and connected to door drive shaft with drive chain and sprockets. Side room is required for this type of mounting. Wall-mounted operator can also be mounted above or below shaft; if above shaft, headroom is required.

        - *** OR ***

Bench Mounted: Operator is mounted to the right or left door head plate and connected to the door drive shaft with drive chain and sprockets. Side room is required for this type of mounting.

        - *** OR ***

Through-Wall Mounted: Operator is mounted on other side of wall from coil side of door.

Motors: Reversible-type motor​<< with controller (disconnect switch); or  None - N/A>>​ for motor exposure indicated for each door assembly.

Electrical Characteristics: Minimum as indicated for each door assembly. If not indicated, large enough to start, accelerate, and operate door in either direction from any position, at a speed not less than 8 inch/s and not more than 24 inch/s, without exceeding nameplate ratings or service factor.

Operating Controls, Controllers, Disconnect Switches, Wiring Devices, and Wiring: Manufacturer's standard unless otherwise indicated.

Coordinate wiring requirements and electrical characteristics of motors and other electrical devices with building electrical system and each location where installed.

Limit Switches: Equip each motorized door with adjustable switches interlocked with motor controls and set to automatically stop door at fully opened and fully closed positions.

Obstruction-Detection Devices: External entrapment protection consisting of indicated automatic safety sensor capable of protecting full width of door opening.

        - ******************************************************************************

        - Retain the following two subparagraphs based on the type of door(s) in project-scope (non-fire rated vs. fire-rated).

        - ******************************************************************************

Non-fire-rated doors: Activation of device immediately stops and reverses downward door travel.

Fire-rated doors: Activation delays closing.

        - ******************************************************************************

        - Select one of the following subparagraphs for the door sensor based on project-specific requirements.

        - ******************************************************************************

Photoelectric Sensor: Manufacturer's standard system designed to detect an obstruction in door opening without contact between door and obstruction.

          - **********************************************************************

          - The following subparagraph is a designer-choice. Retain when required for project.

          - **********************************************************************

Self-Monitoring Type: Designed to interface with door operator control circuit to detect damage to or disconnection of sensing device. When self-monitoring feature is activated, door closes only with sustained or constant pressure on close button.

        - *** OR ***

Electric Sensor Edge: Automatic safety sensor edge, located within astragal or weather stripping mounted to bottom bar. Contact with sensor activates device. Connect to control circuit using manufacturer's standard take-up reel or self-coiling cable.

          - **********************************************************************

          - The following subparagraph is a designer-choice. Retain when required for project.

          - **********************************************************************

Self-Monitoring Type: Four-wire-configured device designed to interface with door operator control circuit to detect damage to or disconnection of sensor edge.

        - *** OR ***

Pneumatic Sensor Edge: Automatic safety sensor edge, located within astragal or weather stripping mounted to bottom bar. Contact with sensor activates device.

Control Station: Three-button control station in fixed location with momentary-contact push-button controls labeled "Open" and "Stop" and sustained-pressure or constant-pressure push-button control labeled "Close."

        - ******************************************************************************

        - Select one of the following subparagraphs for the control station based on project-specific requirements.

        - ******************************************************************************

Interior-Mounted Units: Full-guarded, surface-mounted, heavy-duty type, with general-purpose <<NEMA IA 10030>>, Type 1 enclosure.

        - *** OR ***

Exterior-Mounted Units: Full-guarded, standard-duty, surface-mounted, weatherproof type, <<NEMA IA 10030>>, Type 4 enclosure, key operated.

Emergency Manual Operation: Equip each electrically powered door with capability for emergency manual operation. Design manual mechanism such that required force for door operation does not exceed 25 lbf.

Emergency Operation Disconnect Device: Equip operator with hand-operated disconnect mechanism for automatically engaging manual operator and releasing brake for emergency manual operation while disconnecting motor without affecting timing of limit switch. Mount mechanism such that it is accessible from floor level. Include interlock device to automatically prevent motor from operating when emergency operator is engaged.

Motor Removal: Design operator such that motor may be removed without disturbing limit-switch adjustment and without affecting emergency manual operation.

      - ***************************************************************************************

      - The following two paragraphs are designer-choices. Retain the first paragraph when audible and visual signals required for project. Retain the second paragraph when portable radio-control system required for project.

      - ***************************************************************************************

Audible and Visual Signals: Audible alarm and visual indicator lights in compliance with <<ABA Standards>>.

Portable Radio-Control System: Consisting of ​​​​​​​​​​the following per door operator:

        - ******************************************************************************

        - The following subparagraphs are designer-choices. Retain based on project-specific requirements.

        - ******************************************************************************

Three-channel universal coaxial receiver to open, close, and stop door.

Portable control device to open and stop door may be momentary-contact type; control to close door shall be sustained-pressure or constant-pressure type.

Remote-antenna mounting kit.

GENERAL FINISH REQUIREMENTS

Comply with <<NAAMM AMP 500-06>> for recommendations for applying and designating finishes.

Appearance of Finished Work: Noticeable variations in same piece are not acceptable. Variations in appearance of adjoining components are acceptable if they are within the range of approved Samples and are assembled or installed to minimize contrast.

      - ***************************************************************************************

      - Retain the following three Articles Steel and Galvanized Steel Finishes, and Stainless Steel Finishes, and Aluminum Finishes based on materials and finishes selected for project.

      - ***************************************************************************************

STEEL AND GALVANIZED STEEL FINISHES

      - ***************************************************************************************

      - Select one of the following paragraphs for steel finish (factory prime vs. baked-enamel or powder-coat) based on project-specific requirements.

      - ***************************************************************************************

Factory Prime Finish: Manufacturer's standard primer, compatible with field-applied finish. Comply with coating manufacturer's written instructions for cleaning, pretreatment, application, and minimum dry film thickness.

      - *** OR ***

Baked-Enamel or Powder-Coat Finish: Manufacturer's standard baked-on finish consisting of prime coat and thermosetting topcoat. Comply with coating manufacturer's written instructions for cleaning, pretreatment, application, and minimum dry film thickness.

STAINLESS STEEL FINISHES

Surface Preparation: Remove tool and die marks and stretch lines, or blend into finish.

      - ***************************************************************************************

      - Select one of the following paragraphs for stainless steel finish (polished vs. unpolished) based on project-specific requirements.

      - ***************************************************************************************

Polished Finishes: Grind and polish surfaces to produce uniform finish, free of cross scratches.

Run grain of directional finishes with long dimension of each piece.

When polishing is completed, passivate and rinse surfaces. Remove embedded foreign matter and leave surfaces chemically clean.

Directional Satin Finish: No. 4.

      - *** OR ***

Bright, Cold-Rolled, Unpolished Finish: No. 2B.

ALUMINUM FINISHES

      - ***************************************************************************************

      - Select one of the following paragraphs for aluminum finish (clear anodic vs. color anodic vs. baked-enamel or powder-coated) based on project-specific requirements.

      - ***************************************************************************************

Clear Anodic Finish: <<AAMA 611>>, ​​<< AA-M12C22A41, Architectural Class I, 0.018 mm; or  AA-M12C22A31, Architectural Class II, 0.010 mm>>​​ or thicker.

      - *** OR ***

Color Anodic Finish: <<AAMA 611>>​, << AA-M12C22A42, Architectural Class I, 0.018 mm;  AA-M12C22A44, Architectural Class I, 0.018 mm;  AA-M12C22A32, Architectural Class II, 0.010 mm; or  AA-M12C22A34, Architectural Class II, 0.010 mm>> or thicker.

      - *** OR ***

Baked-Enamel or Powder-Coated Finish: <<AAMA 2603>>. Comply with coating manufacturer's written instructions for cleaning, conversion coating, and applying and baking finish.

PART 3 - EXECUTION

EXAMINATION

Examine substrates areas and conditions, with Installer present, for compliance with requirements for substrate construction and other conditions affecting performance of the Work.

Examine locations of electrical connections.

Proceed with installation only after unsatisfactory conditions have been corrected.

INSTALLATION

Install overhead coiling doors and operating equipment complete with necessary hardware, anchors, inserts, hangers, and equipment supports according to manufacturer's written instructions and as specified.

Install overhead coiling doors, hoods, controls, and operators at the mounting locations indicated for each door.

Accessibility: Install overhead coiling doors, switches, and controls along accessible routes in compliance with <<ABA Standards>>.

      - ***************************************************************************************

      - The following three paragraphs are designer-choices. Retain the first paragraph when fire-rated doors are in project-scope. Retain the second paragraph when smoke-control and draft-control doors are in project-scope. Retain the third paragraph when power-operated doors are in project-scope.

      - ***************************************************************************************

Fire-Rated Doors: Install according to <<NFPA 80>>.

Smoke-Control and Draft-Control Doors: Install according to <<NFPA 80>> and <<NFPA 105>>.

Power-Operated Doors: Install<< automatic garage doors openers; or  None - N/A>> according to <<UL 325>>.

STARTUP SERVICE

Engage a factory-authorized service representative to perform startup service.

Complete installation and startup checks according to manufacturer's written instructions.

Test and adjust controls and safety devices. Replace damaged and malfunctioning controls and equipment.

Test door closing when activated by detector or alarm-connected automatic-closing system. Reset door-closing mechanism after successful test.

ADJUSTING

Adjust hardware and moving parts to function smoothly such that doors operate easily, free of warp, twist, or distortion.

Adjust exterior doors and components to be weather resistant.

Lubricate bearings and sliding parts as recommended by manufacturer.

Adjust seals to provide tight fit around entire perimeter.

MAINTENANCE SERVICE

Initial Maintenance Service: Beginning at Substantial Completion, maintenance service shall include 12 months full maintenance by skilled employees of coiling-door Installer. Include monthly preventive maintenance, repair or replacement of worn or defective components, lubrication, cleaning, and adjusting as required for proper door operation. Parts and supplies shall be manufacturer's authorized replacement parts and supplies.

Perform maintenance, including emergency callback service, during normal working hours.

Include 24-hour-per-day, seven-day-per-week, emergency callback service.

DEMONSTRATION

Engage a factory-authorized service representative to train LANL's maintenance personnel to adjust, operate, and maintain overhead coiling doors.

END OF SECTION

    - **********************************************************************************************

      - Do not omit the following reference information:

    - **********************************************************************************************

THE FOLLOWING STATEMENT IS for lanl use only

THIS PROJECT SPECIFICATION SECTION IS BASED ON LANL MASTER SPECIFICATION SECTION 08 3323, REV. 5, DATED APRIL 15, 2026.