SECTION 08 4113

ALUMINUM-FRAMED ENTRANCES AND STOREFRONTS

*************************************************************************************************************

LANL MASTER SPECIFICATION

In Word, click on the ¶ button to VIEW-HIDDEN TEXT and SEE Authors notes in blue.

This template must be edited for each project.  In doing so, specifier must add job-specific requirements.  Brackets are used in the text to indicate designer choices or locations where text must be supplied by the designer.  Once the choice is made or text supplied, remove the brackets.  The specifications must also be edited to delete specification requirements for processes, items, or designs that are not included in the project - and specifiers’ notes such as these.  Additional tailoring requirements are contained in ESM Chapter 1 Section Z10 Att. F, Specifications.

To seek a variance from requirements in the specifications that are applicable, contact the Engineering Standards Manual Architectural POC. Please contact POC with suggestions for improvement as well.

When assembling a specification package, include applicable specifications from all Divisions, especially Division 1, General requirements.

Specification developed for ML-4 projects.  For ML-1, 2, and 3 applications, additional requirements and independent reviews should be added if increased confidence in procurement or execution is desired; see ESM Chapter 1 Section Z10 Specifications and Quality sections.
*************************************************************************************************************

PART 1  GENERAL

  - SECTION INCLUDES

- Aluminum doors and storefront frames

- Entrance door hardware

  - SYSTEM DESCRIPTION

- Aluminum entrances and storefront system includes tubular aluminum sections with supplementary internal support framing as required, shop fabricated, factory finished; vision glass; related flashings, anchorage and attachment devices, and sealant.

*************************************************************************************************************

Edit the references to include only those that apply to the edited specification section.

*************************************************************************************************************

  - REFERENCES

- Aluminum Association (AA) - Aluminum Association Designation System
For Aluminum Finishes.

- American Architectural Manufacturers Association (AAMA)

- 501.5 - Test Method for Thermal Cycling of Exterior Walls

- 501.6 - Recommended Dynamic Test Method For Determining The Seismic Drift Causing Glass Fallout From A Wall System

- SFM-1 - Aluminum Storefront and Entrance Manual

- AAMA METAL Curtain Wall, Window, Store Front and Entrance – Guide Specifications Manual

- American Society of Civil Engineers / Structural Engineering Institute – ASCE/SEI 7.

- American National Standards Institute (ANSI) A117.1 - Standard for Accessible and Usable Buildings and Facilities

- American Society of Testing and Materials (ASTM) International

- ASTM A 36 - Standard Specification for Carbon Structural Steel

- ASTM A 123 - Standard Specification for Zinc (Hot-Dip Galvanized) Coatings on Iron and Steel Products

- ASTM B 209 - Standard Specification for Aluminum and Aluminum-Alloy Sheet and Plate

- ASTM B 221 - Standard Specification for Aluminum and Aluminum-Alloy Extruded Bars, Rods, Wire, Profiles, and Tubes

- ASTM C 1184 - Standard Specification for Structural Silicone Sealants

- ASTM E 90 - Standard Test Method for Laboratory Measurement of Airborne Sound Transmission Loss of Building Partitions and Elements

- ASTM E 283 - Standard Test Method for Determining Rate of Air Leakage Through Exterior Windows, Curtain Walls, and Doors Under Specified Pressure Differences Across the Specimen

- ASTM E 330 - Standard Test Method for Structural Performance of Exterior Windows, Doors, Skylights and Curtain Walls by Uniform Static Air Pressure Difference

- ASTM E 331 - Standard Test Method for Water Penetration of Exterior Windows, Skylights, Doors, and Curtain Walls by Uniform Static Air Pressure Difference

- ASTM E 1332 - Standard Classification for Rating Outdoor-Indoor Sound Attenuation

- National Fenestration Rating Council (NFRC)

- NFRC 100 - Procedure for Determining Fenestration Product U-factors

- NFRC 200 - Procedure for Determining Fenestration Product Solar Heat Gain Coefficient and Visible Transmittance at Normal Incidence

- Procedure for Determining Fenestration Product Condensation Resistance Values

  - PERFORMANCE REQUIREMENTS

Delegated Design: Engage a qualified professional engineer, licensed in the State of New Mexico, as defined in Section 01 4000 "Quality Requirements," to design aluminum-framed entrances, storefronts and supplemental framing.

General Performance: Comply with performance requirements specified, as determined by testing of aluminum-framed entrances and storefronts representing those indicated for this Project without failure due to defective manufacture, fabrication, installation, or other defects in construction.

Aluminum-framed entrances and storefronts shall withstand movements of supporting structure, including, but not limited to, twist, column shortening, long-term creep, and deflection from uniformly distributed and concentrated live loads.

Failure also includes the following:

Thermal stresses transferring to building structure.

Glass breakage.

Noise or vibration created by wind and thermal and structural movements.

Loosening or weakening of fasteners, attachments, and other components.

Failure of operating units.

Structural Loads:

Usually indicate on Drawings design loads determined by Project's structural engineer. Verify requirements of authorities having jurisdiction. See the Evaluations for additional information.

- Wind Loads: As indicated on Drawings.

- Other Design Loads: As indicated on Drawings.

Deflection of Framing Members: At design wind pressure, as follows:

Based on Project conditions, more stringent deflection criteria than specified in "Deflection Normal to Wall Plane," "Deflection Parallel to Glazing Plane," and "Cantilever Deflection" subparagraphs below may be required; see "Seismic Performance" Article in the Evaluations. First option in "Deflection Normal to Wall Plane" Subparagraph is based on IBC requirements for framing members supporting glass. Second option is based on AAMA TIR-A11 recommendations.

Deflection Normal to Wall Plane: Limited to edge of glass in a direction perpendicular to glass plane not exceeding 1/175 of the glass edge length for each individual glazing lite or an amount that restricts edge deflection of individual glazing lites to 3/4 inch, whichever is less.

Deflection Parallel to Glazing Plane: Limited to 1/360 of clear span or 1/8 inch whichever is less.

Operable Units: Provide a minimum 1/16-inch clearance between framing members and operable units.

Retain "Cantilever Deflection" Subparagraph below for parapets and similar components.

Cantilever Deflection: Where framing members overhang an anchor point, as follows:

Perpendicular to Plane of Wall: No greater than 1/240 of clear span plus 1/4 inch for spans greater than 11 feet 8-1/4 inches or 1/175 times span, for spans of less than 11 feet 8-1/4 inches.

ASTM E 330/E 330M test method evaluates structural performance of aluminum-framed entrances and storefronts and not structural performance of contiguous construction.

Structural: Test according to ASTM E 330 as follows:

When tested at positive and negative wind-load design pressures, storefront assemblies, including entrance doors, do not evidence deflection exceeding specified limits.

When tested at 150 percent of positive and negative wind-load design pressures, storefront assemblies, including entrance doors and anchorage, do not evidence material failures, structural distress, or permanent deformation of main framing members exceeding 0.2 percent of span.

Minimum test duration according to ASTM E 330/E 330M is 10 seconds, which is historically U.S. practice.

Test Durations: As required by design wind velocity, but not less than 10 seconds.

Air Infiltration: Test according to ASTM E 283 for infiltration as follows:

Fixed Framing and Glass Area:

Retain first option in first subparagraph below for maximum air-leakage rate based on ASHRAE/IES 90.1 requirements. Static-air-pressure differential of 1.57 lbf/sq. ft. (75 Pa) in second option, equivalent to a 25-mph (40-km/h) wind, is ASHRAE/IES 90.1 minimum; air-pressure differential in third option is equivalent to a 50-mph (80-km/h) wind.

Maximum air leakage of 0.06 cfm/sq. ft. at a static-air-pressure differential of 1.57 lb/sq. ft.

Entrance Doors:

Retain "Single Doors" Subparagraph below for maximum air-leakage rate based on ASHRAE/IES 90.1.

Single Doors: Maximum air leakage of 0.5 cfm/sq. ft. at a static-air-pressure differential of 1.57 lb/sq. ft.

Retain "Water Penetration under Static Pressure" Paragraph below for static-pressure method, which is most frequently specified. For water-penetration tests, AAMA 501 states that a static-air-pressure differential of 20 percent of wind-load design pressure provides satisfactory performance in most parts of the United States. Locations where high winds and heavy rains occur simultaneously require higher test-pressure differences. Both static and dynamic testing may be required or desired for certain designs, particularly those incorporating special water-drainage features, such as rain screen walls.

Water Penetration under Static Pressure: Test according to ASTM E 331 as follows:

No evidence of water penetration through fixed glazing and framing areas, including entrance doors, when tested according to a minimum static-air-pressure differential of 20 percent of positive wind-load design pressure, but not less than 6.24 lb/sq. ft.

Retain "Seismic Performance" Paragraph below for projects requiring seismic design. Model building codes and ASCE/SEI 7 establish criteria for buildings subject to earthquake motions. Coordinate requirements with structural engineer.

Seismic Performance: Aluminum-framed entrances and storefronts shall withstand the effects of earthquake motions determined according to ASCE/SEI 7.

AAMA 501.6 in "Seismic Drift Causing Glass Fallout" Subparagraph below is a dynamic racking test method focusing on seismic safety (glass fallout).

Seismic Drift Causing Glass Fallout: Complying with criteria for passing based on building occupancy type when tested according to AAMA 501.6 at design displacement.

The IECC and ASHRAE/IES 90.1 require that all fenestration be certified and labeled by manufacturer for energy performance, based on ratings established by NFRC. NFRC ratings for storefronts are determined as a system composed of the framing, glazing, and spacer. Provide storefront manufacturer with glazing and spacer type as specified in Section 088000 "Glazing." Confirm manufacturer can meet required NFRC ratings for the system and can provide NFRC certification and labelling. Verify requirements of authorities having jurisdiction.

Energy Performance: Certify and label energy performance according to NFRC as follows:

Primary energy performance requirements usually include thermal transmittance (U-factor), solar heat gain coefficient, and air infiltration. Options in subparagraphs below are examples only; revise values to suit climate zone of building envelope as defined by the IECC. Testing for visible light transmittance (VT) is specified in Section 088000 "Glazing."

Thermal Transmittance (U-factor): Fixed glazing and framing areas as a system shall have U-factor of not more than 0.41 Btu/sq. ft. x h x deg F as determined according to NFRC 100.

Solar Heat Gain Coefficient (SHGC): Fixed glazing and framing areas as a system shall have SHGC of no greater than 0.26 as determined according to NFRC 200.

Condensation Resistance: Fixed glazing and framing areas as a system shall have an NFRC-certified condensation resistance rating of no less than 45 as determined according to NFRC 500.

Retain "Noise Reduction" Paragraph below if required for Project.

Noise Reduction: Test according to ASTM E 90, with ratings determined by ASTM E 1332, as follows.

Ratings in "Outdoor-Indoor Transmission Class" Subparagraph below represent noise reductions based on a sound spectrum with frequencies weighted to correlate with transportation sources (aircraft takeoff, freeway, and railroad passby). The higher the OITC, the more effective the noise reduction.

Outdoor-Indoor Transmission Class: Minimum 26.

Thermal Movements: Allow for thermal movements resulting from ambient and surface temperature changes.

Differential values in "Temperature Change" Subparagraph below (for aluminum in particular) are suitable for most of the United States.

Temperature Change: 120 deg. F, ambient; material surfaces.

Retain "Thermal Cycling" Subparagraph below if testing is required for Project. Standard systems are usually not tested according to AAMA 501.5. Manufacturers often rely on calculations and in-service performance to verify thermal-movement capabilities.

Thermal Cycling: No buckling; stress on glass; sealant failure; excess stress on framing, anchors, and fasteners; or reduction of performance when tested according to AAMA 501.5.

Retain "Structural-Sealant Joints" Paragraph below if Project includes two-sided structural glazing.

Structural-Sealant Joints

Retain subparagraph below if dead-load support by structural sealant is acceptable.

Designed to carry gravity loads of glazing.

Retain "Structural Sealant" Paragraph below if Project includes two-sided structural glazing.

Structural Sealant: ASTM C 1184. Capable of withstanding tensile and shear stresses imposed by structural-sealant-glazed, aluminum-framed entrances and storefronts without failing adhesively or cohesively. When tested for preconstruction adhesion and compatibility, cohesive failure of sealant shall occur before adhesive failure.

Adhesive failure occurs when sealant pulls away from substrate cleanly, leaving no sealant material behind.

Cohesive failure occurs when sealant breaks or tears within itself but does not separate from each substrate, because sealant-to-substrate bond strength exceeds sealant's internal strength.

*************************************************************************************************************

Edit submittals to include only those absolutely necessary to assure requirements and features that are important for the specific project will be met.

*************************************************************************************************************

  - ACTION SUBMITTALS

- [Submit the following in accordance with requirements of Section 01 3300, Submittal Procedures.

  - Catalog data, for each type of product specified, indicating component dimensions, describing components within assembly, anchorage and fasteners, glass, door hardware, and internal drainage details. Include data indicating percentage of recycled content for aluminum and steel components.

  - Delegated design documents: Calculations, load tables and drawings prepared by a Professional Structural Engineer, licensed as such in the State of New Mexico. Indicate framing member and supplemental framing structural and physical characteristics and dimensional limitations.

  - Shop drawings indicating system dimensions, framed opening requirements and tolerances, affected related work, and expansion and contraction joint locations and details.

  - Two samples of at least 6 square inches of aluminum material finish.

  - Manufacturer’s standard warranty and ensure forms have been completed in Owner’s name and registered with the manufacturer.]

  - QUALITY ASSURANCE

- Perform Work in accordance with AAMA SFM-1.

- Conform to requirements of ANSI A117.1.

- Use products of a single source specializing in manufacturing aluminum glazing systems with minimum of 10 successfully completed projects of similar size and scope as this project.

  - ENVIRONMENTAL REQUIREMENTS

- Do not install sealants when the temperature is less than the manufacturer’s recommended minimum temperature for installation and curing.

  - WARRANTY

- Provide manufacturer’s standard warranty that provides correction of defective Work and materials.

PART 2   PRODUCTS

  - MANUFACTURERS

- Kawneer

- United States Aluminum

# Oldcastle Building Envelope

- Tubelite, Inc.

  - MATERIALS

  - Use extruded aluminum conforming to ASTM B 221.

  - Use sheet aluminum conforming to ASTM B 209.

  - Use steel sections conforming to ASTM A 36, shaped to suit mullion sections.

  - Use stainless steel or galvanized steel fasteners.

  - Use sealants specified in Section 07 9200, Joint Sealers.

  - COMPONENTS

- For exterior applications use frame material with 2 by 4 1/2 inch nominal dimensions; thermally broken, with interior tubular section insulated from exterior; flush glazing stops; drainage holes; internal weep drainage system.

- For interior applications use frame material 1 3/4 by 4 inch nominal dimension; not thermally broken; flush glazing stops.

- For exterior applications of reinforced mullions use standard thermally broken frame with internal steel member reinforcement.

- Use doors 1 7/8 inch thick; 3 3/16 inch top rail; 3 1/2 inch vertical stiles; 7 ½ inch bottom rail; square glazing stops.

- Use flashings of aluminum with finish to match mullion sections.

  - HARDWARE

- Use manufacturer’s standard tubular shape pull that coordinates with exit device specified in Section 08 7100.

- All other hardware is specified in Section 08 7100, Door Hardware.

  - FABRICATION

- Fabricate components with minimum clearance and shim spacing around perimeter of assembly, yet enabling installation and dynamic movement of perimeter seal.

- Accurately fit and secure joints and corners. Make joints flush, hairline and weatherproof.

- Prepare components to receive anchor devices. Fabricate anchors.

- Install fasteners and attachments to be concealed from view.

- Prepare components with internal reinforcement for door hardware.

- Reinforce framing members for imposed loads.

  - FINISHES

- For exterior exposed aluminum surfaces use dark bronze anodize finish conforming to AA-M12-C22-A44, Architectural Class l.

- Use concealed steel items galvanized in accordance with ASTM A 123 to 2.0 oz/sq ft.

- Extent of finish

  - Apply factory finish to all surfaces exposed at completed assemblies.

  - Apply matching finishes to surfaces cut during fabrication, so that no natural aluminum is visible in completed assemblies, including joint edges.

  - Apply touchup materials recommended by finish manufacturer for field application to cut ends and minor damage to factory applied finish.

PART 3   EXECUTION

  - INSPECTION

- Verify dimensions, tolerances, and methods of attachment with other Work.

- Verify wall openings and adjoining air and vapor seal materials are ready to receive Work of this Section.

- Apply bituminous paint to concealed aluminum surfaces in contact with cementitious or dissimilar surfaces.

  - INSTALLATION

- Install wall system in accordance with manufacturer’s installation instructions and AAMA SFM-1.

- Attach to structure to permit sufficient adjustment to accommodate construction tolerances and other irregularities,

- Provide alignment attachments and shims to permanently fasten system to building structure.

- Align assembly plumb and level, free of warp or twist. Maintain assembly dimensional tolerances.

- Provide thermal isolation where components penetrate or disrupt building insulation.

- Install sill flashings. Turn up ends and edges, seal to adjacent Work to form water tight dam.

- Coordinate attachment and seal of perimeter air and vapor barrier materials.

- Pack fibrous insulation in shim spaces at perimeter of assembly to maintain continuity of thermal barrier.

- Set thresholds in bed of mastic and secure.

- Install hardware using templates provided.

- Install glass in accordance with Section 08 8000, using glazing method required to achieve performance criteria.

- Install perimeter sealant in accordance with Section 07 9200.

  - INSTALLATION TOLERANCES

- Maximum variation from plumb is 1/16 inch per 10 feet.

- Maximum misalignment of two adjoining members abutting in a plane is 1/32 inch.

  - ADJUSTING

- Adjust operating hardware for smooth operation.

  - CLEANING

- Remove protective material from frame members.

- Wash surfaces with a solution of mild detergent in warm water, applied with soft, clean wiping cloths. Take care to remove dirt from corners. Wipe surfaces clean and dry.

  - PROTECTION OF FINISHED WORK

- Protect finished work from damage.

end of section

******************************************************************

Do not delete the following reference information:

******************************************************************

THE FOLLOWING REFERENCE IS FOR LANL USE ONLY

This project specification is based on LANL Master Specification 08 4113 Rev. 3, dated February 22, 2017.