SECTION 09 6900

ACCESS FLOORING

****************************************************************************************************************

LANL MASTER SPECIFICATION

Word file at http://engstandards.lanl.gov

This template must be edited for each project.  In doing so, specifier must add job-specific requirements.  Brackets are used in the text to indicate designer choices or locations where text must be supplied by the designer.  Once the choice is made or text supplied, remove the brackets.  The specifications must also be edited to delete specification requirements for processes, items, or designs that are not included in the project, add specification requirements not included herein as well as deleting specifier’s notes such as these.  Additional tailoring requirements are contained in ESM Chapter 1 Section Z10 Att. F, Specifications.

To seek a variance from requirements in the specifications that are applicable, contact the Engineering Standards Manual Architectural POC. Please contact POC with suggestions for improvement as well.

When assembling a specification package, include only applicable specifications from all Divisions, especially Division 1, General requirements.

Specification was developed for ML-4 Projects.  For ML-1, 2, and 3 applications, additional requirements and independent reviews should be added if increased confidence in procurement or execution is desired; see ESM Chapter 1 Section Z10 Specifications and Quality sections.

Seismic

Specification includes requirements associated with seismic design in accordance with ASCE 7, para. 13.5.7, Access Floors.  Note that there are no exceptions/ exemptions from compliance w/ ASCE 7 Ch. 13 (for seismic design of access floors).

ASCE 7 Sect. 13.2 includes two methods for achieving compliance w/ the chapter:

1)  Project-specific design and documentation (PSDD), or

2)  Manufacturer’s certification (MC).

If Project selects 1), it has two options:  The EOR can prepare the PSDD, or responsibility for the PSDD can be delegated to the construction Subcontractor if allowed by EOR subcontract.  This template must be edited for use for one of these options.

If Project selects 2), this template must be edited to reference (in RELATED REQUIREMENTS) Section 01 8734, Seismic Qualification of Nonstructural Components (IBC), & that Section must be edited for Project specificity.

Finally, the Statement of Special Inspections (SSI) for Projects that include access floors shall at least include the anchorage inspection required by the IBC.  And, for Projects using MC, the SSI shall also include the Certificate of Compliance.  Refer to ESM Ch. 16 Sect. IBC-IP, Attachment B, Tables 1705.1.1 (special cases), 1704.5 (steel), & 1705.13 (seismic resistance) -- as applicable.

****************************************************************************************************************

GENERAL

SUMMARY

Section includes access flooring and accessories.

Related Sections:

[Section 01 4000 – Quality Requirements.]

[Section 01 8734 – Seismic Qualification of Nonstructural Components (IBC).]

[Section 05 0520 – Post Installed Concrete and Grouted-Masonry Anchors – Normal Confidence.]

[Section 05 0521 – Post Installed Concrete Anchors – High Confidence.]

[Section 05 5213 – Pipe and Tube Railings.]

[Section 07 9200 – Joint Sealants.]

[Section 09 6500 - Resilient Flooring: Finish for access flooring panels.]

[Section 09 6813 - Tile Carpeting: Finish for access flooring panels.]

[Section 26 0526 - Grounding and Bonding for Electrical Systems:  Grounding and bonding of access floor system to building grounding system.]

[Section 26 2726 – Wiring Devices]

REFERENCES

Definitions:

- ESD – Electrostatic Discharge. The transfer of electric charge between bodies at different potentials.

Reference Standards

American Association of Textile Chemists and Colorists:

AATCC TM134 – Test Method for Electrostatic Propensity of Carpets

American Society of Civil Engineers

ASCE 7 - Minimum Design Loads for Buildings and Other Structures

ASTM International:

ASTM F 150 - Standard Test Method for Electrical Resistance of Conductive and Static Dissipative Resilient Flooring

Ceilings and Interior Systems Construction Association:

CISCA – Recommended Test Procedures for Access Floors.

International Code Council:

International Building Code (IBC)

National Electrical Manufacturers Association:

NEMA LD3 - High Pressure Decorative Laminates.

National Fire Protection Association:

[NFPA 75 - Protection of Electronic Computer/Data Processing Equipment.]

NFPA 253 - Standard Method of Test for Critical Radiant Flux of Floor Covering Systems Using a Radiant Heat Energy Source.

South Coast Air Quality Management District:

SCAQMD Rule 1168 - Adhesive and Sealant Applications.

Underwriters Laboratories Inc.:

UL - Fire Resistance Directory.

COORDINATION

Coordinate location of mechanical and electrical work in underfloor cavity to prevent interference with access flooring.

Mark pedestal locations on subfloor to enable mechanical and electrical work to proceed without interfering with access-flooring pedestals installed after mechanical and electrical work.

[ADMINISTRATIVE REQUIREMENTS]

[Pre-installation Conference: Conduct conference at Project site to:

Review connection with mechanical and electrical systems.

Review and finalize construction schedule and verify availability of materials, Installer’s personnel, equipment, and facilities needed to meet the schedule and avoid delays.]

****************************************************************************************************************

Edit submittals to include only those absolutely necessary to assure the requirements and features that are important for the specific project will be met.

****************************************************************************************************************

[ACTION SUBMITTALS

Product Data: Unless providing exactly as specified, submit data for grid system, panels, and accessories; electrical resistance characteristics and ground connection requirements.

Shop Drawings: Indicate floor layout, interruptions to grid, [special sized panels,] panels requiring drilling or cut-out for services, appurtenances or interruptions, edge details, [elevation differences,] [stairs,] [ramps,] [grilles,] [registers,] [location of perforated panels,] [and] [________].

****************************************************************************************************************

Include the following paragraph for submission of physical samples for selection of finish, color, texture, and other properties unless selected during design and specified in 2.1.A below.

****************************************************************************************************************

[Samples: Submit two [____x____] inch in size of floor grid and panel, illustrating finishes and color.]

Manufacturer's Certificate: Certify products meet or exceed specified requirements. [Specified design strength and electrical resistance requirements.] [____________________.]

*************************************************************************************************************** Include the following paragraph if PSDD will be the responsibility of the Subcontractor.  Don’t include para. if PSDD will be provided by EOR, or if MC applies to Project.  Refer to author note on page 1 for details..

Professional engineer is defined in Section 01 4000 Quality Requirements.
****************************************************************************************************************

Delegated Design Submittal: For seismic design for access floor.

Include design calculations and analysis data, signed and sealed by the professional engineer, registered in the State of New Mexico, responsible for their preparation.

Manufacturer's Installation Instructions: Submit special procedures, perimeter conditions requiring special attention, and [________].

Field quality-control reports.

************************************************************************************************************

Include only sustainable design submittals that are appropriate for the project’s sustainable design goals, if any.

************************************************************************************************************

[SUSTAINABLE DESIGN SUBMITTALS

Manufacturer's Certificate: Certify products meet or exceed specified sustainable design requirements.

****************************************************************************************************************

Edit material certifications list to suit products specified in this section and Project sustainable design requirements.

****************************************************************************************************************

      - Materials Resources Certificates:

  - Certify source and origin for [salvaged] [and] [reused] products.

  - Certify recycled material content for recycled content products.

  - Certify source for local and regional materials and distance from Project site.

      - Indoor Air Quality Certificates: Certify volatile organic compound content for each interior [adhesive] [and] [sealant] and related primer.]

[CLOSEOUT SUBMITTALS

Operation and Maintenance Data

Warranty Documentation

Project Records Documentation]

Extra Stock Materials

Furnish [four] [________] of each size of floor panel.

Furnish [four] [________] spare pedestals [and [four] [________] stringers].

Panel Lifting Devices: [One] [Two] [________], [of manufacturer's standard type.] [____________________.]]

QUALITY ASSURANCE

Qualifications

      - Manufacturer: Company specializing in manufacturing Products specified in this section with minimum three years [documented] experience.

      - Installer: Company specializing in performing Work of this section [with minimum [________] years [documented] experience] [approved by manufacturer].

    - Source Limitations:  Obtain access floor system through one source from a single manufacturer.

    - Provide floor panels that are clearly and permanently marked on their underside with panel type and concentrated load rating.

    - [Mockups:  Build mockups to verify selections made under sample submittals and to demonstrate aesthetic effects and set quality standards for materials and execution.

      - Build mockup of typical access flooring assembly as shown on Drawings. Size to be an area no less that [five] [_______] floor panels in length by [five] [_______] floor panels in width.

      - Approved mockups may become part of the completed Work if undisturbed up to time of Substantial Completion.]

SITE CONDITIONS

Do not install access flooring until spaces are enclosed, [subfloor has been sealed,] ambient temperature is between 40 and 90 deg F, and relative humidity is not more than 70 percent.

WARRANTY

Provide manufacturer’s standard, all inclusive warranty.

PRODUCTS

ACCESS FLOORING

Manufacturers:

[Access Flooring Supplies Inc.] Model [________], Color [_______].

[Bravo Access Floors] Model [________], Color [_______].

[Tate Access Floors, Inc.] Model [________], Color [_______].

[Hayworth, Inc.] Model [________], Color [________].

[Lindner USA, Inc.] Model [_______], Color [_______].

[____________________] Model [________], Color [_______].

DESCRIPTION

System: [Stringerless] [Panel lock] [Snap-on grid] [Clamped stringer] [Rigid grid] system. Access flooring system to achieve finished floor elevation of [________] inches nominal height above building structural floor. Floor Panel Size: 24 x 24 inches.

[Regulatory Requirements: Fabricate and install access flooring to comply with NFPA 75 requirements for raised flooring.]

Sustainability Characteristics

Provide access floor system with minimum 20 percent recycled content and minimum 10 percent post consumer content.

Adhesives: Maximum volatile organic compound content in accordance with SCAQMD Rule 1168.

PERFORMANCE REQUIREMENTS

***************************************************************************************************************

Edit the following Para.in accordance w/ related edits made in PART 1, & the following:

- Retain only subpara. 1 if the access floor (AF) must be designed w/ a Component Importance Factor, Ip, = 1.5 (i.e., it’s a Designated Seismic System, or DSS).

  - Retain the text in the 1st set of brackets if PSDD applies & will be provided by EOR.

  - Retain the text in the 2nd set of brackets if PSDD applies & will be the responsibility of the Subcontractor.

  - Retain the text in the 3rd set of brackets if MC applies to Project.

- Retain only subpara. 2 if AF isn’t a DSS, & edit brackets as described for subpara. 1 (above).

In short, the goals of these performance requirements are as follows:

- DSS:  The extent of damage to the AF caused by the design-basis earthquake shall not result in the loss of functionality/ operability of the facility, or “AF-ed room” within it.   What this means is the AF doesn’t collapse &, as applicable, “services” that are on, in or under the AF (e.g., computers, cabling, HVAC, etc.) won’t be rendered inoperable/ non-functional as a result of AF failure/ deformation(s).

- Non-DSS:  The extent of damage to the AF caused by the design-basis earthquake can be severe up to, but not including, collapse.

***************************************************************************************************************

Seismic Performance:

The access floor is a Designated Seismic System and, as such, it shall withstand the effects of earthquake motions as represented by the [seismic hazard indicated on the drawings] [the forces derived from the specified criteria] [design basis earthquake in Section 01 8734].

The term “withstand” means “the access floor will not sustain damage that would result in it losing functionality, to include failure/ deformation to the extent that nonstructural components that rely on it for support or protection lose functionality/ operability, when subjected to the seismic [hazard indicated on the drawings] [forces derived from the specified criteria].”

The access floor shall withstand the effects of earthquake motions as represented by the [seismic hazard indicated on the drawings] [the forces derived from the specified criteria] [design basis earthquake in Section 01 8734].

The term “withstand” means “no part of the access floor collapses subjected to the [seismic hazard indicated on the drawings] [derived from the specified criteria].”

**************************************************************************************************************** Loads in the following paragraph below are examples only; revise to suit Project. Verify that loading requirements coordinate with each other and match the products specified. If needed, revise the text. For more details on the various loads & amounts, see the AIA MasterSpec Evaluations doc (i.e., 096000_sd.pdf).
****************************************************************************************************************

Structural Performance:  Provide access flooring capable of complying with the following performance requirements according to testing procedures in CISCA:

**************************************************************************************************************** The bracketed loads indicated below represent common standard load ratings of the listed manufacturers. If the specified manufacturer’s standard product, as determined by the Project Structural Engineer of Record the Project, does not meet the Project requirements for these types of loads, provide the required load ratings in the empty brackets.
****************************************************************************************************************

Concentrated Loads:  [900] [1000] [1250] [1500] [2000] [_____] lbf, with the following deflection and  permanent set:

**************************************************************************************************************** Insert requirements for bottom-surface deflection if required.
****************************************************************************************************************

Top-Surface Deflection: [0.10] [_____] inch.

Permanent Set:  [0.10] [____] inch.

Ultimate Loads:  [1800] [2000] [2500] [3000] [4000] [_____] lbf.

**************************************************************************************************************** Coordinate loads specified in subparagraph below with loads specified in "Structural Performance" Paragraph above to avoid failure in panels with insufficient concentrated- and ultimate-load capability.
****************************************************************************************************************

Rolling Loads:  With local or overall deformation not to exceed 0.040 inch.

**************************************************************************************************************** 1st subparagraph below simulates low-repetition, small-wheel loads similar to equipment move-in on dollies; 2nd subparagraph below simulates high-repetition, large-wheel loads similar to recurring office cart traffic.
****************************************************************************************************************

        - CISCA Wheel 1:  10 passes at [400] [500] [600] [800] [1000] [1200] [1250] [2000] [_____] lbf.

        - CISCA Wheel 2:  10,000 passes at [400] [500] [600] [800] [1000] [1250] {1750] [2000] [_____] lbf.

Stringer Load Testing:  [75] [225] [350] [450] [____] lbf at center of span with a permanent set not to exceed 0.010 inch.

Pedestal Axial Load Test:  [5000] [6000] [____] lbf.

**************************************************************************************************************** The lateral-load resistance of pedestals is typically determined by the CISCA pedestal-overturning-moment test, & how the pedestal is attached to the supporting floor slab has a significant effect on it.  Attachment methods include adhered (via adhesives) and mechanically fastened.  1000 in-lb is an “industry-standard value” for adhered pedestals; however, it’s possible that more capacity will be required by the seismic design.  Coordinate with manufacturer, &/or structural EOR, as necessary.  There are author notes related to this topic in the subsequent “Accessories” & “Installation” Articles.
****************************************************************************************************************

Pedestal Overturning Moment Test:  [1000 lbf x inches] [________],

Uniform Load Test: [200] [250] [300] [400] [500] [_______] lbf/sq. ft. with a maximum top-surface deflection not to exceed 0.040 inch and a permanent set not to exceed 0.010 inch.

Drop Impact Load Test: [75] [100] [125] [150] [175] [Insert value] lbf

[ESD Control Properties:  Provide floor coverings with ESD control properties indicated as determined by testing identical products per test method indicated by an independent testing and inspection agency]

[Static Dissipative Floor Covering Properties:

Electrical Resistance:  Test per ASTM F 150 with 100V applied voltage.

Average greater than 1 megohm and less than or equal to 1000 megohms when test specimens are tested surface to ground.

Average greater than 1 megohm and less than or equal to 1000 megohms when installed floor coverings are tested surface to ground.

Static Generation:  Less than [300] [_____]V when tested per AATCC-TM134 at 20 percent relative humidity with conductive footwear.

Static Decay:  5000 to 0V in less than [0.25] [____] seconds.]

[Static Conductive Floor Covering Properties:

Electrical Resistance:  Test per ASTM F150 with 500V applied voltage.

Average greater than 25,000 ohms and less than 1 megohm when test specimens and installed floor coverings are tested surface to surface (point to point).

Average no less than 25,000 ohms with no single measurement less than 10,000 ohms when installed floor coverings are tested surface to ground.

Static Generation:  Less than [100] [____]V when tested per AATCC-TM134 at 20 percent relative humidity with conductive footwear.

Static Decay:  5000 to 0V in less than [0.03] [0.01] [____] seconds.]

[Antistatic Floor Covering Properties:

Electrical Resistance:  Average greater than 25,000 ohms and less than 1,000 megohm when test specimens and installed floor coverings are tested surface to surface (point to point).

Static Generation:  Less than [100] [____]V when tested per AATCC-TM134 at 20 percent relative humidity with conductive footwear.]

[Panel to Understructure Resistance:  Not more than 10 ohms as measured without floor coverings.]

************************************************************************************************************

Retain the following Article if PSDD will be the responsibility of the Subcontractor.  Don’t retain it if PSDD will be provided by EOR, or if MC applies to Project.  
*************************************************************************************************************

SEISMIC DESIGN CRITERIA

Delegated Design: Engage a qualified professional engineer, as defined in Section 01 4000 Quality Requirements, to prepare the seismic design of/ for the access flooring.

************************************************************************************************************

In the following Para., regarding the “special-access-floors option (in the 1st set of brackets),” per ASCE 7 para. C13.5.7.2, “Special access floors are designed for smaller lateral forces [given their larger Rp value], and their use is encouraged at facilities with higher nonstructural performance objectives.”

Ref. ESM Ch. 5 Sect. II, Earthquake Loads for the source of the criteria/ data listed in the subparas, & for editing of them.  
*************************************************************************************************************

Access flooring shall [comply with requirements for “special access floors” per ASCE 7 paragraph 13.5.7.2 and shall] be designed in accordance with the aforementioned “Seismic Performance” requirements, the loads derived from the following parameters/ data, and including loads imposed on the access flooring by items and equipment installed on the access flooring.

Seismic Loading:

        - IBC Risk Category:  [I] [II] [III] [IV].

        - IBC Site Class:  D

        - IBC Design Spectral Response Acceleration Parameters:  SDS = [0.75] [____]g, SD1 = [0.64] [____]g, T0 = 0.1 sec.

        - IBC Seismic Design Category:  D

        - ASCE 7 Component Importance Factor, Ip:  [1.0] [1.5].

************************************************************************************************************

In the following subpara. the default value of Rp is 1.5 because, as indicated in the previous author note, 2.5 is applicable only to “special access floors.”     
*************************************************************************************************************

        - ASCE 7 Component Response Modification Factor, Rp: 1.5 [2.5]

        - ASCE 7 Component Amplification Factor, ap: 1.0.

MATERIALS

Pedestals: [Steel] [Aluminum] with flat bottom base plate, threaded supporting rod, [vibration proof] lock nut to permit [1-1/2] [________] inch adjustment, [galvanized] [manufacturer's standard] finish.

****************************************************************************************************************

Include the following paragraph only when stringer system is specified.

****************************************************************************************************************

Frame Grid Stringers: [Continuous] [Removable] type, consisting of [steel] [aluminum] channels, box, or tee sections.

Floor Panels:

Die formed [galvanized] steel top and bottom plates; steel reinforcement stiffeners.

****** [OR] ******

Cast aluminum, with ribbed stiffeners.

****** [OR] ******

Sheet steel plates, composite [lightweight concrete] [gypsum] [________] core.

Panel Edge: [Vinyl trim] [________], [slip-on type.] [Mechanically locked to panels.]

Floor Panel Finish Adhesive: [Moisture resistant] [Waterproof] [Electrically conductive] type recommended by floor finish manufacturer. Maximum volatile organic compound content in accordance with SCAQMD Rule 1168.

Perforated Floor Panels: Same material, size, and construction as floor panels [with slide dampers for controlled air circulation].

FABRICATION TOLERANCES

****************************************************************************************************************

Reference product manufacturer's tolerances prior to editing the following paragraphs.

****************************************************************************************************************

Floor Panel Flatness: Plus or minus [0.02] [________] inch in any direction.

Floor Panel Width or Length from Specified Size: Plus or minus [0.02] [________] inch.

Floor Panel Squareness: Plus or minus [0.03] [________] inch difference between opposite diagonal dimensions.

FINISHES

    - Floor Panel Finish:

Vinyl tile [, static conductive type] [1/8] [________] inch thick, as specified in Section 09 6500 Resilient Flooring [________]; [________] color [as selected].

****** [OR] ******

Melamine phenolic laminate, NEMA LD3, Type HW120, [________] inch thick; [________] color [as selected].

****** [OR] ******

Carpet tile, as specified in Section 09 6813 Tile Carpeting [________]; [________] color [as selected].

Exposed Metal Surfaces: [Baked enamel finish] [________]; [________] color [as selected].

Fascia Panel: [Baked enamel finish] [________]; [________] color [as selected].

[Ramp] [and] [Stair Tread] Surface: [Sheet rubber] [________]; [________] color [as selected].

ACCESSORIES

****************************************************************************************************************

Retain "Adhesives" or "Post-Installed Anchors" Paragraph below. ASCE 7 prohibits the use of adhesives in the transmission of seismic loads for Special Access Floors (i.e., Rp = 2.5).  Otherwise (i.e., Rp = 1.5), installations are possible with either adhesives or post-installed anchors, depending on Project conditions. Structural EOR must verify anchor requirements with access-flooring manufacturer & coordinate with "Installation" Article. Insert more detailed requirement for type of material in "Adhesives" Subparagraph if necessary.

****************************************************************************************************************

Adhesives: Manufacturer's standard adhesive for bonding pedestal bases to subfloor.

****************************************************************************************************************

Post-installed anchors shall be specified in the appropriate Division-05 Section

****************************************************************************************************************

Post-Installed Anchors:  For anchoring pedestal bases to subfloor, provide anchors indicated and specified in Section 05 0520 [05 0521].

[Cutouts:  Provide cutouts in floor panels for cable penetrations and service outlets. Provide reinforcement or additional support, if needed, to make panels with cutouts comply with specified performance requirements.

Number, Size, Shape, and Location:  As shown on Drawings.

Trim edge of cutouts with manufacturer’s standard plastic molding.

Fit cutouts with manufacturer’s standard grommets in sizes indicated or, if size of cutouts exceeds maximum grommet size available, trim edge of cutouts with manufacturer’s standard plastic molding having tapered top flange. [Furnish removable covers for grommets.]

Provide foam rubber pads for sealing annular space formed in cutouts by cables.]

[Floor Grilles:  Standard load-bearing grilles formed from aluminum to produce removable one-piece unit precisely fitted in factory prepared openings of standard field panels, [with adjustable/removable] [without] dampers and complying with the following requirements.

Air Distribution Characteristics:  468 cfm at 0.10-inch wg static pressure.

Structural Performance:  Capable of supporting a 1000-lbf concentrated load.

Fire Test Response Characteristics:  Classified 94V-0 per UL 94.

[Air Grilles:  [Galvanized sheet steel] [Extruded aluminum]; [______] inch blade size; with [straight] [deflecting] vanes and shut-off damper; [with integral fire damper].]

[Cavity Dividers:  Provide manufacturer’s standard metal dividers located where indicated to divide underfloor cavities.]

[Vertical Closures (Fascia):  Where underfloor cavity is not enclosed by abutting walls or other construction, provide metal closure plates with [manufacturer’s standard] [______] finish.]

[Ramps:  Manufacturer’s standard ramp construction of width and slope indicated but not steeper than 1:12, with raised disc or textured rubber or vinyl floor coverings, and of same materials, performance, and construction requirements as access flooring.]

[Steps:  Provide steps of size and arrangement indicated with floor coverings to match access flooring. Apply nonslip aluminum nosing to treads, unless otherwise indicated.]

[Railings:  Standard extruded aluminum railings, at ramps and open sided perimeter of access flooring where indicated. Include handrail, intermediate rails, posts, brackets, end caps, wall return, wall and floor flanges, plates, and anchorages where required. Railings shall comply with structural performance requirements specified in Specification Section 05 5213 Pipe and Tube Railings.]

Panel Lifting Device:  Manufacturer’s standard portable lifting device of type required for specified panels. Provide [_____] lifting device[s] per room of each type required.

Perimeter Support:  Where indicated, provide manufacturer’s standard method for supporting panel edge and forming transition between access flooring and adjoining floor coverings at same level as access flooring.

Electrostatic Grounding Connectors:  Solid copper.

EXECUTION

EXAMINATION

******************************************************************************************************

Coordinate requirements specified in other Sections for subfloor construction and tolerances to ensure that they are appropriate for pedestal installation.

******************************************************************************************************

Examine substrates, with Installer and manufacturer’s representative present, for compliance with requirements for installation tolerances and other conditions affecting performance of work.

Verify that substrates comply with tolerances and other requirements specified in other Sections and that substrates are free of cracks, ridges, depressions, scale, foreign deposits and debris that might interfere with [adhesive] [post-installed anchor] attachment of pedestals.

Proceed with installation only after unsatisfactory conditions have been corrected.

PREPARATION

Lay out floor panel installation to keep the number of cut panels at floor perimeter to a minimum. Avoid using panels cut to less than 6 inches in any direction.

Locate each pedestal, complete any necessary subfloor preparation, and vacuum clean subfloor to remove dust, dirt, and construction debris before beginning installation.

INSTALLATION

Install access flooring system and accessories under supervision of access-flooring manufacturer’s authorized representative to produce a rigid, firm installation that complies with performance requirements and is free of instability, rocking, rattles, and squeaks.

******************************************************************************************************

Retain "Adhesive Attachment of Pedestals" or "Mechanical Attachment of Pedestals" paragraph below. Retain 1st paragraph for more common adhesive attachment of pedestals. Retain second paragraph if bolted attachment of pedestal bases is required for Special Access Floors or where increased rigidity is needed. Coordinate with "Accessories" Article.

******************************************************************************************************

Adhesive Attachment of Pedestals: Set pedestals in adhesive, according to access-flooring manufacturer’s written instructions, to provide full bearing of pedestal base on subfloor; and as required to meet seismic design requirements.

Mechanical Attachment of Pedestals: Attach pedestals to subfloor with post-installed mechanical anchors as required to meet seismic design requirements.

Adjust pedestals to permit top of installed panels to be set flat, level, and to proper height.

Stringer Systems: Secure stringers to pedestal heads according to access-flooring manufacturer’s written instructions.

Install additional pedestals where grid pattern is interrupted by room appurtenances or at cut-outs.

Install flooring panels securely in place, properly seated with panel edges flush. Do not force panels into place. [For carpeted panels, install panels with carpet pile in same direction.]

Scribe perimeter panels to provide a close fit with adjoining construction with no voids greater than 1/8 inch where panels abut vertical surfaces. Finish field cut floor panels with edge trim.

Cut and trim access flooring and perform other dirt and debris producing activities at a remote location or as required to prevent contamination of subfloor under access flooring already installed.

Ground flooring system as recommended by manufacturer and as needed to comply with performance requirements for electrical resistance of floor coverings.

Underfloor Dividers: Scribe and install underfloor cavity dividers to closely fit against subfloor surfaces, and seal with mastic.

Closures:  Scribe vertical closures to closely fit against subfloor and adjacent finished floor surfaces. Set in mastic and seal to maintain plenum effect within underfloor cavity.

Clean dust, dirt, and construction debris caused by floor installation, and vacuum subfloor area as installation of floor panels proceeds.

Install [grilles,] [perforated panels,] [and] [________] [as indicated on [Drawings.] [shop drawings.] [where directed.]

****************************************************************************************************************

Include the following paragraph to ensure reasonable quantity of hole cuts are included in Subcontract. Delete this paragraph when inapplicable.

****************************************************************************************************************

Cut [ten] [________] holes in floor panels to accommodate specified equipment. Provide cable cut-out protection.

Install floor, [ramp,] [and] [stairs] with edge trim and end closures. [Install lateral braces at stair edges and other locations where pedestals are not braced.]

***************************************************************************************************************

Coordinate the following paragraph with appropriate electrical sections.

***************************************************************************************************************

[Provide positive electrical earth grounding of entire floor assembly in accordance with [NFPA 75.] [____________________.]]

Extend railing posts through floor panels to structural floor; secure to flange fittings anchored to structural floor.

Brace posts in position at floor panels with floor collar retainers.

Secure railings at walls with flanged fittings anchored to walls.

Electrically ground railings to [floor system.] [building grounding system.]

ERECTION TOLERANCES

Install access flooring without change in elevation between adjacent panels and within the following tolerances:

Plus or minus [1/16] [1/8] [________] inch in any 10-ft. distance.

Plus or minus [1/8] [1/4] [_____] inch from a level plane over entire access flooring area.

field quality control

*************************************************************************************************************

The primary purpose of the Article is to alert the Subcontractor that he/she is responsible for quality control (QC) & that, in addition to QC, the access floor is subject to the quality assurance (QA) indicated in the Project’s Statement of Special Inspections.
*************************************************************************************************************

    - Inspection Agency: Engage a qualified inspection agency to perform inspections.

    - Perform inspections during the installation of access flooring as necessary to ensure that the applicable provisions of ASCE 7 are met.

    - Prepare an inspection report.

    - Access floors will be considered defective if they do not pass the Special Inspection indicated in the Project’s Statement of Special Inspections.

ADJUSTING, CLEANING, AND PROTECTION

Prohibit traffic on access flooring for 24 hours and removal of floor panels for [72] [____] hours after installation to allow pedestal adhesive to set.

After completing installation, vacuum clean access flooring and cover with continuous sheets of reinforced paper or plastic. Maintain protective covering until time of Substantial Completion.

Replace access flooring panels that are stained, scratched, or otherwise damaged or that do not comply with specified requirements.

[SCHEDULES]

****************************************************************************************************************

Include schedule when differing types of floor panels, finishes, fascia or ramp components, railings, or accessories are required. Consider the following examples when developing access flooring schedule.

[Computer Room 308: 24 x 24 inch floor panel, 18 inch above floor slab, ramp, fascia panels, tubular aluminum hand railing; plastic laminate floor panel finish.]

[Printer Room 309: 30 x 30 inch floor panels, 6 inches above floor slab; vinyl finish; two stair risers at door to Room 308.]

****************************************************************************************************************

END OF SECTION

************************************************************

Do not delete the following reference information:

************************************************************

THE FOLLOWING REFERENCE IS FOR LANL USE ONLY

This Project specification is based on LANL Master Specification 09 6900 Rev. 3, dated March 28, 2017.