Section 10 4400 
Fire Protection Specialties

  - *************************************************************************************************************

    - LANL MASTER SPECIFICATION Section

Rev. 4 Summary of Changes: Edited and updated as required for import into SpecLink.

      - NOTE TO SPECIFIER ON USAGE IN SPECLINK: Activate the Section by turning on Seq #0000, followed by activating paragraphs in PART 1, Article SECTION INCLUDES. This will activate related articles, paras/subparas in the rest of the Section (i.e., PART 1 activates articles and paras/subparas in PARTS 2 and 3). If there are choice fields to edit the entire Section (typically in this first author note or beginning of the Section), make selections at those locations, which will filter through the remaining Section. All Articles, paragraphs and subparagraphs must be activated sequentially from top to bottom, unless noted otherwise.

      - This template must be edited for each project. In doing so, specifier must add job-specific requirements. Selections and choice fields are used to indicate designer choices or locations where text must be supplied by the designer. The section must also be edited to remove requirements for processes, items, or designs that are not included in the project.

      - To seek a variance from applicable requirements in this Section, contact the Engineering Standards Manual (ESM) Architectural/Fire POC  (LANL access only). Please contact POC with suggestions for improvement as well. LANL personnel should submit here: Suggested Change or Request Clarification; subcontractors via email to engstandards@lanl.gov.

      - When assembling a specification package, include applicable specification sections from all Divisions, especially Division 1, General Requirements.

      - Section is developed for ML-4 projects.  For ML-1, 2, and 3 applications, additional requirements and independent reviews should be added if increased confidence in procurement or execution is desired; see LANL ESM Chapter 1 - General, Section Z10 Specifications and Quality sections.

      - ==========================================================

      - The component importance factor, Ip, for fire extinguishers is typically 1.0 unless required for life-safety purposes, in which case it is 1.5. The fire protection engineer is responsible to coordinate with the structural engineer on seismic anchorage/fastener requirements for non-structural components in accordance with ASCE 7, Chapter 13, as applicable.

  - *************************************************************************************************************

PART 1 - GENERAL

SECTION INCLUDES

      - ***************************************************************************************

      - The following paragraphs are designer choices based on project-specific conditions.

      - ***************************************************************************************

Fire extinguishers.

Fire extinguisher cabinets.

Accessories.

RELATED REQUIREMENTs

Section << 01 2500 - Substitution Procedures>>

Section << 01 7823 - Operation and Maintenance Data>>

REFERENCE STANDARDS

ABA Standards - ABA Accessibility Standards.

ASTM E814 - Standard Test Method for Fire Tests of Penetration Firestop Systems.

FM (AG) - FM Approval Guide.

NFPA 10 - Standard for Portable Fire Extinguishers.

UL (DIR) - Online Certifications Directory.

ACTION SUBMITTALS

Product Data: Provide extinguisher operational features, extinguisher ratings and classifications, color and finish, and anchorage details.

      - ***************************************************************************************

      - Retain Shop Drawings submittal if fire extinguisher or cabinet locations and types are not provided in the engineering drawings.

      - ***************************************************************************************

Shop Drawings: Indicate locations of cabinets, cabinet physical dimensions, rough-in measurements for recessed cabinets; locations, weights and types of individual fire extinguishers; mounting measurements for wall bracket; and accessories required for complete installation.

INFORMATIONAL SUBMITTALS

Manufacturer's Installation Instructions: Indicate special criteria and wall opening coordination requirements.

At Closeout

Operation and Maintenance data.

Manufacturer’s warranty.

FIELD CONDITIONS

The space shall be dried-in and conditioned prior to installation of permanent fire extinguishers.  Permanent fire extinguishers shall not be used during construction.

WARRANTY

The manufacturer shall provide, at no additional cost, a standard parts warranty in which manufacturer agrees to repair or replace fire extinguishers that fail in materials or workmanship within the specified warranty period.

Failures include but are not limited to:

Failure of <<NFPA 10>> hydrostatic test, when the required test falls within the warranty period.

Faulty operation of release levers or valves.

PART 2 - PRODUCTS

MANUFACTURERS

Fire Extinguishers

Activar Construction Products Group, Inc. - JL Industries.

Ansul, a Tyco Business.

Brooks Equipment.

Kidde, a unit of United Technologies Corp.

Getz Fire Equipment Company.

Nystrom, Inc.

Oval Brand Fire Products.

Potter-Roemer.

Pyro-Chem, a Tyco Business.

Fire Extinguisher Cabinets and Accessories:

        - ******************************************************************************

        - Retain the following subparagraphs as applicable.

        - ******************************************************************************

Activar Construction Products Group, Inc. - JL Industries ​<< Ambassador Series;  Academy Series;  Cosmopolitan Series;  Embassy Series;  Panorama Series;  Clear Vu Series; or  Security Series>>​.

Kidde, a unit of United Technologies Corp << Surface-mounted;  semi-recessed; or  keyed semi-recessed>>.

Larsen's Manufacturing Co ​​<< Specifier to select from website>>​​.

Nystrom, Inc. ​<< Alpine;  Palisade;  Summit; or  Ridge>>​.

Oval Brand Fire Products ​<< CRST;  CRSS;  CSST; or  CSSS>>​.

Potter-Roemer ​​<< Specifier to select from website>>​​.

Substitutions: ​<< Alternate products may be accepted, follow Section 01 2500 – Substitution Procedures; or  Not permitted – No Substitutions>>​​.

      - ***************************************************************************************

      - The following three Articles are designer choices based on project-specific conditions.

      - ***************************************************************************************

FIRE EXTINGUISHERS

Fire Extinguishers - General: Comply with product requirements of <<NFPA 10>>.

Provide extinguishers labeled by ​<< UL (DIR); or  FM (AG)>>​ for purpose specified and acceptable to the LANL Fire Marshal (Authority Having Jurisdiction).

      - ***************************************************************************************

      - For each of the three subparagraphs below, retain content as applicable to project.

      - Designer to include "Class" and "Size" content OR "Size and classification as scheduled."

      - ***************************************************************************************

<< Multipurpose Dry Chemical; or  Halogenated Agents>> Type Fire Extinguishers: << Carbon steel; or  Aluminum>> tank, with pressure gauge.

Stored Pressure Operated: << Deep Drawn; or  _______>>.

Class: << ABC;  BC;  Purple K; or  _______>> type.

Size: << 2.5 pound;  2.6 pound;  5 pound;  10 pound;  30 pound; or  20 pound>>.

Size and classification as scheduled.

Finish: ​<< Baked polyester powder coat ____ color;  Polished chrome; or  ___>>​.

Temperature range: << Minus 40;  Minus 65; or  _______>> degrees Fahrenheit to << _______; or  120>>​ degrees Fahrenheit.

Wet Chemical Type Fire Extinguishers: Stainless steel tank, with pressure gauge.

Class: K - type.

Size: << 1.6; or  _______>>  gallons.

Size and classification as scheduled.

Finish: Polished stainless steel.

Temperature range: << Minus 20;  32; or  _______>> degrees Fahrenheit to << 120; or  _______>> degrees Fahrenheit.

FE-36 Clean Agent Type Fire Extinguishers: << Stainless steel;  Carbon steel; or  _______>> tank, with pressure gauge.

Class: << ABC;  BC; or  _______>> type.

Size: << 2.5;  5;  9;  10;  13; or  _______>> pound.

Size and classification as scheduled.

Finish: << Baked polyester powder coat ____ color;  Polished chrome;  No. 4 brushed Satin chrome; or  ___>>

Temperature Range: ​<< Minus 40; or  _______>>​ degrees Fahrenheit to ​<< 120; or  _______>>​ degrees Fahrenheit.

FIRE EXTINGUISHER CABINETS

Fire Rating: Listed and labeled in accordance with <<ASTM E814>> requirements for fire resistance rating of walls where being installed.

      - ***************************************************************************************

      - Retain either or both of the following two Cabinet Construction options as applicable to the project.

      - ***************************************************************************************

Cabinet Construction: Non-fire rated.

        - ******************************************************************************

        - Retain only one of the following two subparagraphs.

        - ******************************************************************************

Formed ​<< primed;  galvanized;  stainless; or  _______>>​ steel sheet; ​<< 0.036; or  _______>>​ inch thick base metal.

        - *** OR ***

Formed aluminum; ​<< _______>>​ inch thick base metal.

Fire Rated Cabinet Construction: << One-hour fire rated;  Two-hour fire rated; or  _______>>.

Steel; << double wall;  outer and inner boxes; or  _______>> with << 5/8; or  _______>> inch thick fire barrier material.

Cabinet Configuration: << Recessed;  Semi-recessed; or  Surface mounted>> type.

Size to accommodate accessories.

Exterior nominal dimensions of << _______>> inch wide by << _______>> inch high by << _______>> inch deep.

Trimless type.

Trim: << Flat square edge;  Flat rolled edge; or  _______>> with << _______>>  inch wide face.

Projected Trim: Returned to wall surface, with << _______>> inch projection, and << _______>> inch wide face.

Provide cabinet enclosure with right angle inside corners and seams, and with formed perimeter trim​​<< and door stiles; or  _______>>​​.

Door: << 0.036; or  _______>> inch metal thickness, reinforced for flatness and rigidity << with nylon catch;  with roller type catch;  with lock and breakable window access; or  _______>>. Hinge doors for 180 degree opening with << two butt hinges;  continuous piano hinge; or  _______>>.

      - ***************************************************************************************

      - Retain only one of the following two Door Glazing options.

      - ***************************************************************************************

Door Glazing: << Float;  Tempered;  Heat strengthened; or  _______>> glass, clear, << 1/8; or  _______>> inch thick, and set in resilient channel glazing gasket.

      - *** OR ***

Door Glazing: ​<< Acrylic;  Polycarbonate; or  _______>>​ plastic, clear, ​<< 1/8; or  _______>>​ inch thick, ​<< flat;  full view bubble; or  _______>>​ shape and set in resilient channel glazing gasket.

Cabinet Mounting Hardware: Appropriate to cabinet, with pre-drilled holes for placement of anchors.

Fabrication: Weld, fill, and grind components smooth.

Finish of Cabinet Exterior Trim and Door: ​<< Primed for field paint finish;  Polished chrome;  Satin chrome;  No. 4 - Brushed stainless steel;  Red enamel;  Red baked enamel;  Baked enamel, ___ color;  Baked enamel, color as selected;  Anodized to _______ color;  Anodized to color as selected; or  _______>>​.

Finish of Cabinet Interior: << White colored enamel;  _______ colored enamel; or  _______>>.

ACCESSORIES

Extinguisher Brackets: Formed steel, << chrome-plated;  galvanized and enamel finished; or  _______>>.

<< Cabinet Signage; or  Graphic Identification>>​: << _______>>.

Lettering: “FIRE EXTINGUISHER” decal, or vinyl self-adhering, pre-spaced black lettering.

PART 3 - EXECUTION

EXAMINATION

Verify existing conditions before starting work.

Verify rough openings for cabinet are correctly sized and located.

INSTALLATION

Install fire extinguishers and cabinets in accordance with manufacturer's instructions, <<NFPA 10>>, and <<ABA Standards>>.

      - ***************************************************************************************

      - Per NFPA 10 and ABA, operable parts of fire extinguisher shall be 42 inches maximum from finished floor for extinguishers weighing more than 40 lbs and 48 inches maximum from finished floor for extinguishers weighing 40 lbs or less.

      - ***************************************************************************************

Install cabinets plumb and level​<< in wall openings; or  None - N/A>>​, ​<< 42; or  _______>>​ inches from finished floor to ​<< inside bottom of cabinet; or  _______>>​.

Secure fire extinguishers and cabinets rigidly in place to ensure position retention during a seismic event.

Place extinguishers<< and accessories; or  None - N/A>><< in cabinets; and  on wall brackets>>.

Position cabinet signage at << _______>>.

MAINTENANCE

See Section << 01 7823 - Operation and Maintenance Data>>​, for additional requirements relating to maintenance service.

      - ***************************************************************************************

      - Provide fire extinguisher schedule in this specification section or on the engineering drawing. Information to be included in the schedule is noted below. If schedule is not included in this specification section, omit the following Article on Fire Extinguisher Schedule.

      - ***************************************************************************************

FIRE EXTINGUISHER SCHEDULE

Corridors:  Dry Chemical Type:

Class: << ABC;  BC; or  _______>>

Size: << _______>>

Cabinet: << _______>>

Other: << _______>>

Common Areas:  Dry Chemical Type:

Class: << ABC;  BC; or  _______>>

Size: << _______>>.

Cabinet: << _______>>.

Other: << _______>>.

Kitchens:  Dry Chemical type:

Class: << Purple K; or  _______>>

Size: << _______>>.

Cabinet: << _______>>.

Other: << _______>>.

Kitchens:  Wet Chemical type:

Class: << K; or  _______>>.

Size: << _______>>.

Cabinet: << _______>>.

Other: << _______>>.

Computer Room: FE-36 Clean Agent Type:

Class: << ABC;  BC; or  _______>>

Size: << _______>>.

Cabinet: << _______>>.

Other: << _______>>.

END OF SECTION

    - **********************************************************************************************

      - Do not omit the following reference information:

    - **********************************************************************************************

THE FOLLOWING STATEMENT IS FOR LANL USE ONLY

THIS PROJECT SPECIFICATION SECTION IS BASED ON LANL MASTER SPECIFICATION SECTION 10 4400, REV. 4, DATED APRIL 15, 2026.