SECTION 12 3100

MANUFACTURED METAL CASEWORK

**************************************************************************************************************

LANL GUIDE SPECIFICATION

Word file at http://engstandards.lanl.gov

This template must be edited for each project.  In doing so, specifier must add job-specific requirements.  Brackets are used in the text to indicate designer choices or locations where text must be supplied by the designer.  Once the choice is made or text supplied, remove the brackets.  The specifications must also be edited to delete specification requirements for processes, items, or designs that are not included in the project -- and specifier’s notes such as these.  To seek a variance from requirements in the specifications that are applicable, contact the Engineering Standards Manual Architectural POC. Please contact POC with suggestions for improvement as well.

When assembling a specification package, include applicable specifications from all Divisions, especially Division 1, General requirements.

Specification developed for ML-4 projects.  For ML-1, 2, and 3 applications, additional requirements and independent reviews should be added if increased confidence in procurement or execution is desired; see ESM Ch 1 Section Z10 Specifications and Quality sections.

*******************************************************************************************************************

PART 1  GENERAL

  - SECTION INCLUDES

- Metal cabinet units and bases

- Countertops

- Cabinet hardware

- Preparation for installation of utilities

- Service fittings and outlets

  - RELATED REQUIREMENTS

- Section 07 9200	Joint Sealants

- Section 23 3816	Fume Hoods

  - SUBMITTALS

- Action / Informational Submittals

- [Product Data:  manufacturer’s specifications and other data for compliance with specified requirements.]

- Shop Drawings:  showing catalog number and location of each item, dimensioned plans and elevations, large scale details, attachment devices, and other components.

- [Samples:  manufacturer’s standard color and finishes.]

- Manufacturer’s Instructions:  recommended installation instructions.

- Sustainable Design Submittals

  - Manufacturer's Certificate: Certify products meet or exceed specified sustainable design requirements.

**************************************************************************************************************

Edit material certifications list to suit products specified in this section and Project sustainable design requirements.

**************************************************************************************************************

      - Materials Resources Certificates:

        - Certify source and origin for [salvaged] [and] [reused] products.

        - Certify recycled material content for recycled content products.

        - Certify source for local and regional materials and distance from Project site.

        - Certify lumber is harvested from Forest Stewardship Council Certified well managed forest.

      - Indoor Air Quality Certificates:

Certify each composite wood [and agrifiber] product contains no added urea-formaldehyde resins.

  - Product Cost Data: Submit cost of products to verify compliance with Project sustainable design requirements. Exclude cost of labor and equipment to install products.

**************************************************************************************************************

Edit list of material cost data to suit products specified in this section and Project sustainable design requirements.

**************************************************************************************************************

      - Salvaged products.

      - Reused products.

      - Products with recycled material content.

      - Local and regional products.

      - [____________________.]

- Closeout Submittals

  - Operation and Maintenance Data:  manufacturer’s operation and maintenance instructions.

  - Manufacturer’s Warranty Documentation

  - QUALITY ASSURANCE

Use products of a company that specializes in the manufacture of the products specified in this Section that has successfully completed at least 25 projects of the same size and scope as this project.

Sustainable Design Requirements:

**************************************************************************************************************

Edit sustainable design requirements to suit content of this section and Project sustainable design requirements.

**************************************************************************************************************

Recycled Content Materials: Furnish materials with recycled content [including:] [.]

**************************************************************************************************************

List materials specified in this section required to have recycled content in the following chart. Indicate minimum recycled content when recycled percentage is determined by design team.

**************************************************************************************************************

| Material | Minimum Recycled Content (Percent) |
| --- | --- |
|  | Post Consumer | Pre Consumer |

****** [OR] ******

**************************************************************************************************************

List materials specified in this section required to have recycled content in the following paragraph when recycled percentage is determined by Subcontractor.

**************************************************************************************************************

[____________________.]

Regional Materials: Furnish materials extracted, processed, and manufactured within 500 miles (800 km) of Project site [including:] [.]

******************************************************************************************

List materials specified in this section required to be regional materials.

******************************************************************************************

[____________________.]

Certified Wood Materials: Furnish wood materials certified in accordance with FSC Guidelines [including:] [.]

******************************************************************************************

List materials specified in this section required to be certified wood.

******************************************************************************************

[____________________.]

Qualifications

Manufacturer:  Minimum, ten (10) years experience in the fabrication of metal casework of the type and quality specified.

Installer:  Successful experience completing a minimum of ten (10) projects of similar installations and licensed by the manufacturer.

Mockup

**************************************************************************************************************

Use this article for full sized erected assemblies required for review of construction, coordination of work of several sections, testing, or observation of operation.

**************************************************************************************************************

Construct full size mockup including [base cabinet] [and] [base] [and] [upper cabinet] [________] complete with drawers, door, adjustable shelf and counter top of [________].

Locate [where directed by Architect/Engineer.] [where indicated on Drawings.]

Incorporate accepted mockup as part of Work.

***** [OR] ******

Remove mockup [when directed by Architect/Engineer.] [____________________.]

  - DELIVERY, STORAGE AND HANDLING

- Delivery and Acceptance Requirements:

      - Deliver casework so it will not be damaged or deformed.

      - Package for protection from damage during transportation.

- Storage and Handling Requirements

      - Exercise care in unloading, storing and installing casework to prevent bending, warping, twisting and damage.

      - Stack materials on platforms or pallets, covered with tarpaulins or other suitable weather tight, ventilated covering.

  - WARRANTY

A.	Provide manufacturer’s standard warranty for labor and materials.

PART 2  PRODUCTS

  - MANUFACTURERS

- [Kewaunee Scientific Corporation, GSA Program] Model [              ].

- [Fisher Hamilton Scientific Inc., Modular Steel] Model [            ].

- [Jamestown Metal Products] Model [________].

- [____________________] Model [________].

  - PERFORMANCE / DESIGN CRITERIA

          - Dimensions are to be obtained from site.

          - Drawer, doors, and other casework arrangements to be as in the Subcontract Drawings or as otherwise specified.

          - Construct base cabinets to support a minimum uniformly distributed load of 200 lbs per square foot of cabinet top area, including working surface, without distortion or interference with door and drawer operation.

          - Base cabinet corner gussets with leveling bolts shall support 500 lbs per corner at 1-1/2 inch projection of the leveling bolt below the gusset.

          - Each adjustable and fixed shelf 4 feet or shorter in length shall support an evenly distributed load of 40 lbs per square foot up to a maximum of 200 lbs, with nominal temporary deflection, but without permanent set.

          - Drawer construction and performance shall allow 13 5/8 inch clear when in an extended position and suspension system shall prevent friction contact with any other drawer or door during opening or closing. All drawers shall operate smoothly after a minimum of 10,000 cycles with an evenly distributed load of 150 lbs.

          - Swinging doors on floor mounted casework shall support 200 lbs suspended at a point 12 inches from the hinged side with door swung through an arc of 160°. Weight load test shall allow only a temporary deflection without permanent distortion or twist. Door shall operate freely after test and assume a flat plane in a closed position.

  - MATERIALS

- Sheet steel: ASTM A446, Grade D, stretcher leveled.

- Metal gauges: for construction of cases, 18 gauge, except as follows:

      - Corner gussets for leveling bolts and apron corner braces, 12 gauge;

      - Hinge reinforcements, case and drawer suspension channels, 14 gauge;

      - Top and intermediate front horizontal rails, table aprons and reinforcement gussets, 16 gauge;

      - Drawer assemblies, door assemblies and adjustable shelves, 20 gauge.

- [Glass

- [Framed sliding and swinging doors:  safety glass conforming to ASTM C1048, FT-fully tempered, uncoated, Type 1 transparent, 1/8 inch thick minimum.]

- [Unframed sliding doors:  safety glass conforming to ASTM C1048, FT-fully tempered, uncoated, Type 1 transparent, 1/4 inch thick minimum.]]

- Hardware and trim

- Drawer and door pulls:  satin finish aluminum with a clear lacquer finish securely fastened to doors and drawers with vandal resistant screws. Provide two pulls on all drawers greater than 24 inches long.

- Flush pulls:  satin finish chrome providing a recessed finger grip.

- Hinges:  stainless steel with brushed satin finish, institutional type with a five-knuckle bullet type barrel. Attach to both door and case with two screws through each hinge leaf. Doors under 36 inches in height shall have 1 pair of 2 ½ inch high hinges; doors over 36 inches in height shall have 1 ½ pair of 2 ½ inch high hinges.

- Friction catches:  adjustable nylon roller type with strike.

- Elbow catches and strike plates:  provide steel, cadmium plated on left hand doors of double door cases where locks are used.

- Magnetic latches:  provide on all upper case glazed swinging doors enclosed in a plastic case with a plated steel strike plate screwed to the door. Provide double door cases with latches on both doors.

- Shelf Adjustment Clips:  nickel plated steel.

- Countertops

******************************************************************************************

When special work surfaces are required, edit following paragraph accordingly.

******************************************************************************************

- Counter Tops [, Back Splash] [and Side Splash]: [Solid laminate, acid resistant finish] [Stainless steel] [Maple] [Birch] [Modified epoxy resin] [Quarried natural soap stone, machine finished] [High pressure molded cement fiber] [Calcium aluminum silicate base, mineral fiber reinforced], [acid resistant]; [________] manufactured by [____________________].

- Joint sealant at joints in countertops and splashes as recommended by countertop material manufacturer.

*************************************************************

Coordinate 3. below with samples submittals above.

***********************************************************

- [Color:  [select from manufacturer’s standard selection].]

- Service fittings and fixtures as indicated on the Drawings.

- [Stainless steel] [One piece solid epoxy resin casting] cup sinks with waste fittings, [   ] inch diameter, [   ] inch deep.

- Stainless steel trim escutcheons.

- Stainless steel electrical outlet covers.

  - FABRICATION

- Welded construction throughout where practical.

- Welded joints:  grind joints smooth and flush.

- Fabricate corners and joints without gaps or inaccessible spaces where dirt or moisture could accumulate.

- Fabricate components of die formed sheet steel. Form each unit rigid, not dependent on adjacent units or building structure for rigidity.

- Form edges and seams smooth.

- Turn down edges of shelves 1 inch on each side and return 5/8 inch front and back.

- Bottoms

  - Interior of cabinet bottoms flanged on all sides.

  - Heavy gauge triangular gusset welded in each bottom corner of floor mounted units.

  - Exposed undersides of wall units to have pan-shaped bottom fitted into interior bottom.

- Backs

- Wall and floor units:  welded to rear flanges of sides.

- Removable for base units from inside of cabinet.

- Metal Doors

  - Reinforced double wall construction.

  - Both panels pan-shaped.

  - Corners welded.

  - Filled with sound deadening material

  - Rubber bumpers

- Drawers and Front Doors

  - Two panels with face and back welded together.

  - Bonded sound deadening filler core.

  - Mounted on channel-shaped slides with four ball bearings.

  - Rubber stoppers and snubbers to control drawer action.

  - Drawers easily removable.

- Fabricate countertops of full length material wherever possible.

- Set glass in doors with gasket and removable stops to minimize rattles or vibration.

- Cut and drill countertops, backs and other components for service outlets and fixtures.

- Install fixtures and fittings built into or part of casework. Provide access panels for maintenance of utility service and mechanical and electrical components.

- Special Purpose Storage Cabinets

  - Acid Storage Cabinets:  utilize the same gauges of metal and construction features as other base cabinets except provide a corrosion resistant liner and a set of louvers at the top and bottom of each door. Provide a half width removable shelf of the same material as the liner with each cabinet.

  - Solvent Storage Cabinets:  Specifically designed for the storage of flammable and combustible liquids. Provide construction in accordance with OSHA and NFPA 30 and provide Factory Mutual Approved label. Cabinet bottoms, top, sides and doors are to be of 18 gauge steel of double panel construction with a 1- ½ inch air space between panels. All joints are to be welded, or screwed, to provide a rigid enclosure. Doors are to swing on full length piano hinges and fully insulated. Right hand door is to be equipped with a three point locking device and the left hand door is to have a full height astragal. Provide a 2 inch deep liquid tight pan that covers the entire bottom of the cabinet to contain liquid leaks and spills. Provide heavy duty shelves with reinforced bottom formation. Provide a grounding screw. The cabinet is to have interior finish same as exterior. Label cabinet: “FLAMMABLE – KEEP FIRE AWAY”.

  - SHOP FINISHING METHODS

  - Manufacturer’s degreasing and phosphate etch: 150 to 200 milliliters per square foot

  - Factory applied primer and baked electrodeposited epoxy enamel, acid-alkali resistant

****************************************************************

Coordinate C. below with sample submittals above.

*************************************************************

  - Color:  [manufacturer’s standard colors].

  - Shop finish all components.

PART 3  EXECUTION

  - EXAMINATION

- Prior to all work of this section, carefully inspect the installed work of all other trades and verify that it is complete to the point where this installation may properly commence.

- Examine areas to receive this work and verify that:

- Backing, support framing and anchors not included in this work is correct.

- Surfaces are dry, clean, free from foreign matter and otherwise proper for installation.

- Verify presence of required utilities.

  - INSTALLATION

- Install casework, components and accessories in accordance with manufacturer’s installation instructions and approved shop drawings.

- Use only skilled mechanics.

- Attach casework securely with concealed fastenings unless otherwise note. Ensure true alignment.

- Use anchoring devices to suit conditions and substrate materials encountered.  Follow Section 03 1550 Post-Installed Concrete Anchors- Installation and Testing for anchoring to concrete and masonry.

- Set casework items plumb and square, securely anchored to building structure.

- Insulate to prevent electrolysis between dissimilar metals.

- Scribe to abutting surfaces and align adjoining components. Apply matching filler pieces where casework abuts dissimilar construction materials.

- Field touchup blemishes to match original finish.

- [Close joints in units and countertops and splashes with sealant.]

  - ADJUSTING

- Adjust all components as required for correct operation.

  - PROTECTION

- Protect finished casework from damage during continued construction activity.

  - SCHEDULE OF MANUFACTURED METAL CASEWORK

*****************************************************************************************************

Edit schedule as required to reflect specific project requirements. Further, add or delete items as necessary.

************************************************************************************************

- Base cabinets, model [         ].

- Wall cabinets, model [          ].

- Corner cabinets, model [            ], [with lazy susan shelves.]

- Tall storage cabinets, model [             ].

- Island cabinet, model [               ], finish of sides and/or back to match front finish of other cabinets.

- Sink cabinet, model [               ].

- [Tub sink, [                  ], model [              ].]

- [Double tub sink, [                ], model [                  ].]

- [Hot and cold water mixing gooseneck faucet, model [             ].]

- [Sink outlet, model [                 ].]

- [Overflow, model [                   ].]

- Acid storage cabinet, model [              ].

- Solvent storage cabinet, model [              ].

- Service fittings – provide the following service fittings where indicated on drawings.

- [                  ]

- [                   ]

- [                   ]

- Table assemblies

- Wall table assembly, model [            ], length x [               ].

- Center table assembly, model [             ], length x [               ].

- Pass thru storage cases, model [              ]

- Flammable material storage refrigerator, model [            ].

- Water still, model [             ].

- Gas bottle rack, model [               ].

END OF SECTION

*****************************************************************

Do not delete the following reference information:

*****************************************************************

FOR LANL USE ONLY

This project specification is based on LANL Master Specification 12 3100 Rev. 2, dated September 23, 2009.