Section 21 1200 
Fire-Suppression Standpipes

  - *************************************************************************************************************

    - LANL MASTER SPECIFICATION SECTION

Rev. 1 Summary of Changes: Edited and updated as required for import into SpecLink.

      - NOTE TO SPECIFIER ON USAGE IN SPECLINK: Activate the Section by turning on Seq #0000, followed by activating paragraphs in PART 1, Article SECTION INCLUDES. This will activate related articles, paras/subparas in the rest of the Section (i.e., PART 1 activates articles and paras/subparas in PARTS 2 and 3). If there are choice fields to edit the entire Section (typically in this first author note or beginning of the Section), make selections at those locations, which will filter through the remaining Section. All Articles, paragraphs and subparagraphs must be activated sequentially from top to bottom, unless noted otherwise.

      - This template must be edited for each project. In doing so, Specifier must add job-specific requirements. Selections and choice fields are used to indicate designer choices or locations where text must be supplied by the designer. The section must also be edited to remove requirements for processes, items, or designs that are not included in the project.

      - To seek a variance from applicable requirements in this Section, contact the Engineering Standards Manual (ESM) Fire POC  (LANL access only). Please contact POC with suggestions for improvement as well. LANL personnel should submit here: Suggested Change or Request Clarification; subcontractors via email to engstandards@lanl.gov.

      - When assembling a specification package, include applicable specifications from all Divisions, especially Division 1, General Requirements.

      - Section is developed for ML-4 projects.  For ML-1, 2, and 3 applications, additional requirements and independent reviews should be added if increased confidence in procurement or execution is desired; see LANL ESM Chapter 1 - General, Section Z10 Specifications and Quality sections.

      - ==========================================================

      - Note that DOE-1066 Appendices A and B are not applicable to the Work specified herein. Consider the scope and purpose of DOE documents as pertains to commercial construction before editing such requirements into this specification.

      - Standpipe systems will typically be delegated designs.  This template is written as such.  If the design is provided by LANL ES, revise accordingly.

  - *************************************************************************************************************

PART 1 - GENERAL

SECTION INCLUDES

      - ***************************************************************************************

      - Class 2 and Class 3 standpipes are intentionally not specified for commercial construction projects at LANL.  Both Class 2 and Class 3 standpipes require occupant training, permanent hoses and hose maintenance regimens.

      - The following paragraphs are designer choices based on project-specific conditions.

      - ***************************************************************************************

Hydraulically designed Class 1 << combined;  automatic wet;  manual wet;  automatic dry; and  manual dry>> standpipe system.

Specialty Valves for standpipe systems.

Fire Department Connections for standpipes.

RELATED REQUIREMENTS

Section << 01 2500 - Substitution Procedures>>.

Section ​<< 01 7700 - Closeout Procedures>>​.

Section ​<< 21 0500 - Common Work Results for Fire Suppression>>​.

Section ​​<< 21 0523 - General-Duty Valves for Water-Based Fire-Suppression Piping>>​​.

    - **********************************************************************************************

      - The codes/standards listed below are provided for reference only and are not listed within the body of this section. It is a designer-choice to include these codes/standards.

      - <<ASTM A795/A795M>>

      - <<NFPA 1963>>

    - **********************************************************************************************

REFERENCE STANDARDS

ASTM A536 - Standard Specification for Ductile Iron Castings.

ASTM A795/A795M - Standard Specification for Black and Hot-Dipped Zinc-Coated (Galvanized) Welded and Seamless Steel Pipe for Fire Protection Use.

ASTM B61 - Standard Specification for Steam or Valve Bronze Castings.

NFPA 14 - Standard for the Installation of Standpipe and Hose Systems.

NFPA 1963 - Standard for Fire Hose Connections.

UL 405 - Standard for Safety Fire Department Connection Devices.

DELEGATED DESIGN SUBMITTALS

Submit shop drawings, corresponding hydraulic calculations and product data to the LANL Fire Marshal’s office for approval.

Product Data: Provide manufacturer's catalog data for equipment indicating rough-in size, finish, and accessories.

Shop Drawings: Indicate supports, components, accessories, and sizes.

Hydraulic Calculations.

INFORMATIONAL SUBMITTALS

Completed “Contractor’s Materials and Test Certificate for Aboveground Piping”.

Project Record Documents: Record Documents reflecting final installed conditions. Include Drawings<< and 3D model; or  None - N/A>> and the corresponding Hydraulic Calculations.

Operation and Maintenance Data: Manufacturer’s data including parts diagrams, lists of spare parts, and service requirements.

QUALITY ASSURANCE

Perform Work in accordance with <<NFPA 14>>. One bound copy of the applicable edition of <<NFPA 14>> shall remain on site and accessible while work is being performed.

Designer Qualifications: Design system under direct supervision of a << Professional Fire Protection Engineer experienced in fire suppression design and licensed in NM state; or  NICET Level III certified technician “Water-Based Systems Layout”>>. Drawings and calculations shall be sealed by NICET Level III or Professional Engineer.

Installer Qualifications: Company specializing in performing the Work of this section << with documented experience;  with minimum ___ years documented experience; or  _______>>.

DELIVERY, STORAGE AND HANDLING

Deliver and store products in shipping packaging until installation.

WARRANTY

See Section << 01 7700 - Closeout Procedures>> for additional warranty requirements.

Correct defective Work within one year following the date of Substantial Completion.

      - ***************************************************************************************

      - Select galvanized pipe and fittings for MANUAL AND DRY standpipe systems.

      - ***************************************************************************************

PART 2 - PRODUCTS

    - **********************************************************************************************

      - The following Articles are designer choices based on project-specific conditions.

    - **********************************************************************************************

PIPE AND FITTINGS

For pipe and fittings, refer to Section << 21 0500 - Common Work Results for Fire Suppression>>.

VALVES

General Duty Valves: Refer to Section << 21 0523 - General-Duty Valves for Water-Based Fire-Suppression Piping>>.

      - ***************************************************************************************

      - The following paragraph and the various specialty valve options in the subparagraphs are designer choices.

      - ***************************************************************************************

Specialty Valves

Hose Connection Valve

Manufacturers

Elkhart Brass.

Potter Roemer.

Reliable.

Zurn .

<< _______>>.

Substitutions: << Alternate products may be accepted, follow Section 01 2500 - Substitution Procedures; or  Not permitted – No substitutions>>​.

Angle Type: << Brass; or  Chrome plated>> finish; << 2-1/2 inch NPS; or  ______>>, thread to match fire department hardware, << 300; or  ______>> psi working pressure, with threaded cap and chain of same material and finish.

Pressure Reducing Valve

Manufacturers

Elkhart Brass.

Potter Roemer.

<< _______>>.

Substitutions: << Alternate products may be accepted, follow Section 01 2500 - Substitution Procedures; or  Not permitted – No substitutions>>.

<< Angle; or  Straight>> type: << Brass; or  Chrome plated>> finish with inner hydraulic controls; << 2;  2-1/2;  8; or  _______>> inch size, thread to match fire department hardware, << 400; or  _______>>​ psi inlet pressure, with threaded cap and chain of same material and finish.

Pilot Operated Control Valves

Manufacturers

Zurn Industries, LLC

Cla-Val.

Reliable.

Substitutions: << Alternate products may be accepted, follow Section 01 2500 - Substitution Procedures; or  Not permitted – No substitutions>>.

Size: << 2-1/2 to 8 inch NPS;  2-1/2 inch NPS;  As indicated on drawings; or  _______>>, << flanged;  grooved;  threaded; or  _______>> end-connections.

Type: Field adjustable in-line valve rated for << 400; or  _______>>​ psi inlet pressure with outlet discharge field-set to system pressure.

Construction

Body: <<ASTM A536>>, ductile iron, grade 65-45-12.

Internal Ferrous Materials: Coated with 4 mils of epoxy.

External Surface Coating: 4 mils of epoxy and fire red enamel.

Main Valve Seat Ring: <<ASTM B61>>, bronze.

Stem: Stainless Steel.

Elastomers for Diaphragms, Resilient seats, and O-rings: Buna-N.

Pilot Control: <<ASTM B61>>, bronze with stainless steel trim and pressure gages.

<< In-line;  Angle; or  _______>>​ Floor Control Valves

Manufacturers

Reliable.

Potter Roemer.

Zurn.

<< _______>>.

Substitutions: << Alternate products may be accepted, follow Section 01 2500 - Substitution Procedures; or  Not permitted – No substitutions>>.

Cast bronze, ​​<< 2-1/2 inch NPS; or  _______>>​​, ​​<< handwheel operated;  bonnet operated; or  _______>>​​ globe valve with ​​<< grooved;  threaded; or  _______>>​​ end connections, rated for ​​<< 400; or  _______>>​​ psi maximum inlet pressure with outlet discharge ​​<< factory;  field; or  _______>>​​-set to system inlet pressure. Provide ​​<< integral normally-closed supervisory switch;  integral normally-open supervisory switch;  cap;  chain; and  _______>>​​.

FIRE DEPARTMENT CONNECTIONS

Type: ​<< Free standing;  Flush, wall mount; or  Exposed, projected wall mount>>​ made of corrosion resistant metal​<< complying with UL 405; or  None - N/A>>​.

Manufacturers

Elkhart Brass Manufacturing Company.

Fire End & Croker Corporation.

Potter Roemer.

<< _______>>.

Substitutions: ​<< Alternate products may be accepted, follow Section 01 2500 - Substitution Procedures; or  Not permitted – No substitutions>>​.

Inlets: << Two;  Three;  Four; or  _______>>-way, << 2-1/2; or  _______>> inch swivel fittings, internal threaded. Brass caps with gaskets, chains, and lugs.

Configuration: << Horizontal;  Vertical;  Square; or  _______>>.

Outlet: ​<< With pipe threads;  Back with pipe threads;  Bottom with pipe threads; or  _______>>​, ​<< 4;  5;  6; or  _______>>​​ inch NPS.

Location: << Back;  Bottom;  Left;  Right; or  _______>>.

Rated Working Pressure: << 175; or  _______>> psi.

Finish: << Chrome;  Polished chrome;  Brass or bronze;  Polished brass; or  _______>>.

Sleeve: << Brass, ; or  None - N/A>>​<< 18; or  _______>> inch height.

Signage: Raised or engraved lettering << 1; or  _______>>​ inch minimum indicating system type.

PART 3 - EXECUTION

INSTALLATION

Install in accordance with manufacturer's instructions and <<NFPA 14>>.

Connect standpipe system to water source ahead of domestic water connection.

Where static pressure exceeds << 100; or  _______>> psi but is less than << 100; or  _______>> psi at any hose station, provide pressure orifice disc in discharge of hose station valve to prevent pressure on hose exceeding << 90; or  _______>> psi.

Where static pressure exceeds << 100; or  _______>> psi at any hose station, provide pressure reducing valve to prevent pressure on hose exceeding << 90; or  _______>> psi.

Flush entire system of foreign matter.

FIELD QUALITY CONTROL

Perform field ​<< inspection and ;  _______; or  None - N/A>>​testing.

Test entire system and document in accordance with <<NFPA 14>>.

Test shall be witnessed by a representative of the LANL Fire Marshal.

An executed Contractor’s Materials and Test Certificate for Aboveground Piping shall be signed by the installing subcontractor and a representative of the LANL Fire Marshal.

END OF SECTION

    - **********************************************************************************************

      - Do not omit  the following reference information:

    - **********************************************************************************************

THE FOLLOWING STATEMENT IS FOR LANL USE ONLY

THIS PROJECT SPECIFICATION SECTION IS BASED ON LANL MASTER SPECIFICATION SECTION 21 1200, REV. 1, DATED APRIL 15, 2026.