Section 21 1300 
Fire-Suppression Sprinkler Systems

  - *************************************************************************************************************

    - LANL MASTER SPECIFICATION SECTION

Rev. 1 Summary of Changes: Edited and updated as required for import into SpecLink.

      - NOTE TO SPECIFIER ON USAGE IN SPECLINK: Activate the Section by turning on Seq #0000, followed by activating paragraphs in PART 1, Article SECTION INCLUDES. This will activate related articles, paras/subparas in the rest of the Section (i.e., PART 1 activates articles and paras/subparas in PARTS 2 and 3). If there are choice fields to edit the entire Section (typically in this first author note or beginning of the Section), make selections at those locations, which will filter through the remaining Section. All Articles, paragraphs and subparagraphs must be activated sequentially from top to bottom, unless noted otherwise.

      - This template must be edited for each project. In doing so, Specifier must add job-specific requirements. Selections and choice fields are used to indicate designer choices or locations where text must be supplied by the designer. The section must also be edited to remove requirements for processes, items, or designs that are not included in the project.

      - To seek a variance from applicable requirements in this Section, contact the Engineering Standards Manual (ESM) Fire POC  (LANL access only). Please contact POC with suggestions for improvement as well. LANL personnel should submit here: Suggested Change or Request Clarification; subcontractors via email to engstandards@lanl.gov.

      - When assembling a specification package, include applicable specifications from all Divisions, especially Division 1, General Requirements.

      - Section is developed for ML-4 projects.  For ML-1, 2, and 3 applications, additional requirements and independent reviews should be added if increased confidence in procurement or execution is desired; see LANL ESM Chapter 1 - General, Section Z10 Specifications and Quality sections.

      - Note that DOE-STD-1066 Appendices A and B are not applicable to the Work specified herein. Consider the scope and purpose of DOE documents as pertains to commercial construction before editing such requirements into this specification Section.

  - *************************************************************************************************************

PART 1 - GENERAL

SCOPE OF WORK

      - ***************************************************************************************

      - Select one of the following paragraphs. Last paragraph related to non-hydraulically designed modifications is for instances where it can be demonstrated without performing hydraulic calculations that the Work does not affect the hydraulically-remote areas.

      - ***************************************************************************************

Provide hydraulically-designed complete fire sprinkler system(s) to achieve fully-sprinklered coverage.  The Work shall be complete in all respects.  Provide shop drawings, calculations, installation and testing compliant with <<NFPA 13>>.

Provide hydraulically-designed modification(s) to existing fire sprinkler system(s) to achieve fully-sprinklered coverage.  The Work shall be complete in all respects.  Provide shop drawings, calculations, installation and testing compliant with <<NFPA 13>>.

Provide non-hydraulically-designed modification(s) to existing fire sprinkler system(s) to achieve fully-sprinklered coverage.  Justification for non-hydraulic designs shall be vetted through the AHJ prior to generating shop drawings.  The Work shall be complete in all respects.  Provide shop drawings, installation and testing compliant with <<NFPA 13>>.

SECTION INCLUDES

      - ***************************************************************************************

      - The following paragraphs are designer choices based on project-specific requirements.

      - ***************************************************************************************

Wet-pipe Fire Sprinkler Systems.

Dry-pipe Fire Sprinkler Systems.

Preaction Fire Sprinkler Systems.

RELATED REQUIREMENTS

Section << 01 2500 - Substitution Procedures>>.

Section << 01 3300 - Submittal Procedures>>.

Section ​<< 01 7700 - Closeout Procedures>>​.

Section ​<< 22 0813 - Testing Piping Systems>>​.

Section << 28 4600 - Fire Detection and Alarm>>.

REFERENCE STANDARDS

FM (AG) - FM Approval Guide.

NFPA 13 - Standard for the Installation of Sprinkler Systems.

NFPA 24 - Standard for the Installation of Private Fire Service Mains and Their Appurtenances.

NFPA 25 - Standard for the Inspection, Testing, and Maintenance of Water-Based Fire Protection Systems.

NFPA 70 - National Electrical Code.

NFPA 72 - National Fire Alarm and Signaling Code.

NFPA 1963 - Standard for Fire Hose Connections.

UL (DIR) - Online Certifications Directory.

UL 405 - Standard for Safety Fire Department Connection Devices.

Action SUBMITTALS

Delegated Design Submittals: Submit shop drawings, corresponding hydraulic calculations and product data to the LANL Fire Marshal’s office for approval per Section << 01 3300 - Submittal Procedures>>.

Product Data: Provide manufacturer's catalog sheet for equipment indicating rough-in size, finish, and accessories.

Shop Drawings: Indicate supports, components, accessories, and sizes.

Hydraulic Calculations. Calculations shall be performed using current fire hydrant flow test data << obtained by the subcontractor; or  provided by LANL>>.

INFORMATIONAL SUBMITTALS

Completed “Contractor’s Materials and Test Certificate for Aboveground Piping”.

Project Record Documents. Record Documents reflecting final installed conditions. Include Drawings​<< and 3D model,; or  None - N/A>>​ and the corresponding Hydraulic Calculations.

Operation and Maintenance Data: Manufacturer’s data including parts diagrams, lists of spare parts, and service requirements.

QUALITY ASSURANCE

Perform Work in accordance with <<NFPA 13>>. One bound copy of the applicable edition of <<NFPA 13>> shall remain onsite and accessible while Work is being performed and until ​<< Certificate of Occupancy; or  acceptance>>​.

Designer Qualifications: Design system under direct supervision of a << Professional Fire Protection Engineer experienced in fire suppression design and licensed in NM state; or  NICET Level III certified technician “Water-Based Systems Layout”>>. Drawings and calculations shall be sealed by NICET Level III or Professional Engineer.

Installer Qualifications: Company specializing in performing the Work of this Section << with minimum ____ years' experience;  with documented experience;  ___; or  None - N/A>>.

DELIVERY, STORAGE, AND HANDLING

Store products in shipping containers and maintain in place until installation. Provide temporary inlet and outlet caps. Maintain caps in place until installation.

WARRANTY

See Section << 01 7700 - Closeout Procedures>> for additional warranty requirements.

Correct defective Work within one year following the date of Substantial Completion.

PART 2 - PRODUCTS

PERFORMANCE REQUIREMENTS

All materials and components shall meet applicable requirements. Products shall be UL listed and/or FM approved.

Fire sprinkler system design, components and installation shall comply with <<NFPA 13>>.

      - ***************************************************************************************

      - Retain only one of the following two paragraphs.

      - ***************************************************************************************

Obtain a current fire hydrant flow test<< from LANL; or  None - N/A>>.

      - *** OR ***

Fire hydrant flow test data:

Date: << _______>>.

Gage Hydrant Number: << _______>>.

Flow Hydrant Number: << _______>>.

Static Pressure: << _______>>.

Residual Pressure:<< _______>>.

Flow: << _______>>.

Distance from test gage to base of riser: << _______>>.

Elevation of test gage: << _______>>.

Elevation of base of riser: << _______>>.

Hydraulic calculations shall achieve a margin of 10 psig or 10 percent – whichever is greater.

      - ***************************************************************************************

      - The following Articles in PART 2 are designer choice based on project-specific requirements.

      - ***************************************************************************************

FIRE SPRINKLERS

Manufacturers: Provide fire sprinklers from the following manufacturers.  Each type of fire sprinkler listed on the shop drawings shall be from a single manufacturer.

Reliable Sprinkler.

Tyco Fire Protection Products.

Victaulic.

Viking.

<< _______>>.

Substitutions: ​<< Alternate products may be accepted, follow Section 01 2500 - Substitution Procedures; or  Not permitted – No substitutions>>​.

      - ***************************************************************************************

      - Select paragraphs below as applicable to the project. If selecting the first paragraph, it is likely none of the subsequent paragraphs need to be selected.

      - ***************************************************************************************

Refer to fire sprinkler schedule on Drawings.

Suspended Ceiling Application: << Semi-recessed;  Recessed; or  Concealed>>, << pendant;  upright; or  _______>> type with matching << push on;  clamp on; or  screw on>>, << escutcheon; or  cover>> plate.

Response Type: << Quick;  Standard; or  _______>>.

Coverage Type: << Standard;  Extended; or  _______>>.

Finish: ​​<< Brass;  Chrome plated;  Enamel,  color  ___;  Teflon;  Wax; or  _______>>​​.

​​<< Escutcheon; or  Cover>>​​ Plate Finish: ​​<< Chrome; or  Enamel,  color  _______>>​​.

Heat-Responsive Element: << Fusible solder link type; or  Glass bulb type>> temperature rated for specific area hazard.

Exposed Area Application: << Pendant; or  Upright>> type<< with guard; or  None - N/A>>.

Response Type: << Quick;  Standard; or  _______>>.

Coverage Type: << Standard;  Extended; or  _______>>.

Finish: ​<< Brass;  Chrome plated;  Enamel,  color  ___;  Teflon;  Wax; or  _______>>​.

Heat-Responsive Element: << Fusible solder link type; or  Glass bulb type>> temperature rated for specific area hazard.

Sidewall Application: << Semi-recessed;  Recessed; or  _______>> horizontal sidewall type with matching << push on;  clamp on; or  screw on>> escutcheon plate.

Response Type: << Quick;  Standard; or  _______>>.

Coverage Type: << Standard;  Extended; or  _______>>.

Finish: ​<< Brass;  Chrome plated;  Enamel,  color  ___;  Teflon;  Wax; or  _______>>​

Heat-Responsive Element: << Fusible solder link type; or  Glass bulb type>> temperature rated for specific area hazard.

Dry Sprinklers: << Concealed;  Exposed;  Plain barrel;  Recessed; or  _______>> pendant type with matching push on << escutcheon plate; or  cover plate>>.

Response Type: << Quick;  Standard; or  _______>>.

Coverage Type: << Standard;  Extended; or  _______>>.

Finish: ​<< Brass;  Chrome plated;  Enamel,  color ___; or  _______>>​​.

​​<< Cover; or  Escutcheon>>​​ Plate Finish: ​​<< Chrome plated; or  Enamel, color  _______>>​​.

Heat-Responsive Element: << Fusible solder link type; or  Glass bulb type>> temperature rated for specific area hazard.

Storage Sprinklers: << Pendant;  Standard;  Upright; or  _______>> type<< with guard; or  None - N/A>>.

Type: << In-Rack;  CMDA;  CMSA; or  ESFR>>.

Finish: ​<< Chrome-plated; or  Enamel, color  _______>>​.

Heat-Responsive Element: << Fusible solder link type;  Glass bulb type; or  _______>> temperature rated for specific area hazard.

Guards: << Red; or  Chrome>> finish.

Flexible Drop System: Stainless steel, multiple use, open gate type.

Manufacturers:

Victaulic.

Application: Use to properly locate sprinkler heads.

Include all supports and bracing.

Type: ​<< Braided;  Unbraided; or  _______>>​ tube as required for the application.

PIPING SPECIALTIES

Manufacturers for Wet Pipe Sprinkler Alarm, Dry Pipe Sprinkler Alarm and Preaction Valves:

Reliable Automatic Sprinkler

Tyco Fire Products

Victaulic

Viking

​<< _______>>​.

Substitutions: ​​<< Alternate products may be accepted, follow Section 01 2500 - Substitution Procedures; or  Not permitted – No substitutions>>​​.

      - ***************************************************************************************

      - Select paragraphs below as applicable to the project.

      - ***************************************************************************************

Wet Pipe Sprinkler Alarm Valve: Check type valve with divided seat ring, rubber-faced clapper to automatically actuate water motor alarm, pressure retard chamber and variable pressure trim with the following additional capabilities and features:

Electric alarm interface.

Test and drain valve.

Dry Pipe Sprinkler Alarm Valve: Check type valve with divided seat ring, rubber faced clapper to automatically actuate water motor alarm, accelerator, and with the following additional capabilities and features:

Electric alarm interface.

Test and drain valve.

Externally resettable.

Preaction Valve:

Operated by detection system listed for releasing service and independent of building fire alarm system with provisions for local, manual​<< , and indicated remote;  _______; or  None - N/A>>​ releases.

Incorporate << mechanical; or  _______>> latching mechanism incorporating valve clappers independent of system water pressure fluctuations.

Provide test detection device for each actuation circuit adjacent to each controlled valve in accordance with <<NFPA 13>>.

      - ***************************************************************************************

      - Fire suppression systems supplied from a dedicated fire loop or tank (non-potable water) do not require backflow prevention.

      - ***************************************************************************************

Backflow Preventer: Reduced pressure principle valve assembly backflow preventer with drain and OS&Y (Open Stem & Yoke) gate valve on each end.

Manufacturers:

Febco, Model LF880V

Wilkins, Model 475V

<< _______>>

Substitutions: ​<< Alternate products may be accepted, follow Section 01 2500 - Substitution Procedures; or  Not permitted – No substitutions>>​.

Test Connections:

Inspector's Test Connection:

Provide test connections approximately << 6; or  ___>>​​ ft above floor for << each;  portion of each; or  _______>> sprinkler system equipped with an alarm device, located at the most remote part of each system.

Route test connection to an exterior location or floor drain location, excluding janitor sinks, accepting full flow that will not result in negative consequences.

Supply discharge orifice with same size as corresponding sprinkler orifice.

Limit vertical height of exterior wall penetration to ​<< 2 ft; or  _______  ft>>​ above finished grade.

Backflow Preventer Test Connection:

Manufacturers:

Guardian Fire Equipment

Potter Roemer

<< _______>>

Substitutions:  << Alternate products may be accepted, follow Section 01 2500 - Substitution Procedures; or  Not permitted – No substitutions>>.

Provide downstream of the backflow prevention assembly, listed hose valves with 2.5 inch National Standard male hose threads with cap and chain.

Furnish one valve for each 250 gpm of system demand or fraction thereof.

Provide permanent sign reading "Test Valve".

      - ***************************************************************************************

      - If applicable to the project, only select one of Water Motor Alarm OR Electric Alarm Bell paragraphs.

      - ***************************************************************************************

Water Motor Alarm: Hydraulically operated impeller type alarm with aluminum alloy ​<< chrome plated;  red enameled; or  _______>>​ gong and motor housing, nylon bearings, and inlet strainer.

Manufacturers:

Reliable Automatic Sprinkler

Tyco Fire Products

Victaulic

Viking

​<< _______>>​

Substitutions: ​​<< Alternate products may be accepted, follow Section 01 2500 - Substitution Procedures; or  Not permitted – No substitutions>>​​.

      - *** OR ***

Electric Alarm Bell: Electrically operated ​​<< chrome plated;  red enameled; or  _______>>​​ gong with pressure alarm switch.

Manufacturers:

Edwards Signaling.

Potter Electric Signal Company, LLC

<< _______>>

Substitutions: ​<< Alternate products may be accepted, follow Section 01 2500 - Substitution Procedures; or  Not permitted – No substitutions>>​.

Supervisory Switches

Manufacturers

Potter Electric Signal Company, LLC

CoilKeeper Solenoid Supervisory Switch

SignaLink Bridge Wireless Supervisory System

​<< _______>>​

Substitutions: ​​<< Alternate products may be accepted, follow Section 01 2500 - Substitution Procedures; or  Not permitted – No substitutions>>​​.

Water Level Supervisory Switches

Manufacturers

Potter Electric Signal Company, LLC

​​<< _______>>​​

Substitutions: ​<< Alternate products may be accepted, follow Section 01 2500 - Substitution Procedures; or  Not permitted – No substitutions>>​.

Fire Department Connections

Type: ​<< Free standing;  Flush, wall mount; or  Exposed, projected wall mount>>​ made of corrosion resistant metal complying with <<UL 405>>.

Manufacturers:

Elkhart Brass Manufacturing Company, Inc.

Fire End & Croker Corporation

Potter Roemer

​​​<< _______>>​​​

Substitutions: << Alternate products may be accepted, follow Section 01 2500 - Substitution Procedures; or  Not permitted – No substitutions>>.

Inlets: ​​​<< Two;  Three;  Four; or  _______>>​​​ way, 2-1/2 inch swivel fittings, internal threaded. Thread size and inlets according to <<NFPA 1963>>. Brass caps with gaskets, chains, and lugs.

Configuration: ​​​<< Square; or  Linear>>​​​.

Outlet: Threaded ​​​​​<< 4 NPS;  5 NPS;  6 NPS; or  _______  NPS>>​​​​​.

Location: ​​​<< Back; or  Bottom>>​​​.

Rated Working Pressure: 175 psi.

Finish: ​​​<< Chrome;  Brass or bronze;  Polished brass; or  _______>>​​​.

Sleeve: ​​​<< Brass;  _______; or  None - N/A>>​​​ 18 inches height.

Signage: Raised or engraved lettering 1 inch minimum indicating system type.

PREACTION VALVE CONTROL PANEL

Manufacturers

Reliable Automatic Sprinkler

Tyco Fire Products

Viking

​<< _______>>​

Substitutions: ​​<< Alternate products may be accepted, follow Section 01 2500 - Substitution Procedures; or  Not permitted – No substitutions>>​​.

Provide a << modular; or  _______>> type control panel for electrically operated detection and extinguishing systems for each preaction valve.

Factory mount in surface mounted, steel cabinet with hinged doors​​<< , and cylinder lock; or  None - N/A>>​​.

Provide factory wired assembly containing components and equipment as required to perform specified system operating and supervisory functions.

Include isolation switch to allow system testing without activation of the preaction valve.

House batteries in separate and lockable, steel cabinet.

Finish interior and exterior of cabinet with ​<< enamel paint; or  _______>>​ and provide identification.

Include trouble lights and trouble alarm.

Provide 120 volt AC service transformed through a two-winding, isolation type transformer and rectified to low voltage DC for operation of all system actuating, signal sounding, trouble signal, and fire alarm tripping circuits.

Provide ​<< UL (DIR);  FM (AG); or  _______>>​ listed as an extinguishing system releasing panel and separate from the building's fire alarm control panel.

Secondary Power Supply:

Provide << nickel cadmium;  lead calcium;  sealed lead acid; or  _______>> rechargeable storage batteries and battery charger.

Storage Batteries:

Provide with sufficient ampere-hour rating to operate under ​<< supervisory;  trouble; and  _______>>​ conditions​<< , including audible trouble signal devices;  _______; or  None - N/A>>​ under alarm conditions for an additional ​<< 10; or  _______>>​ minutes and as required in accordance with the equipment listing.

Prevent contact between terminals of adjacent cells, battery terminals, and other metal parts with separate cell construction.

Battery Charger:

Provide solid-state automatic two rate type, capable of recharging completely discharged batteries to fully charged condition in << 24; or  _______>> hours or less.

Locate charger within control panel or battery cabinet.

Supervision: Refer to Section << 28 4600 - Fire Detection and Alarm>>​.

      - ***************************************************************************************

      - The following two articles are designer choices related to Dry Pipe and Preaction Fire Sprinkler Systems.

      - When considering Articles Air Compressor and/or Nitrogen Generator below - Consider application of bottled nitrogen where system size may not justify an air compressor or nitrogen generator.

      - ***************************************************************************************

AIR COMPRESSOR

Compressor: Single-unit, electric motor driven, motor, motor starter, safety valves, check valves, air maintenance device incorporating electric pressure switch and unloader valve.

Electrical Characteristics:

<< 1/3;  3/4;  1-1/2; or  _______>> hp.

​<< _______>>​ volts, ​<< single; or  three>>​ phase, 60 Hz.

NITROGEN GENERATOR

Nitrogen Generator: Provide <<FM (AG)>> approved system and accessories.

Minimum Nitrogen Purity: << 95;  98;  99; or  _______>> percent.

Provide piping and accessories to connect to dry and preaction fire suppression systems.

Electrical Characteristics:

​<< _______>>​ volts, ​<< single; or  three>>​ phase, 60 Hz.

Accessories:

Provide << control panel;  remote annunciator panel; or  _______>>.

Provide air maintenance device.

Provide nitrogen storage tank sized to comply with <<NFPA 13>>.

Provide purge valves to remove oxygen from the system.

Provide nitrogen analyzer to determine the nitrogen purity.

Provide system with replaceable filters.

PART 3 - EXECUTION

INSTALLATION

Install in accordance with referenced design and installation standards.

Provide pipe supports in accordance with <<NFPA 13>>.

Provide signage required by <<NFPA 13>> and <<NFPA 25>>.

Provide power and signal wiring in accordance with <<NFPA 70>>.

Install equipment in accordance with manufacturer's instructions.

Install direct-buried valves with a valve box. Provide post indicator.

Locate fire department connection with sufficient clearance from walls, obstructions, or adjacent siamese connectors to allow full swing of fire department wrench handle.

Locate outside alarm gong on building wall << as indicated; or  _______>>.

Place piping in concealed spaces above finished ceilings.

Center sprinklers in ​<< two directions in ceiling tile and provide piping offsets as required;  one direction only in ceiling tile with location in other direction variable, dependent upon spacing and coordination with ceiling elements; or  _______>>​.

Mask fire sprinklers to ensure that they do not receive field paint finish. Remove after painting.  Replace painted sprinklers.

      - ***************************************************************************************

      - The following paragraph is a designer-choice based on project-specific requirements and applies to air compressors.

      - ***************************************************************************************

Install air compressor on vibration isolators.

Below ground piping shall be flushed and documented prior to tie-in to above ground piping.  Ensure that all piping is free of foreign material at time of installation.

Install guards on sprinklers << where indicated;  located 7 feet or less above finished floor; or  _______>>.

Hydrostatically test entire system in accordance with <<NFPA 13>> and/or <<NFPA 24>> and Section << 22 0813 - Testing Piping Systems>>​.

Required inspections and testing shall be scheduled with, and witnessed by the Fire Marshal’s office.

INTERFACE WITH FIRE ALARM

Ensure required devices are installed and connected as required to fire alarm system in accordance with <<NFPA 72>>.

END OF SECTION

    - **********************************************************************************************

      - Do not omit the following reference information:

    - **********************************************************************************************

THE FOLLOWING STATEMENT IS FOR LANL USE ONLY

THIS PROJECT SPECIFICATION SECTION IS BASED ON LANL MASTER SPECIFICATION SECTION 21 1300, REV. 1, DATED APRIL 15, 2026.