Section 21 3000 
Fire Pumps

  - *************************************************************************************************************

    - LANL MASTER SPECIFICATION SECTION

Rev. 1 Summary of Changes: Edited and updated as required for import into SpecLink.

      - NOTE TO SPECIFIER ON USAGE IN SPECLINK: Activate the Section by turning on Seq #0000, followed by activating paragraphs in PART 1, Article SECTION INCLUDES. This will activate related articles, paras/subparas in the rest of the Section (i.e., PART 1 activates articles and paras/subparas in PARTS 2 and 3). If there are choice fields to edit the entire Section (typically in this first author note or beginning of the Section), make selections at those locations, which will filter through the remaining Section. All Articles, paragraphs and subparagraphs must be activated sequentially from top to bottom, unless noted otherwise.

      - This template must be edited for each project. In doing so, Specifier must add job-specific requirements. Selections and choice fields are used to indicate designer choices or locations where text must be supplied by the designer. The section must also be edited to remove requirements for processes, items, or designs that are not included in the project.

      - To seek a variance from applicable requirements in this Section, contact the Engineering Standards Manual (ESM) Fire POC  (LANL access only). Please contact POC with suggestions for improvement as well. LANL personnel should submit here: Suggested Change or Request Clarification; subcontractors via email to engstandards@lanl.gov.

      - When assembling a specification package, include applicable specifications from all Divisions, especially Division 1, General Requirements.

      - Section is developed for ML-4 projects.  For ML-1, 2, and 3 applications, additional requirements and independent reviews should be added if increased confidence in procurement or execution is desired; see LANL ESM Chapter 1 - General, Section Z10 Specifications and Quality sections.

      - Note that DOE-STD-1066 Appendices A and B are not applicable to the Work specified herein. Consider the scope and purpose of DOE documents as pertains to commercial construction before editing such requirements into this specification section.

  - *************************************************************************************************************

PART 1 - GENERAL

SECTION INCLUDES

      - ***************************************************************************************

      - The following paragraphs are designer choices based on project-specific conditions.

      - ***************************************************************************************

Fire Pumps:

Inline Fire Pump.

End-suction Fire Pump.

Split-case Fire Pump.

Vertical Turbine Fire Pump.

Electric Motor Drive.

Diesel Engine Drive.

Pressure Maintenance Pump.

Fire Pump Package Systems.

RELATED REQUIREMENTS

Section << 01 2500 - Substitution Procedures>>.

Section ​<< 01 4000 - Quality Requirements - Non-Nuclear>>​​.

Section << 01 7700 - Closeout Procedures>>.

Section ​<< 21 0500 - Common Work Results for Fire Suppression>>​.

Section ​<< 22 0713 - Plumbing and HVAC Insulation>>​.

Section << 26 2933 - Controllers for Fire Pump Drivers>>.

Section << 28 4600 - Fire Detection and Alarm>>​.

REFERENCE STANDARDS

ASCE 7 - Minimum Design Loads and Associated Criteria for Buildings and Other Structures.

NEMA EN 10250 - Enclosures for Electrical Equipment (1000 Volts Maximum).

NEMA MG 00001 - Motors and Generators.

NFPA 13 - Standard for the Installation of Sprinkler Systems.

NFPA 20 - Standard for the Installation of Stationary Pumps for Fire Protection.

NFPA 37 - Standard for the Installation and Use of Stationary Combustion Engines and Gas Turbines.

UL 448 - Centrifugal Stationary Pumps for Fire-Protection Service.

UL 778 - Standard for Motor-Operated Water Pumps.

UL 1004-5 - Fire Pump Motors.

UL 1247 - Diesel Engines for Driving Centrifugal Fire Pumps.

UL 1478 - Fire Pump Relief Valves.

ACTION SUBMITTALS

Product Data: Provide manufacturer’s literature including general assembly, pump curves  showing performance characteristics with pump and system, operating point indicated, Net Positive Suction Head (NPSH) curve, controls, wiring diagrams, and service connections.

Shop Drawings: Shop Drawings shall be in accordance with <<NFPA 20>>, to include but not limited to indication of layout, general assembly, components, dimensions, weights, center of gravity, clearances, and methods of assembly.

Special Certification from Manufacturer (only applicable if Fire Pump is a Designated Seismic System)

      - ***************************************************************************************

      - Commissioning Acceptance and Test Plans are typically generated by LANL Cx for nuclear facilities.

      - ***************************************************************************************

Commissioning Acceptance and Test Plan: Provided by << LANL Cx; or  Subcontractor>>​, the Commissioning Acceptance and Test Plan shall be submitted for approval by the Fire Marshal’s office prior to execution.

Test Reports: Indicate results of hydrostatic test, flushing, and field acceptance tests.

INFORMATIONAL SUBMITTALS

Project Record Documents: Record Documents reflecting final installed conditions. Include Drawings,​<< 3D Model; or  None - N/A>>​ and the corresponding hydraulic calculations.

Provide a fully executed copy of the Contractor’s Materials and Test Certificate for Fire Pump Systems.

Operation Data: Include manufacturer’s instructions, start-up data, trouble-shooting check lists, for pumps, drivers, and controllers, in accordance with <<NFPA 20>>.

Maintenance Data: Include manufacturers literature, cleaning procedures, replacement parts lists, and repair data for pumps, drivers and controllers.

Manufacturer’s standard warranty.

QUALITY ASSURANCE

Perform Work in accordance with <<NFPA 13>> and <<NFPA 20>>; where requirements differ comply with the most stringent.

Installer Qualifications: Company specializing in performing Work of this section << with minimum ______ years experience;  with minimum  ______  years experience and approved by the manufacturer;  with documented experience;  with documented experience and approved by the manufacturer; or  None - N/A>>​.

DELIVERY, STORAGE, AND HANDLING

Deliver fire pumps and components in factory packing. Comply with manufacturer's rigging and installation instructions.

Protect fire pumps and components from physical damage including effects of weather, water, and construction debris.

Provide temporary inlet and outlet caps, and maintain in place until installation.

PART 2 - PRODUCTS

    - **********************************************************************************************

      - Designated Seismic Systems (DSS): LANL Utility System is not seismically credited. Equipment that is designated DSS must be fed from a seismically credited generator or UPS.

    - **********************************************************************************************

SEISMIC PERFORMANCE REQUIREMENTS

Component importance factor of 1.0 is default unless noted otherwise on engineering drawings. If Fire Pump is a Designated Seismic System (DSS), component importance factor is 1.5.

The following nonstructural components (Fire Pumps) are seismically exempt per <<ASCE 7>>, Section 13.1.4, but shall be positively attached to the structure provided that:

Component weighs 400 lbs or less with center of mass located 4 ft or less above the adjacent floor level, flexible connections are provided between the component and associated conduit (Note: trade size 2.5 or less is considered flexible), and component importance factor is equal to 1.0 or

Component weighs 20 lbs or less.

For Fire Pumps outside the above exemptions, Engineer of Record shall provide support/anchorage details for the fire pumps that meet seismic requirements per LANL ESM Chapter 5 - Structural, Section II and <<ASCE 7>>. If the Fire Pump is a DSS, manufacturer shall provide special certification per <<ASCE 7>>, Section 13.2.2.

      - ***************************************************************************************

      - The following PART 2 Articles are designer choices based on project-specific conditions.

      - ***************************************************************************************

FIRE PUMPS

Inline Fire Pump

Manufacturers

AC Fire Pump, a Xylem brand.

Aurora, a Pentair brand.

Fairbanks Nijhuis, a Pentair brand.

SPP Pumps, Inc.

SyncroFlo, Inc.

Substitutions: ​<< Alternate products may be accepted, follow Section 01 2500 - Substitution Procedures; or  Not permitted – No substitutions>>​.

<<UL 448>>​​<< and UL 778; or  None - N/A>>​​; vertical- or horizontal-mounted, single-stage, close- coupled centrifugal pump for maximum working pressure of 186 psi.

Casing: Cast or ductile iron, or bronze with suction and discharge gauge port, casing wear ring, seal flush connection, drain plug, flanged suction and discharge.

Impeller: Bronze, fully enclosed, keyed directly to motor shaft.

Shaft: Solid alloy steel with bronze sleeve.

Seal: Carbon rotating against a stationary ceramic seat​<< viton fitted; or  None - N/A>>​, ​<< 225;  275; or  _______>>​ degrees F maximum continuous operating temperature.

Performance: ​<< As scheduled on the Drawings; or  As shown below>>​​

Capacity: << _______>> gpm at << _______>> psi of head.

Electric Motor Drive: << _______>> hp, << _______>> VAC, << single;  three; or  _______>> phase, 60 Hz.

End-Suction Fire Pump

Manufacturers

AC Fire Pump, a Xylem brand.

Aurora, a Pentair brand.

Fairbanks Nijhuis, a Pentair brand.

Patterson Pump Company, a Gorman-Rupp Company.

SPP Pumps, Inc.

SyncroFlo, Inc.

Substitutions: << Alternate products may be accepted, follow Section 01 2500 - Substitution Procedures; or  Not permitted – No substitutions>>.

<<UL 448>><< and UL 778; or  None - N/A>>​; horizontal-end-suction, single-stage centrifugal pump for maximum working pressure of 186 psi.

Casing: Cast iron, with suction and discharge gauge ports, renewable bronze casing wearing rings, seal flush connection, drain plug, flanged suction and discharge.

Impeller: Bronze double suction fully enclosed, balanced and keyed to shaft.

Bearings: Grease lubricated ball bearings, replaceable without opening casing.

Shaft: Alloy steel with replaceable bronze shaft sleeve.

Seal: Packing gland with minimum four rings graphite impregnated packing and bronze lantern rings, 230 degrees F maximum continuous operating temperature.

Drive: Flexible coupling with coupling guard.

Baseplate: Fabricated steel with integral drain rim.

        - ******************************************************************************

        - When choosing "As shown below" in the subparagraph below, the subparagraphs under it are to be considered by the designer.

        - ******************************************************************************

Performance: ​​<< As scheduled on the Drawings; or  As shown below>>​​

Capacity: << _______>> gpm at << _______>> psi of head.

          - **********************************************************************

          - The following two subparagraphs are designer choices.

          - **********************************************************************

Diesel Engine Drive: ​<< _______>>​ hp.

Electric Motor Drive: << _______>> hp, << _______>> VAC, << single;  three; or  _______>> phase, 60 Hz.

Split-Case Fire Pump

Manufacturers

AC Fire Pump, a Xylem brand.

Aurora, a Pentair brand.

Fairbanks Nijhuis, a Pentair brand.

Patterson Pump Company, a Gorman-Rupp Company.

SPP Pumps, Inc.

SyncroFlo, Inc.

Substitutions: << Alternate products may be accepted, follow Section 01 2500 - Substitution Procedures; or  Not permitted – No substitutions>>.

<<UL 448>>​<< and UL 778; or  None - N/A>>​; vertical- or horizontal-mounted, ​<< single-stage;  multistage; or  _______>>​, double-suction centrifugal pump for maximum working pressure of 294 psi.

Casing: Cast iron, with suction and discharge gauge ports, renewable bronze casing wearing rings, seal flush connection, drain plug, flanged suction and discharge.

Impeller: Bronze double suction fully enclosed, balanced and keyed to shaft.

Bearings: Grease lubricated ball bearings, replaceable without opening casing.

Shaft: Alloy steel with replaceable bronze shaft sleeve.

Seal: Packing gland with minimum four rings graphite impregnated packing and bronze lantern rings, 230 degrees F maximum continuous operating temperature.

Drive: Flexible coupling with coupling guard.

Baseplate: Cast iron << or fabricated steel;  _______; or  None - N/A>>​ with integral drain rim.

Performance: << As scheduled on the Drawings; or  As shown below>>

Capacity: << _______>> gpm at << _______>> psi of head.

Diesel Engine Drive: << _______>> hp.

Electric Motor Drive: << _______>> hp, << _______>> VAC, << single;  three; or  _______>> phase, 60 Hz.

Vertical Turbine Fire Pump

Manufacturers

Armstrong Fluid Technology.

Aurora, a Pentair brand.

Fairbanks Nijhuis, a Pentair brand.

Peerless Pump Company.

SPP Pumps, Inc.

SyncroFlo, Inc.

Substitutions: << Alternate products may be accepted, follow Section 01 2500 - Substitution Procedures; or  Not permitted – No substitutions>>.

<<UL 448>><< and UL 778; or  None - N/A>>; vertical, multistage centrifugal pump for well water source for maximum working pressure of 510 psi.

Casing: Cast iron rated for 1.20 times actual working pressure. Include discharge gauge, air vent, wear rings, seal flush connection, drain plug, and flanged discharge.

Impellers: Bronze, fully enclosed, keyed to shaft or secured with lock nut.

Shaft: Stainless steel or carbon steel with bronze or stainless steel sleeve through seal chamber.

Seals: Packing gland with minimum four rings graphite impregnated packing and bronze lantern rings.

Performance: << As scheduled on the Drawings; or  As shown below>>

Capacity: << _______>> gpm at << _______>> psi of head.

Diesel Engine Drive: << _______>> hp.

Electric Motor Drive: << _______>> hp, << _______>> VAC, << single;  three; or  _______>> phase, 60 Hz.

      - ***************************************************************************************

      - Retain the paragraph below, and any accessories, as applicable to the project.

      - ***************************************************************************************

Accessories

Eccentric suction reducer and Open Stem & Yoke (OS&Y) gate or butterfly valve on suction side of pump.

Concentric reducer and check valve in pump discharge and OS&Y gate or butterfly valve on system side of check valve.

Fire pump bypass fitted with OS&Y gate or butterfly valves and check valve.

Main relief valve, <<UL 1478>>,<< and enclosed type waste cone;   and open type waste cone;  _______; or  None - N/A>>.

Suction pressure gauge, 4-1/2 inch diameter dial with snubber, valve cock and lever handle.

Discharge pressure gauge mounted on board attached to pump, with snubber, valve cock and lever handle.

3/4 inch casing relief valve.

Float operated << 3/4;  one; or  _______>> inch automatic air release valve.

Hose valve manifold with 2-1/2 inch hose gate valves with caps and chains.

Flow metering system for closed loop testing.

ELECTRIC MOTOR DRIVE

Motor: Squirrel cage induction type; listed for fire protection service in accordance with <<UL 1004-5>>; <<NEMA MG 00001>>; in open drip-proof <<NEMA EN 10250>> enclosure, << 3,500;  1,750; or  _______>> rpm.

Controller: Refer to Section << 26 2933 - Controllers for Fire Pump Drivers>>.

DIESEL ENGINE DRIVE

Diesel Engine: Comply with requirements of <<NFPA 20>>, <<NFPA 37>> and <<UL 1247>>; automatic operation with overspeed/overcrank switch and drive, two contactor switches, low oil pressure and high water temperature warning switches, and fuel shut-off solenoid, with wiring terminating in junction box.

Include the following engine accessories

Stub shaft.

Oil bath air cleaner.

Water cooled exhaust manifold.

Heat exchanger.

Mechanical speed governor.

Fuel filter.

Lube oil filter and by-pass valve.

Lube oil cooler and relief valve.

Fuel pump.

Instrument panel with tachometer, hour meter, oil pressure gauge, water temperature gauge, ammeter, hand speed control and start switch.

Starting system including generator/alternator, starting motor and voltage regulator.

Exhaust silencer, residential type.

Flexible exhaust tubing, << 24; or  _______>> inches long.

Thermal insulation for personnel protection on exhaust shall comply with Section << 22 0713 - Plumbing and HVAC Insulation>>​.

Cooling Water System: Closed system with cooling water supply to heat exchanger from fire pump discharge. Include four manual shut-off valves (including by-pass line), two strainers, pressure regulating valve, automatic solenoid valve and pressure gauge.

Storage Batteries: Dual lead acid batteries with cables and battery racks.

Fuel Tank: << _______>> gal above ground storage tank, fill pipe and cap, manual shut-off valve, flame arrestor, oil level gauge, braided bronze flexible connectors, seamless type L copper tubing with flared joints. Fill tank at completion.

Engine Controller: Refer to Section << 26 2933 - Controllers for Fire Pump Drivers>>.

PRESSURE MAINTENACE PUMP

Manufacturers:

Armstrong Fluid Technology.

Aurora, a Pentair brand.

Fairbanks Nijhuis, a Pentair brand.

Grundfos.

Talco Fire Systems.

Substitutions: << Alternate products may be accepted, follow Section 01 2500 - Substitution Procedures; or  Not permitted – No substitutions>>.

Electrically operated, horizontal or vertical, single or multi stage, << turbine;  close-coupled; or  _______>> type centrifugal pump with standard open drip-proof horizontal motor.

Controller: Refer to Section << 26 2933 - Controllers for Fire Pump Drivers>>​.

Performance: << As scheduled on the Drawings; or  As shown below>>

Capacity: << _______>> gpm at << _______>> feet of head.

Electric Motor Drive: << _______>> hp, << _______>> VAC, << single;  three; or  _______>> phase, 60 Hz.

FIRE PUMP PACKAGE SYSTEMS

Manufacturers:

Armstrong Fluid Technology.

SPP Pumps, Inc.

SyncroFlo, Inc.

Substitutions: << Alternate products may be accepted, follow Section 01 2500 - Substitution Procedures; or  Not permitted – No substitutions>>.

Description: Factory built, skid-mounted, custom-assembled fire pump package. Unit to be pretested and ready to use. Include system controller, piping, fittings, valves, and other required externally mounted components and accessories for field installation.

Package Configuration

        - ******************************************************************************

        - Retain only one of the two following subparagraphs.

        - ******************************************************************************

<< One;  Two;  Three; or  ______>> << end-suction;  split-case; or  turbine>> type fire pump(s) with electric motor drive prewired into associated starter.<< Package to include pressure maintenance pump prewired into associated starter.; or  None - N/A>>​

        - *** OR ***

​<< One;  Two;  Three; or  _______>>​ ​<< end-suction;  split-case; or  turbine>>​ type fire pump(s) with diesel engine drive and reserve tank. ​<< Package to include pressure maintenance pump prewired into associated starter.; or  None - N/A>>​

Pipe-installed system visual indicating flow meter prewired into junction box for remote monitoring.

Prewire alarm and trouble or fault contacts into central junction box or panel for field interface by fire alarm system.

        - ******************************************************************************

        - Select subparagraph below if fire pump is outdoors.

        - ******************************************************************************

Package System Housing Enclosure:

Weatherproof enclosure with lockable door.

Thermostat-controlled enclosure heating and ventilation.

Indoor and outdoor lighting with respective light switches.

Insulated wall panel assembly according to climatic data in ESM Chapter 6 - Mechanical, Section D30, Table D30GEN-1.

<< _______>>.

PART 3 - EXECUTION

INSTALLATION

Install fire pump in accordance with <<NFPA 20>> and manufacturer’s installation instructions.

      - ***************************************************************************************

      - The paragraph below is a designer choice based on project-specific conditions.

      - ***************************************************************************************

Install diesel engine drive in accordance with <<NFPA 20>>, <<NFPA 37>> and manufacturer’s installation instructions.

Provide access space around pumps for service; no less than minimum as recommended by manufacturer.

Piping: Decrease from line size with long radius reducing elbows or reducers. Support piping adjacent to pump such that no weight is carried on pump casings. For base mounted pumps, provide supports under elbows on pump suction and discharge; see Section << 21 0500 - Common Work Results for Fire Suppression>>.

Provide drains for bases and seals, piped to and discharging into floor drains.

Lubricate pumps before start-up.

Check, align, and certify pumps by qualified installer prior to start-up.

Provide supervisory alarm notifications using auxiliary dry contacts interconnected into fire alarm system for monitoring by LANL Emergency Operations Support Center (EOSC); see Section << 28 4600 - Fire Detection and Alarm>>​.

FIELD QUALITY CONTROL

      - ***************************************************************************************

      - Field acceptance tests are part of the formal process to verify compliance with  NFPA 20; therefore, all pre-acceptance testing preparation should be complete before scheduling the tests for witnessing by authorities having jurisdiction.

      - ***************************************************************************************

See Section << 01 4000 - Quality Requirements - Non-Nuclear>>, for additional requirements.

Perform hydrostatic testing, flushing, and field acceptance testing required by <<NFPA 20>>. Subcontractor shall coordinate date, time and location of field acceptance test with LANL STR and AHJ.

Flushing shall precede hydrostatic testing.

Flushing and hydrostatic testing shall precede field acceptance testing.

Perform field acceptance tests in the presence of Fire Marshal, and <<NFPA 20>> required manufacturer’s representatives.

Acceptance Tests and Inspections:

Do not begin field acceptance testing until suction piping has been flushed and hydrostatically tested and the certificate for flushing and testing has been submitted to LANL STR, Design Agency, and AHJ.

Prior to starting, notify authorities having jurisdiction of the time and place of the acceptance testing.

Engage manufacturer's factory-authorized service representative to be present during the testing.

Perform field acceptance tests as outlined in <<NFPA 20>>.

      - ***************************************************************************************

      - See << 01 4000 - Quality Requirements - Non-Nuclear>> for retesting and reinspecting requirements.

      - ***************************************************************************************

Nonconforming Work:

Fire pumps will be considered defective if they do not pass tests and inspections.

For nonconformance, adjust and retest. Repeat until conformance is achieved.

Prepare test and inspection reports.

CLOSEOUT ACTIVITIES

See Section << 01 7700 - Closeout Procedures>> for additional requirements.

Demonstrate automatic operation of system including verification of pressure switch set points to LANL.

Use operation and maintenance data as reference during demonstration.

Briefly describe function, operation, and maintenance of each component.

Training: Train LANL's personnel on operation and maintenance of system.

Use operation and maintenance manual as training reference, supplemented with additional training materials as required.

Provide minimum of << two hours;  one day; or  _______>> of training.

Instructor: Manufacturer's training personnel.

Location: << At project site;  LANL's offsite classroom facilities may be used;  Provide local classroom facilities; or  At manufacturer's training facility>>; << include travel expenses for one member of LANL's staff.;  include travel expenses for two members of LANL's staff.;  include travel expenses for  _______  member(s) of LANL's staff.; or  None - N/A>>

END OF SECTION

    - **********************************************************************************************

      - Do not omit the following reference information:

    - **********************************************************************************************

THE FOLLOWING STATEMENT IS FOR LANL USE ONLY

THIS PROJECT SPECIFICATION SECTION IS BASED ON LANL MASTER SPECIFICATION SECTION 21 3000, REV. 1, DATED APRIL 15, 2026.