Section 22 0529 
Hangers and Supports for Plumbing Piping and Equipment

  - *************************************************************************************************************

    - LANL MASTER SPECIFICATION SECTION

Rev. 8 Summary of Changes: Edited and updated as required for import into SpecLink.

      - NOTE TO SPECIFIER ON USAGE IN SPECLINK: Activate the Section by turning on Seq #0000, followed by activating paragraphs in PART 1, Article SECTION INCLUDES. This will activate related articles, paras/subparas in the rest of the Section (i.e., PART 1 activates articles and paras/subparas in PARTS 2 and 3). If there are choice fields to edit the entire Section (typically in this first author note or beginning of the Section), make selections at those locations, which will filter through the remaining Section. All Articles, paragraphs and subparagraphs must be activated sequentially from top to bottom, unless noted otherwise.

      - This template must be edited for each project. In doing so, Specifier must add job-specific requirements. Selections and choice fields are used to indicate designer choices or locations where text must be supplied by the designer. The section must also be edited to remove requirements for processes, items, or designs that are not included in the project.

      - To seek a variance from applicable requirements in this Section, contact the Engineering Standards Manual (ESM) Mechanical/Pressure Safety POC  (LANL access only). Please contact POC with suggestions for improvement as well. LANL personnel should submit here: Suggested Change or Request Clarification; subcontractors via email to engstandards@lanl.gov.

      - When assembling a specification package, include applicable sections from all Divisions, especially Division 1, General Requirements.

      - Section is developed for ML-4 projects. For ML-1, 2, and 3 applications, additional requirements and independent reviews should be added if increased confidence in procurement or execution is desired; see LANL ESM Chapter 1 - General, Section Z10 Specifications and Quality sections.

      - This template is developed for piping that requires support of only gravity loads using MSS SP-58 pipe hangers and supports. MSS SP-58 is not suitable for seismic supports. For seismic supports, designers are referenced to MSS SP-127, Bracing For Piping Systems: Seismic – Wind – Dynamic Design, Selection, and Application. The Designer is cautioned that MSS SP-127 may not be a listed standard based on the ASME Code of Record.

  - *************************************************************************************************************

PART 1 - GENERAL

SECTION INCLUDES

Furnish and install pipe hangers, supports, hanger rods, and sleeves, and other positive fastenings for mechanical non-structural components such that gravity loads are safely transferred to the structure.

        - ******************************************************************************

        - The following subparagraphs are designer choices based on project-specific conditions.

        - ******************************************************************************

Pipe Hangers and Supports

Hanger Rods

Sleeves

Steel Metal Framing Channel Pipe Supports

      - ***************************************************************************************

      - The Section listed below may need to be selected when the project requires seismic control/protection for plumbing piping and equipment.

      - Section ​<< 22 0548.23 - Vibration and Seismic Controls for Mechanical Systems>>​

      - ***************************************************************************************

Related REQUIREMENTS

Section ​<< 01 2500 - Substitution Procedures>>​

Section ​​<< 01 4444 - Offsite Welding, Brazing and Joining Requirements>>​​

Section ​<< 01 4455 - Onsite Welding, Brazing and Joining Requirements>>​

Section ​<< 01 4525 - Non-Destructive Examination (NDE) Requirements>>​

Section << 05 0520 - Post-Installed Concrete and Grouted Masonry Anchors - Normal Confidence>>​

Section ​<< 07 8400 - Firestopping>>​

Section ​<< 09 9100 - Painting>>​

Section << 22 0548.23 - Vibration and Seismic Controls for Mechanical Systems>>

Section ​<< 22 0713 - Plumbing and HVAC Insulation>>​​

REFERENCE STANDARDS

      - ​​​<< All national standards invoked herein shall be taken to be the edition in effect for the code of record listed in the design drawings, unless noted otherwise; or  All national standards invoked below and herein shall be taken to be the latest edition>>​​​.

      - ASME B1.1 - Unified Inch Screw Threads (UN, UNR, and UNJ Thread Forms).

ASME B18.2.1 - Square, Hex, Heavy Hex, and Askew Head Bolts and Hex, Heavy Hex, Hex Flange, Lobed Head, and Lag Screws (Inch Series).

ASME B18.2.2 - Nuts for General Applications: Machine Screw Nuts; and Hex, Square, Hex Flange, and Coupling Nuts (Inch Series).

ASME B18.21.1 - Washers: Helical Spring-Lock, Tooth Lock, and Plain Washers (Inch Series).

ASME B31.1 - Power Piping.

ASME B31.3 - Process Piping.

ASME B31.5 - Refrigeration Piping and Heat Transfer Components.

ASME B31.9 - Building Services Piping.

ASTM A123/A123M - Standard Specification for Zinc (Hot-Dip Galvanized) Coatings on Iron and Steel Products.

ASTM A307 - Standard Specification for Carbon Steel Bolts, Studs, and Threaded Rod 60 000 PSI Tensile Strength.

ASTM A576 - Standard Specification for Steel Bars, Carbon, Hot-Wrought, Special Quality.

ASTM A653/A653M - Standard Specification for Steel Sheet, Zinc-Coated (Galvanized) or Zinc-Iron Alloy-Coated (Galvannealed) by the Hot-Dip Process.

ASTM A1011/A1011M - Standard Specification for Steel, Sheet and Strip, Hot-Rolled, Carbon, Structural, High-Strength Low-Alloy, High-Strength Low-Alloy with Improved Formability, and Ultra-High Strength.

ASTM B633 - Standard Specification for Electrodeposited Coatings of Zinc on Iron and Steel.

AWS D1.1/D1.1M - Structural Welding Code - Steel.

IAPMO (UPC) - Uniform Plumbing Code.

MFMA-4 - Metal Framing Standards Publication.

MSS SP-58 - Pipe Hangers and Supports - Materials, Design, Manufacture, Selection, Application, and Installation.

NFPA 13 - Standard for the Installation of Sprinkler Systems.

NFPA 54 - National Fuel Gas Code.

SAE J429 - Mechanical and Material Requirements for Externally Threaded Fasteners.

ACTION SUBMITTALS

Product Data: For each type of product indicated.

      - ***************************************************************************************

      - Shop drawing submittals are typically not required for ML-4 projects, but may be required for engineered supports regardless of ML.

      - ***************************************************************************************

Shop Drawings: Show fabrication and installation details​<< and include calculations; or  None - N/A>>​ for the following, as applicable for the project:

Trapeze pipe hangers.

Metal framing systems.

Pipe stands.

      - ***************************************************************************************

      - The following two paragraphs should only be selected for custom fabrications.

      - ***************************************************************************************

For custom fabrications, per the requirements of Sec << 01 4444 - Offsite Welding, Brazing and Joining Requirements; and  01 4455 - Onsite Welding, Brazing and Joining Requirements>>, submit:

        - ******************************************************************************

        - For high risk applications such as ML-1 or ML-2, add submittals for “Weld Filler Material Control Procedures” and “Filler Material Certified Material Test Reports (CMTRs)” when required. Add “Post-Weld Heat Treatment Procedures” when required.

        - ******************************************************************************

        - *******Note: Only required as a submittal for Onsite welding, when subcontractor not using LANL WPS/PQR*******

Welding Procedure Specification (WPS) and supporting Procedure Qualification Record (PQR).

        - ********Note: Only required as a submittal for Onsite welding, when subcontractor not tested at LANL*******

Welder Performance Qualification Records (WPQR) including continuity.

For custom fabrications, per the requirements of Section ​<< 01 4525 - Non-Destructive Examination (NDE) Requirements>>​​, submit:

Written Practice or procedure for qualification and certification of NDE Personnel.

NDE Personnel Qualification Records.

NDE Procedures.

NDE Procedure Qualification Records (when required by code)

NDE Report(s).

QUALITY ASSURANCE

      - ***************************************************************************************

      - Select only the codes/standards applicable to the project.

      - ***************************************************************************************

Hangers and supports shall conform to the requirements of the following codes and standards as applicable:

<<ASME B31.1>>, Power Piping

<<ASME B31.3>>, Process Piping

<<ASME B31.5>>, Refrigeration Piping and Heat Transfer Components

<<ASME B31.9>>, Building Services Piping

<<IAPMO (UPC)>>​, Uniform Plumbing Code

<<NFPA 13>>, Standard for the Installation of Sprinkler Systems

<<NFPA 54>>, National Fuel Gas Code

<<MSS SP-58>>, Pipe Hangers and Supports – Materials, Design, Manufacture, Selection, Application, and Installation

Qualify welding processes and welding operators in accordance with <<AWS D1.1/D1.1M>>​ for hangers and supports.

PART 2 - PRODUCTS

PRODUCT OPTIONS AND SUBSTITUTIONS

Alternate products may be accepted; follow Section ​<< 01 2500 - Substitution Procedures>>​.

PIPE HANGERS AND SUPPORTS

      - ***************************************************************************************

      - The supports listed below are typical options from MSS SP-58. Designer to select applicable support types based on project requirements.

      - ***************************************************************************************

Hangers for Pipe Sizes 1/2 to 1-1/2 inches: Malleable iron or carbon steel, adjustable swivel or  split ring. <<MSS SP-58>>, Type ​<< 10;  11; or  ______>>​​.

Hangers for Cold Pipe Sizes 2 inches and over: Carbon steel, adjustable, clevis. <<MSS SP-58>>, Type ​<< 1; or  ______>>​​.

Hangers for Hot Pipe Sizes 2 to 4 inches: Carbon steel, adjustable, clevis. <<MSS SP-58>>, Type ​<< 1; or  ______>>​.

Hangers for Hot Pipe Sizes 6 inches and over: Adjustable steel yoke, cast iron roll, double hanger. <<MSS SP-58>>, Type ​<< 43; or  ______>>​.

Multiple or Trapeze Hangers: Steel channels with welded spacers and hanger rods. <<MSS SP-58>>, Type ​<< 59; or  ______>>​.

Multiple or Trapeze Hangers for Hot Pipe Sizes 6 inches and over: Steel channels with welded spacers and hanger rods. <<MSS SP-58>>, Type ​<< 59; or  ______>>​. Cast iron roll <<MSS SP-58>>, Type ​<< 45;  46; or  ______>>​.

Wall Support for Pipe Sizes to 3 inches: Strut clamp <<MSS SP-58>>, Type ​<< 26; or  ______>>​.

Wall Support for Pipe Sizes 4 inches and over: Welded steel bracket and wrought steel clamp. <<MSS SP-58>>, Type ​<< 31;  32;  33; or  ______>>​.

Wall Support for Hot Pipe Sizes 6 inches and over: Welded steel bracket <<MSS SP-58>>, Type ​<< 31;  32;  33; or  ______>>​ and wrought steel clamp with adjustable steel yoke and cast-iron roll <<MSS SP-58>>, Type ​<< 46; or  ______>>​.

Vertical Support: Steel riser clamp. MSS-SP-58, Type ​<< 8; or  ______>>​.

Floor Support for Cold Pipe: Cast iron adjustable pipe saddle, lock nut, nipple, floor flange, and concrete pier or steel support. <<MSS SP-58>>, Type ​<< 38; or  ______>>​.

Floor Support for Hot Pipe Sizes to 4 inches: Cast iron adjustable pipe saddle, lock nut, nipple, floor flange, and concrete pier or steel support. <<MSS SP-58>>, Type ​<< 38; or  ______>>​.

Floor Support for Hot Pipe Sizes 6 inches and over: Adjustable cast iron roll and stand, steel screws, and concrete pier or steel support. <<MSS SP-58>>, Type ​<< 46; or  ______>>​.

Copper Pipe Support: <<MSS SP-58>>, Types 1 through 65, non-metallic coating, jacket, or liner on steel factory-fabricated components.

HANGER RODS

Mild steel threaded both ends, threaded on one end, or continuous threaded.

Rods for trapeze hangers shall be a minimum 3/8-inch.  The use of pipe hooks, chains, perforated iron strapping, or wire for pipe supports are NOT permitted.

SLEEVES

      - ***************************************************************************************

      - Designer to select paragraphs below that are applicable to the project.

      - ***************************************************************************************

Sleeves for Pipes through Non-Fire Rated Beams, Walls, Footings, and Floors:  Steel pipe or 18 gage galvanized steel.

Sleeves for Pipes through Fire Rated and Fire Resistive Floors, Walls, and Roof: Prefabricated fire rated sleeves including seals, approved by a nationally recognized testing laboratory (UL listed).

Sleeves for Ductwork: Galvanized steel.

STEEL METAL FRAMING CHANNEL PIPE SUPPORTS

Supplier: ​<< Unistrut;  B-Line;  Power-Strut; or  ______>>​

Solid structural channel

Size: ​<< 1-5/8" x 1-5/8"; or  ______>>​, Solid

Gage:  ​<< 12;  14;  16; or  ______>>​.

Material: ​​<< ASTM A653/A653M SS GR 33; or  ASTM A1011/A1011M SS GR 33>>​​.

        - ******************************************************************************

        - Designer to select finish based on availability from manufacturer.

        - ******************************************************************************

Finish: ​​<< Pre-Galvanized;  Hot-Dipped Galvanized ASTM A123/A123M; or  Perma-Green ® II, E-Coat>>​​.

Channel conforming to Metal Framing Standards Publication <<MFMA-4>>​.

Channel Nuts​​<< With Springs; or  None - N/A>>​​:

Material: ​<< ASTM A576 GR 101; or  ______>>​.

Finish: Electro-galvanized per <<ASTM B633>> Type III SC1 finish.

Threads: <<ASME B1.1>>, coarse series (UNC) class 2, <<ASME B18.2.2>>

Part number(s) and size(s): << _______>>.

Hex Head Cap Screws:

Material: <<SAE J429>> GR 2 meets and exceeds <<ASTM A307>>

Finish: Electro-galvanized per <<ASTM B633>>​ Type III SC1 finish.

Threads: <<ASME B1.1>>, coarse series (UNC) class 2, <<ASME B18.2.1>>.

Part number(s) and size(s) (diameter x length): << _______>>.

Flat Washer:

Finish: Electro-galvanized per <<ASTM B633>>​ Type III SC1 finish.

Dimensions conforming to <<ASME B18.21.1>>

Part number(s) and size(s): ​<< _______>>​.

      - ***************************************************************************************

      - Consult catalog to obtain exact part numbers for pipe clamps being used. Size clamps to include insulation thickness.

      - ***************************************************************************************

Pipe Clamp:

Part number(s) and size(s): << _______>>.

PART 3 - EXECUTION

    - **********************************************************************************************

      - Verify that supporting structural elements are adequate to support the imposed hanger load.

    - **********************************************************************************************

PIPE HANGERS AND SUPPORTS

Support piping to maintain its alignment and prevent sagging.

Place hangers within 12 inches of each horizontal elbow.

Support vertical piping with riser clamps secured to the piping and resting on the building structure at each floor.

Install hangers to provide minimum 1/2 inches space between finished covering and adjacent work.

Use hangers with 1-1/2 inches minimum vertical adjustment.

Where several pipes can be installed in parallel and at same elevation, provide multiple or trapeze hangers.

Support riser piping independently of connected horizontal piping.

Provide coated, jacketed, or liner on steel hangers and supports for copper piping.

For nonmetallic piping, hangers and support shall comply with <<MSS SP-58>>, Section 5.3.6.​

      - ***************************************************************************************

      - Designer shall select the paragraph below when Section << 22 0713 - Plumbing and HVAC Insulation>> is included in the project specification package.

      - ***************************************************************************************

Provide insulation continuous through hangers and rollers.  Protect insulation by steel shields in accordance with Section ​<< 22 0713 - Plumbing and HVAC Insulation>>​.

Provide hangers on piping on each side of, and within 6 inches of, hubless pipe couplings so the couplings will bear no weight.

Provide supports that allow free axial movement and only support the weight of the piping or tubing. Provide additional hangers or brackets to support valves, flanges, specialties, etc., to prevent excessive deflection.

Prime coat exposed steel hangers and supports.  Refer to Section ​<< 09 9100 - Painting>>​.  Hangers and supports located in crawl spaces, pipe shafts, and suspended ceiling spaces are not considered exposed.

Refer to Section ​​​<< 05 0520 - Post-Installed Concrete and Grouted Masonry Anchors - Normal Confidence>>​​​​, for installation of support anchors for the steel metal framing channel pipe support post base.

Installation of fasteners for steel metal framing channel pipe supports:

Align the component and hand tighten bolt and nut.  Tighten the bolt to appropriate torque value shown in the manufacturer’s literature.

Torque tolerances:

2 ft-lbs if torque value is 50 ft-lbs or less

4 ft-lbs if torque value is greater than 50 but less than 100 ft-lbs

4% of torque value if greater than 100 ft-lbs.

Final bolt torque values (non-lubricated) shall be in accordance with ​​<< manufacturer’s literature; or  as shown below>>​​.

        - ******************************************************************************

        - When selecting the table below, designer shall edit it to match manufacturer’s literature for the selected steel metal framing channel pipe supports.

        - ******************************************************************************

| Bolt Size | ¼”-20 | 5/16”-18 | 3/8”-16 | ½”-13 | 5/8”-11 | ¾”-10 |
| --- | --- | --- | --- | --- | --- | --- |
| Torque (Ft-lbs) | 6 | 11 | 19 | 50 | 100 | 125 |
| Torque (N-m) | 8 | 15 | 25 | 68 | 135 | 170 |

SLEEVES

Provide sleeves for all pipe penetrations through walls, roof, or slab above grade.

Neatly cut holes in existing walls, floors, or roof for placement of sleeves.  Place sleeve and grout and caulk annular space to provide finished appearance.

Extend sleeves through floor slab 2 inches above finished floor level.  Caulk sleeves full depth and provide floor plate.

Seal space between pipe and sleeve watertight for all sleeves penetrating the roof.

      - ***************************************************************************************

      - The following is a designer choice.

      - ***************************************************************************************

Where piping or ductwork penetrates a fire rated wall or floor, provide fire-stopping insulation so that the assembly when complete retains the fire rating of construction penetrated by the sleeve. Refer to Section ​​<< 07 8400 - Firestopping>>​​ for additional information on firestopping details.

HANGER SPACING

      - ***************************************************************************************

      - The hanger spacing tables are for straight runs of standard and heavier steel pipe, Type L and heavier copper tube, stainless steel tube, and polyvinyl chloride (PVC)/ chlorinated polyvinyl chloride (CPVC) thermoplastic pipe.  They are not intended to be used as specifications for all installations.  These do not apply where span calculations are made or where there are concentrated loads between supports, such as flanges, valves, specialties, etc, or changes in direction requiring additional supports.

      - For Victaulic flexible systems and other piping material, consult with the manufacturer for suggested hanger spacing.  For Victaulic rigid couplings used in steel piping systems, the spacing below may be used.​

      - Designer shall make selections throughout the article below to reflect piping systems and materials included in the project.

      - ***************************************************************************************

Plumbing Piping – Water, Gas, Drain, Waste and Vent (DWV)

Comply with the requirements of UPC for hanger spacing and materials.

Maximum Hanger Spacing from UPC, Table 313.3:

| Materials | Types of Joints | Horizontal | Vertical​ |
| --- | --- | --- | --- |
| Cast | Lead and Oakum | 5 feet, except 10 feet where 10-foot lengths are installed1,2,3 | Base and each floor, not to exceed 15 feet |
|  | Compression Gasket | Every other joint, unless over 4 feet then support each joint1,2,3 | Base and each floor, not to exceed 15 feet |
| Cast-Iron Hubless | Shielded Coupling | Every other joint, unless over 4 feet then support each joint1,2,3,4 | Base and each floor, not to exceed 15 feet |
| Copper & Copper Alloys | Soldered, Brazed, Threaded, or Mechanical | 1½ inches and smaller, 6 feet; 2 inches and larger, 10 feet | Each floor, not to exceed 10 feet5 |
| Steel Pipe for Water or DWV | Threaded or Welded | ¾ inch and smaller, 10 feet; 1 inch and larger, 12 feet | Every other floor, not to exceed 25 feet5 |
| Schedule 40 PVC and ABS DWV | Solvent Cemented | All sizes, 4 feet; allow for expansion every 30 feet3 | Base and each floor; provide mid-story guides; provide for expansion every 30 feet |
| CPVC | Solvent Cemented | 1 inch and smaller, 3 feet; 1¼ inches and larger, 4 feet | Base and each floor; provide mid-story guides |
| CPVC-AL-CPVC | Solvent Cemented | ½ inch, 5 feet; ¾ inch 65 inches; 1 inch, 6 feet | Base and each floor; provide mid-story guides |
| Notes: 1) Support adjacent to joint, not to exceed 18 inches. 2) Brace not to exceed 40 foot intervals to prevent horizontal movement. 3) Support at each horizontal branch connection. 4) Hangers shall not be placed on the coupling. 5) Vertical water lines shall be permitted to be supported in accordance with recognized engineering principles with regard to expansion and contraction, where first approved by the Authority Having Jurisdiction. |  |  |  |

Fire Protection Piping:

Comply with the requirements of <<NFPA 13>> for hanger spacing and materials.

Facility Natural Gas Piping

Comply with the requirements of <<NFPA 54>> for hanger spacing and materials.

Maximum Hanger Spacing from <<NFPA 54>>, Table 7.2.6.2:

| Size (NPS) | ½ | ¾ to 1 | 1 ¼ or larger |
| --- | --- | --- | --- |
| Spacing (Feet) Steel Pipe | 6 | 8 | 10 |

Steam/Condensate Piping per <<ASME B31.9>>​ Code of Record

Maximum Hanger Spacing:

| Size (NPS) | 1 | 1 ¼ | 1 ½ | 2 | 3 | 4 | 6 | 8 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Spacing (Feet) Steel Pipe | 9 | 11 | 13 | 15 | 17 | 21 | 25 | 28 |

Steam/Condensate Piping per <<ASME B31.1>>​ Code of Record

Maximum Hanger Spacing:

| Size (NPS) | 1 to 1 ½ | 2 | 3 | 4 | 6 | 8 |
| --- | --- | --- | --- | --- | --- | --- |
| Spacing (Feet) Steel Pipe | 9 | 13 | 15 | 17 | 21 | 24 |

Water Building Services Piping (Heating, Cooling, and Tower Water)

Comply with the requirements of <<ASME B31.9>>.

Maximum Hanger Spacing:

| Size (NPS) | Less Than 1 | 1 | 1¼ | 1½ | 2 | 3 | 4 | 6 | 8 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |

Hidden Paragraph

| Spacing (Feet) Steel Pipe | 6 | 9 | 11 | 12 | 13 | 16 | 18 | 23 | 25 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |

Hidden Paragraph

| Spacing (Feet) Copper Tube | 5 | 7 | 7 | 8 | 9 | 10 | 12 | 14 | 16 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |

Compressed Air Building Services Piping

Comply with the requirements of <<ASME B31.9>>.

Maximum Hanger Spacing:

| Size (NPS) | ¼ to ½ | 5/8 to 7/8 | 1 | 1¼ | 1½ | 2 | 3 | 4 | 6 | 8 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |

Hidden Paragraph

| Spacing (Feet) Steel Pipe | 6 | 6 | 9 | 11 | 13 | 15 | 17 | 21 | 25 | 28 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |

Hidden Paragraph

| Spacing (Feet) Copper/SS Tube | 3 | 5 | 7 | 9 | 10 | 12 | 15 | 17 | 21 | 24 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |

Laboratory Gas Piping per <<ASME B31.3>> Code of Record

Maximum Hanger Spacing based on <<MSS SP-58>>, Table 4:

| Size (NPS) | ¼ to ½ | 5/8 to 7/8 | 1 | 1¼ | 1½ | 2 | 3 | 4 | 6 | 8 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |

Hidden Paragraph

| Spacing (Feet) Copper Tube | 5 | 7 | 8 | 9 | 10 | 11 | 14 | 16 | 20 | 23 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |

Hidden Paragraph

| Spacing (Feet) SS Tube | 8 | 9 | 9 | 9 | 12 | 13 | 15 | 17 | 21 | 24 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |

Nonmetallic Process Piping, up to 100°F

Maximum Hanger Spacing based on <<MSS SP-58>>, Table 4:

      - ***************************************************************************************

      - For other thermoplastic materials, consult with manufacturer installation guidelines. Maximum support spacing is often a function of pipe size, design temperature, and specific gravity of system fluid. If using other thermoplastic materials, the table below shall be edited.

      - ***************************************************************************************

| Size (NPS) | ¼ to ½ | 5/8 to 7/8 | 1 | 1 ¼ | 1 ½ | 2 | 3 | 4 | 6 | 8 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |

Hidden Paragraph

| Spacing (Feet) PVC Pipe | 3.5 | 4 | 4.5 | 5 | 5 | 5 | 6 | 7.5 | 7.5 | 8 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |

Hidden Paragraph

| Spacing (Feet) CPVC pipe | 3.5 | 5 | 5.5 | 5.5 | 6 | 6 | 7 | 7.5 | 8 | 9 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |

Hidden Paragraph

| Spacing (Feet) ​​<< material>>​​ pipe | ​​<< ______>>​​ | ​​<< ______>>​​ | ​<< ____>>​ | ​<< ____>>​ | ​<< ____>>​ | ​​<< ______>>​​ | ​​<< ____>>​​ | ​​<< ____>>​​ | ​​<< ____>>​​ | ​​<< ____>>​​ |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |

Refrigeration Piping

Comply with the requirements of <<ASME B31.5>>.

Maximum Hanger Spacing:

| Size (NPS) Nominal | 1/4 to 3/4 | 1 | 1 ¼ | 1 ½ to 2 | 2-1/4 to 2-1/2 |
| --- | --- | --- | --- | --- | --- |
| Spacing (Feet) Copper Tube (Liquid or Vapor Service) | 5 | 6 | 7 | 8 | 9 |

HANGER ROD SIZE

      - ***************************************************************************************

      - The following paragraphs are designer choices based on project-specific conditions.

      - ***************************************************************************************

Plumbing (UPC) Piping (Water, Gas, Drain, Waste & Vent (DWV))

| Pipe Size (NPS) | 1/2 - 4 | 5 - 8 |
| --- | --- | --- |
| Rod Size (Inches) | 3/8 | 1/2 |

Other Piping (NFPA, ASME, etc.)

| Pipe or Tubing Size (NPS) | 3/8 - 2 | 2 ½ - 3 ½ | 4 - 5 | 6 – 8 | 10 - 12 |
| --- | --- | --- | --- | --- | --- |
| Rod Size (Inches) | 3/8 | 1/2 | 5/8 | 3/4 | 7/8 |

END OF SECTION

    - **********************************************************************************************

      - Do not omit the following reference information:

    - **********************************************************************************************

THE FOLLOWING STATEMENT IS FOR LANL USE ONLY

THIS PROJECT SPECIFICATION SECTION IS BASED ON LANL MASTER SPECIFICATION SECTION 22 0529, REV. 8, DATED APRIL 15, 2026.