Section 22 0713 
Plumbing and HVAC Insulation

  - *************************************************************************************************************

    - LANL MASTER SPECIFICATION SECTION

Rev. 8 Summary of Changes: Edited and updated as required for import into SpecLink.

      - NOTE TO SPECIFIER ON USAGE IN SPECLINK: Activate the Section by turning on Seq #0000, followed by activating paragraphs in PART 1, Article SECTION INCLUDES. This will activate related articles, paras/subparas in the rest of the Section (i.e., PART 1 activates articles and paras/subparas in PARTS 2 and 3). If there are choice fields to edit the entire Section (typically in this first author note or beginning of the Section), make selections at those locations, which will filter through the remaining Section. All Articles, paragraphs and subparagraphs must be activated sequentially from top to bottom, unless noted otherwise.

      - This template must be edited for each project. In doing so, Specifier must add job-specific requirements. Selections and choice fields are used to indicate designer choices or locations where text must be supplied by the designer. The section must also be edited to remove requirements for processes, items, or designs that are not included in the project.

      - To seek a variance from applicable requirements in this Section, contact the Engineering Standards Manual (ESM) Mechanical POC  (LANL access only). Please contact POC with suggestions for improvement as well. LANL personnel should submit here: Suggested Change or Request Clarification; subcontractors via email to engstandards@lanl.gov.

      - When assembling a specification package, include applicable specifications from all Divisions, especially Division 1, General Requirements.

      - Section is developed for ML-4 projects.  For ML-1, 2, and 3 applications, additional requirements and independent reviews should be added if increased confidence in procurement or execution is desired; see ESM Chapter 1 - General, Section Z10 Specifications and Quality sections.

  - *************************************************************************************************************

Part 1 - GENERAL

SECTION INCLUDES

      - ***************************************************************************************

      - The following paragraphs are designer choices based on project-specific conditions.

      - ***************************************************************************************

Fiberglass Pipe Insulation

Elastomeric Pipe Insulation

Underground Pipe Insulation

Hydrous Calcium Silicate Pipe Insulation

Undersink Piping Covers

Glass Fiber Blanket Duct Insulation

Glass Fiber Board Duct Insulation

Metal Jacketing - Piping/Ductwork

Protection Saddles and Shields

Removable Insulation Kits

Insulation for Equipment Not Factory Insulated.

      - ***************************************************************************************

      - Section << 01 8113.13 - Sustainable Design>> is not referenced in the body of this Section. Including it is a designer-choice when applicable to the project.

      - ***************************************************************************************

related requirements

Section << 01 2500 - Substitution Procedures>>.

Section << 01 8113.13 - Sustainable Design>>.

reference standards

ASHRAE Std 55 - Thermal Environmental Conditions for Human Occupancy.

ASTM C177 - Standard Test Method for Steady-State Heat Flux Measurements and Thermal Transmission Properties by Means of the Guarded-Hot-Plate Apparatus.

ASTM C533 - Standard Specification for Calcium Silicate Block and Pipe Thermal Insulation.

ASTM C534/C534M - Standard Specification for Preformed Flexible Elastomeric Cellular Thermal Insulation in Sheet and Tubular Form.

ASTM C547 - Standard Specification for Mineral Fiber Pipe Insulation.

ASTM C612 - Standard Specification for Mineral Fiber Block and Board Thermal Insulation.

ASTM C1136 - Standard Specification for Flexible, Low Permeance Vapor Retarders for Thermal Insulation.

ASTM C1290 - Standard Specification for Flexible Fibrous Glass Blanket Insulation Used to Externally Insulate HVAC Ducts.

ASTM C1695 - Standard Specification for Fabrication of Flexible Removable and Reusable Blanket Insulation for Hot Service.

ASTM E84 - Standard Test Method for Surface Burning Characteristics of Building Materials.

ICC A117.1 - Accessible and Usable Buildings and Facilities.

MSS SP-58 - Pipe Hangers and Supports - Materials, Design, Manufacture, Selection, Application, and Installation.

UL 723 - Standard for Test for Surface Burning Characteristics of Building Materials.

DEFINITIONS

For definitions and acronyms, refer to COE Glossary of Terms.

Finished Areas: Areas where floor, walls, ceilings, trim, or exposed steel are painted, tiled, or similarly finished.

Unfinished Areas: Areas with unpainted walls.

Conditioned Spaces: A heated or cooled space, or both, within a building and, where required, provided with humidification or dehumidification means so as to be capable of maintaining a space condition falling within the comfort envelope set forth in <<ASHRAE Std 55>>, e.g., offices, mechanical rooms, storage rooms, etc.

Unconditioned Spaces: Pipe tunnels, covered pipe trenches, spaces inside walls, duct or pipe shafts, spaces above dropped ceilings, unfinished attic spaces and crawl spaces.

Ductwork Exposed to Outdoor Temperatures: Includes ductwork located outdoors, and ductwork located indoors that transports unconditioned outside air.

Exposed Areas: Finished areas and other areas used by personnel in the normal use of the building, such as fan rooms, mechanical room, and storage rooms.

Concealed Areas: Pipe tunnels, covered pipe trenches, spaces inside walls, duct or pipe shafts, spaces above dropped ceilings, unfinished attic spaces and crawl spaces.

submittals

Action Submittals

Product Data: For each type of product indicated. Include thermal conductivity, water-vapor permeance thickness, and jackets (both factory and field applied, if any).

Informational Submittals

Manufacturer's Installation Instructions: Manufacturers published literature indicating proper installation procedures.

QUALITY ASSURANCE

Materials: Flame spread/smoke developed rating of 25/50 or less in accordance with <<ASTM E84>> and <<UL 723>>.

Provide insulation material 100 percent asbestos-free.

Provide products that do not promote or support the growth of mold, fungi, or bacteria.

FIELD CONDITIONS

Maintain ambient temperatures and conditions required by manufacturers of adhesive, mastic, and insulation cements.

Maintain temperature during installation per manufacturer’s instructions.

Install insulation only when ambient temperature and humidity conditions are within range recommended by manufacturer.

PART 2 - PRODUCTS

GENERAL

K-factors (thermal conductivity) shown are expressed in BTU-in/hr-ft2-deg. F.

MANUFACTURERS

Knauf Fiber Glass.

Owens/Corning Fiberglass.

CertainTeed.

Johns Manville.

Armaflex.

PRODUCT OPTIONS AND SUBSTITUTIONS

Alternate products may be accepted; follow Section ​<< 01 2500 - Substitution Procedures>>​.

      - ***************************************************************************************

      - The following PART 2 Articles are designer choices based on project-specific conditions.

      - ***************************************************************************************

FIBERGLASS PIPE INSULATION

Insulation: Rigid molded in compliance with <<ASTM C547>>, Class 1, minimum density 3.5 pounds/cubic foot, K-factor of approximately 0.23 at 75 degrees F, suitable for temperatures from 0 degrees F to 850 degrees F.

Jacket: Factory applied vapor barrier, reinforced foil kraft with self-sealing adhesive joints, <<ASTM C1136>>.

Valves and Fitting Covers: Pre-molded PVC covers with fiber glass insert.

Manufacturers: Proto Corp., Ceelco.

ELASTOMERIC PIPE INSULATION

Manufacturer: Armacell AP Armaflex.

Insulation: Cellular closed cell in compliance with <<ASTM C534/C534M>>, Type 1, Grade 1 minimum density 5 pounds/cubic foot, K-factor of approximately 0.30 at 75 degrees F, suitable for temperatures up to 220 degrees F.

Valve and Fitting Covers: Same as pipe insulation, cut to fit.

      - ***************************************************************************************

      - Designer should retain the paragraph below when a paint finish is preferred to an aluminum jacket.

      - ***************************************************************************************

Weather Resistant Protective Finish: Acrylic latex enamel paint.

Manufacturer: WB Armaflex finish.

UNDERGROUND PIPE INSULATION

Insulation: Gilsulate 500XR dry granular particles in compliance with <<ASTM C177>>​, density 30-34 lbs/ft3 K-factor of approximately 0.53 at 100 degrees F suitable for temperatures up to 300 degrees F.

Fittings: Same material as pipe insulation.

HYDROUS CALCIUM SILICATE PIPE INSULATION

Insulation: Rigid, in compliance with <<ASTM C533>>​, Type 1, minimum density 13 pounds/cubic foot, K-factor of approximately 0.45 at 200 degrees F, suitable for temperature from 140 degrees F to 1200 degrees F.

Valve and Fitting Covers: Same as pipe insulation or "Quick Set" insulating cement.

UNDERSINK PIPING COVERS

Provide <<ICC A117.1>>-compliant, resilient, molded, white vinyl covers for wheelchair-accessible lavatory/sink P-traps and angle valve/supply line (hot and cold) assemblies.

Manufacturer: Truebro Lav Guard 2 E-Z Series.

GLASS FIBER BLANKET DUCT INSULATION

      - ***************************************************************************************

      - Exterior ductwork may also be insulated using duct liner installed inside the ductwork. Refer to Section << 23 3101 - HVAC Ducts>>  Ducts, for liner specification and limitations.

      - ***************************************************************************************

Insulation: Flexible blanket, in compliance with <<ASTM C1290>>, Type III, minimum density 3/4 lbs/ft3, K-factor of approximately 0.30 at 75 degrees F, suitable for temperature up to 250 degrees F.

Jacket: Factory applied reinforced aluminum foil jacket meeting <<ASTM C1136>>.

Fittings: Same material as insulation.

GLASS FIBER BOARD DUCT INSULATION

      - ***************************************************************************************

      - Exterior ductwork may also be insulated using duct liner installed inside the ductwork. Refer to << 23 3101 - HVAC Ducts>> for liner specification and limitations.

      - ***************************************************************************************

Insulation: Rigid glass fiber, in compliance with <<ASTM C612>>, Type IA or IB,, minimum density of 3 pounds/cubic foot, K-factor approximately 0.23 at 75 degrees F, suitable for temperature up to 450 degrees F.

Jacket: Factory applied, metalized, polypropylene-scrim kraft facing meeting <<ASTM C1136>>.

Fittings: Same material as insulation.

      - ***************************************************************************************

      - In heavy abuse areas, use metal jacketing to protect piping or ductwork insulation.

      - ***************************************************************************************

METAL JACKETING - PIPING/DUCTWORK

Jacketing: Aluminum, 0.016 inches thick, embossed surface, with factory bonded moisture barrier.

Valve and Fitting Insulation Covers: Fabricate from same material as jacketing or use prefabricated insulation covers made in two matching halves.

Metal Jacketing Bands: 3/8 inch wide, 0.010 inch thick stainless steel.

protection saddles and shields

Provide factory engineered galvanized steel hanger shields on horizontal insulated pipe complying with <<MSS SP-58>> standards for gauge and length of saddle.

Saddles (Piping/tubing up to 2 inches):

Use 180 degree saddle on systems utilizing teardrop type hangers. B-Line B3151 or B3153 Series.

Use 360 degree saddle on systems utilizing trapeze hangers or clamps. B-Line B338 Series.

Inserts and Shields (Piping/tubing over 2 inches):

Manufacturer: B-Line B338 series.

Use 360 degree calcium silicate insert with a 180 degree shield on systems utilizing clevis or teardrop type hangers.

Use 360 degree calcium silicate with a 360 degree shield on systems utilizing trapeze hangers or clamps.

The unit shall have an integral moisture barrier consisting of a tri-laminate All-Service Jacket equal and similar to the jacketing on the adjoining insulation.

Insert: Calcium silicate, minimum density 9 lbs/ft3.

REMOVABLE INSULATION kits

Manufacturer: Auburn Manufacturing.

Style: Ever Green Cut ‘N Wrap.

<<ASTM C1695>>, fiberglass inner core and high-performance-polymer coated woven glass fiber fabric outer layer on both sides.

Maximum temperature 500 degrees F.

Weight, oz./ft2: 7.65.

Insulation For equipment not factory insulated

      - ***************************************************************************************

      - Complete as required to meet job requirements.

      - ***************************************************************************************

<< _______>>.

PART 3 - EXECUTION

EXAMINATION

Verify that items to be insulated have been pressure tested and approved before applying insulation material.

Verify that surfaces are clean, foreign material removed, and dry.

INSTALLATION - GENERAL

Install materials in accordance with manufacturer's instructions.

Do not insulate factory-insulated equipment.

Do not insulate nameplates.

Fit insulation tightly against surface to which it is applied.

Do not insulate flexible connections.

For non-fire rated barriers (e.g., wall, floor, ceiling, or roof) continue insulation and vapor barrier through penetrations. For fire rated barriers, provide UL/FM approved through penetration stop systems.

Weatherproof outdoor installations of piping or ductwork covered with aluminum jacket. Provide watershed lap joints and seal with mastic as required.

Do not install metal jacketing with raw edges; provide a safety edge.

Replace existing insulation where it has been damaged or removed as a result of modifications. Vapor barrier shall be continuous. Thickness of insulation that is replaced shall match new.

INSTALLATION - PIPING INSULATION

On exposed piping located in finished areas, locate insulation and cover seams in least visible area.

Provide calcium silicate shields (for piping/tubing over 2 inches) or saddles (for piping/tubing up to 2 inches) through pipe hangers or supports. Do not notch insulation.

Where insulation terminates, taper to pipe and finish with insulating cement or acrylic mastic.

Cover insulated pipes located outdoors or in utility tunnels with aluminum jacket. Secure with aluminum bands and screws as required.

For underground pipe insulation, follow manufacturer’s instructions.

Tape circumferential joints of pipe insulation with 3 inch wide white vinyl tape.

Insulate fitting and valves where required with same material thickness as specified for adjacent pipe.

Insulate potable and non-potable cold water piping within walls, chases, or ceiling plenums where return air is present.

Insulate potable and non-potable cold water piping in equipment rooms.

Do not insulate unions, flanges and valves in potable or non-potable piping systems of 140 degrees F or less, except for chilled water. << Provide removable insulation at these locations.; or  None - N/A>>

Insulate refrigerant discharge line (hot gas discharge) when there is a danger of personnel coming in contact with piping or when the line is passing through a conditioned space. Insulate refrigerant liquid line when it is passing through spaces having temperatures greater than the refrigerant condensing temperatures. Insulate refrigerant suction piping.

Provide removable insulation kits for piping components such as valve stems and bonnets, flanges, pressure regulators, data and name plates, pot feeders, flanges, pressure regulating valves, strainers, etc. that are not easily insulated with standard insulation.

INSTALLATION - DUCTWORK INSULATION

Secure rigid board insulation to ductwork with metal fasteners (stick-klip) and scrim washer on 12 inch centers each way. Secure fasteners to duct work with recommended adhesive.

Tape ductwork insulation joints and penetrations caused by mechanical fasteners with 3 inch wide Foil-Scrim-Kraft tape.

Cover insulated ductwork located outdoors with aluminum jacketing. Secure with bands as required.

Provide continuous insulation through hangers or supports. Do not notch insulation.

Use blanket insulation on round ductwork and board insulation (rigid) on rectangular ductwork. Exception: In concealed areas blanket insulation may be used on rectangular ductwork.

Stop insulation around access doors and damper operators to allow operation without disturbing wrapping.

INSULATION SCHEDULE

      - ***************************************************************************************

      - When using the insulation schedule tables below, the Designer shall retain the paragraphs and table row(s) that apply to the project.

      - ***************************************************************************************

HVAC Piping Systems: Use fiberglass pipe insulation with thickness determined by the table below. Note, increase insulation thickness by 1/2 inch when piping is exposed to outdoor temperatures except when service is noted for outdoor temperatures.

      - ***************************************************************************************

      - Verify insulation thickness with ASHRAE 90.1.

      - ***************************************************************************************

| Service | Nominal Pipe Diameter (inches) | Insulation Thickness (inches) |
| --- | --- | --- |

Hidden Paragraph

| Steam (to 15 psi) | Less than 4 4 and over | 2 1/2 3 |
| --- | --- | --- |

Hidden Paragraph

| Steam (above 15 psi to 100 psi) | Less than 1 1 to 1-1/4 1 1/2 and over | 3 4 4 1/2 |
| --- | --- | --- |

Hidden Paragraph

| Steam Condensate | Less than 1 1/2 1 1/2 and over | 1 1/2 2 |
| --- | --- | --- |

Hidden Paragraph

| Steam Blowdown Piping | All Sizes | 2 |
| --- | --- | --- |

Hidden Paragraph

| Heating hot water, 141 to 200 degrees F | Less than 1 1/2 1 1/2 and over | 1 1/2 2 |
| --- | --- | --- |

Hidden Paragraph

| Heating hot water, 105 to 140 degrees F | Less than 1 1/2 1 1/2 and over | 1 1 1/2 |
| --- | --- | --- |

Hidden Paragraph

| Potable hot water, 105 degrees F & greater | Less than 1 1/2 1 ½ and over | 1 1 1/2 |
| --- | --- | --- |

Hidden Paragraph

| Non-potable hot water, 105 degrees F & greater | Less than 1 1/2 1 1/2 and over | 1 1 1/2 |
| --- | --- | --- |

Hidden Paragraph

| Chilled water, 40 to 60 degrees F | Less than 1 1/2 1 ½ and over | 1/2 1 |
| --- | --- | --- |

Hidden Paragraph

| Potable cold water | Less than 1 1/2 1 ½ and over | 1/2 1 |
| --- | --- | --- |

Hidden Paragraph

| Non-potable cold water | Less than 1 1/2 1 ½ and over | 1/2 1 |
| --- | --- | --- |

Hidden Paragraph

| Tower water exposed to outdoor temperatures | All sizes | 1 1/2 |
| --- | --- | --- |

Hidden Paragraph

| Roof drain bowl and storm water piping | All sizes | 1 |
| --- | --- | --- |

Refrigerant Piping: Use elastomeric piping insulation. Protect insulation exposed to weather with aluminum jacket or weather resistant protective finish.

| Service | Nominal Pipe Diameter (inches) | Insulation Thickness (inches) |
| --- | --- | --- |

Hidden Paragraph

| Refrigerant suction | Less than 1 1 and over | 1/2 1 |
| --- | --- | --- |

Hidden Paragraph

| Refrigerant discharge | Up to 1-1/4 Over 1-1/4 | 1/2 1 |
| --- | --- | --- |

Hidden Paragraph

| Refrigerant liquid | All Sizes | 1/2 |
| --- | --- | --- |

Hidden Paragraph

| Refrigerant Coil Condensate Drain | All Sizes | 1/2 |
| --- | --- | --- |

Handicapped Lavatory Piping: Use elastomeric pipe insulation per <<ICC A117.1>>​ Section 606.6:

| Service | Pipe Sizes (inches) | Insulation Thickness (inches) |
| --- | --- | --- |
| Exposed drain and hot water lines | All sizes | 1/2 |

Concealed Ductwork: Use glass fiber (flexible blanket) duct insulation..

| Service | Insulation Thickness (inches) |
| --- | --- |
| Supply and return air | 1 1/2 |

Exhaust Piping: Use hydrous calcium silicate insulation. Wrap with aluminum jacketing.

| Service | Insulation Thickness (inches) |
| --- | --- |
| Generator Exhaust Piping/Muffler | 1 1/2 |

Exposed Rectangular Ductwork: Use glass fiberboard (rigid) duct insulation on the exterior of the ductwork.

NOTE: Use nominal 4-inch-thick insulation (R-12 equivalent) for ductwork exposed to outdoor temperatures.

| Service | Insulation Thickness (inches) |
| --- | --- |
| Supply and return air | 1 1/2 |

Exposed Round Ductwork: Use glass fiber (flexible blanket) duct insulation.

NOTE: Use nominal 4-inch-thick insulation (R-12 equivalent) for ductwork exposed to outdoor temperatures.

| Service | Insulation Thickness (inches) |
| --- | --- |
| Supply and return air | 1 1/2 |

END OF SECTION

    - **********************************************************************************************

      - Do not omit the following reference information.

    - **********************************************************************************************

THE FOLLOWING STATEMENT IS FOR LANL USE ONLY

THIS PROJECT SPECIFICATION SECTION IS BASED ON LANL MASTER SPECIFICATION SECTION 22 0713, REV. 8, DATED APRIL 15, 2026.